## Content List
Schedule of Particular Standard Material Specifications |  | Summary
Schedule | Description of Particulars
No.
0. | General Requirements
0.1. | Climatic Conditions
0.2. | Main Design Data 330 kV, 2000 m.a.s.l
0.3. | Main Design Data 132(66) kV, 2000 m.a.s.l
0.4. | Main Design Data 11 kV, 2000 m.a.s.l
0.5. | Main Design Data 0.4 kV, 2000 m.a.s.l
0.6. | Material
Transmission Substations
1. | Conductor
1.1. | Tarantula
1.2. | LGKK-600
1.3. | Bison
1.4. | ACS 7/4.11 Shield Wire
1.5. | Tension insulator set
1.6. | Suspension insulator set
1.7. | Post insulator
1.8. | Hardware and fitting for phase conductor
1.9. | Hardware and fitting for Earth-wire
1.10. | Earthing Conductor for Substation
2. | 330 kV Equipment
2.1. | 330 kV Circuit Breaker
2.2. | 330 kV Disconnector Line
2.3. | 330 kV Disconnector Transformer
2.4. | 330 kV Earthing Switch at Disconnector
2.5. | 330 kV Current Transformer Line Feeder Bay
2.6. | 330 kV Current Transformer - Transformer Bay
2.7. | 330 kV Capacitive Voltage Transformers
2.8. | 330 kV Surge Arresters
2.9. | #N/A
3. | 132 kV & 66kV Equipment
3.1. | 132 kV Circuit Breaker
3.2. | 132 kV Disconnector
3.3. | 132 kV Earthing Switch
3.4. | 132 kV Current Transformers
3.5. | 132(66) kV Capacitive Voltage Transformers
4. | Transformers
4.1. | Power Transformer 330/132(66)/11 kV
5. | Reactor
5.1. | Shunt Reactor 330 kV (10MVAr)
5.2. | Neutral Compensating Reactor 35 kV
6. | 11 kV Equipment
6.1. | 11 kV Indoor Compact Metal Clad Air Insulated Switchgear
6.2. | 11 kV Surge Arresters
7. | Power Cables
7.1. | 11 kV Power Cable
7.2. | 11 kV Cable Terminations
8. | Auxiliary Systems
8.1. | 11/0.4 kV Substation Auxiliary Transformer
8.2. | Stand-by Diesel Generator
8.3. | Battery 110 V DC
8.4. | Battery Chargers 110 V DC
8.5. | Battery 48 V DC
8.6. | Battery Chargers 48 V DC
8.7. | CCTV Surveillance System and Access Control
9. | Control and Protection Equipment
9.1. | Three Phase Programmable Meter
9.2. | Three Phase Power Quality Meter
9.3. | Metering Workingstation and Automatic Meter Infrastructure
9.4. | Station Servers
9.5. | Gateway
9.6. | Remote Terminal Unit
9.7. | Engineering Workstation
9.8. | Station LAN
9.9. | All Bay Control Units
9.10. | Bay Control Unit OHL and Reactor
9.11. | Busbar protection 330 and 132 kV - Main I
9.12. | Line Protection 330 and 132 kV - Main I Diff. Protection
9.13. | Line Protection 330 and 132 kV - Main II Distance Protection
9.14. | Line Protection 330 and 132 kV - Back-up
9.15. | Transformer Automatic Voltage Control
9.16. | Transformer, Reactor Protection 330 and 132 kV - Main I
9.17. | Transformer, Reactor Protection 330 and 132 kV - Main II
9.18. | Transformer, Reactor and Neutral Reactor Protection 330 and 132 kV - Back-up
9.19. | Transformer Protection 11/0.4 kV
9.20. | Digital Meetering
9.21. | Meters, indicating Instrument
9.22. | OFC Approach Fibre Cable
9.23. | Optical Distribution Frame (ODF)
9.24. | Optical Transport Network (OTN)
9.25. | Optical Transport Network Equipment
9.26. | Packet Transport Network Equipment
9.27. | Synchronous Digital Hierarchy (SDH)Equipment STM-64
9.28. | FOX 615 Equipment STM-16
9.29. | PABX Equipment
9.30. | Laptop Computer
10. | Wide Area Monitoring Protection and Control
10.1. | WAMPACS
11. | Distribution
11.1. | Wooden poles 12m
11.2. | ABC 3x120+70
11.3. | 33 kV Single-phase Load Break Fuse
11.4. | 33/0.4 kV Housing Distribution Transformer
12. | Civil
12.1. | Gabions (for substation perimeter; Refer to drawing PP-ZTIP-P04-ODSS-C109_Nakonde SS GA_R00_30062026 Note 4)
13. | Tools
13.1. | Splicing Machine
13.2. | Circuit Breaker Analyser
13.3. | Omicron CT Analyser
13.4. | OTDR
13.5. | Earth Resistance Tester
13.6. | Micro-Ohmmeter
13.7. | Dielectric Oil Tester
13.8. | SF6 Gas Leak Detector
13.9. | SF6 Gas Filling kits
13.10. | Secondary Injection Test Set
13.11. | Tool Box
13.12. | Disturbance fault recorder
13.13. | Vacuum Pump for Transformer Drying
13.14. | Insulation Resistance Tester 15000V
13.15. | OMICRON CPC100
14. | Transformer and Reactor Mechanical Protection
14.1. | Sergi Fire Protection or Equivalent
14.2. | Kelman Online Dissolve Gas Analysis or Equivalent

## General
0. | General Requirements |  |  |  | 0. |  |  | 0 |  |  | R1
0.1. | Climatic Conditions |  |  |  | 0. | 1. |  | 0 | 1 |  | R2
[8 empty] | 0 | 1 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 0 | 1 | 1 | R3
0.1.1 | Maximum outdoor air temperature; | +45 |  | °C | 0. | 1. | 1 | 0 | 1 | 1
0.1.2 | Minimum outdoor air temperature | -1 |  | °C | 0. | 1. | 2 | 0 | 1 | 2
0.1.3 | Annual max. average air temperature | +35 |  | °C | 0. | 1. | 3 | 0 | 1 | 3
0.1.4 | Maximum temperature of conductor | +75 |  | °C | 0. | 1. | 4 | 0 | 1 | 4
0.1.5 | Maximum temperature of earth wire | +50 |  | °C | 0. | 1. | 5 | 0 | 1 | 5
0.1.6 | Precipation | 850-1200 |  | mm/year | 0. | 1. | 6 | 0 | 1 | 6
0.1.7 | Precipation > 1 mm | 81 |  | days/year | 0. | 1. | 7 | 0 | 1 | 7
0.1.8 | Design wind (gust, 3 sec); | 40 |  | m/s | 0. | 1. | 8 | 0 | 1 | 8
0.1.9 | Design wind speed (sustained); | 100 |  | km/h | 0. | 1. | 9 | 0 | 1 | 9
0.1.10 | Average lightning | High, 10-15 |  | flashes/km² | 0. | 1. | 10 | 0 | 1 | 10
0.1.11 | Relative humidity (min/max) | 39/85 |  | % | 0. | 1. | 11 | 0 | 1 | 11
0.1.12 | Maximum soil temperature (at 1 m depth); | +30 |  | °C | 0. | 1. | 12 | 0 | 1 | 12
0.1.13 | Maximum soil thermal resistivity | 1.2 |  | km/W | 0. | 1. | 13 | 0 | 1 | 13
0.1.14 | Maximum solar radiation on plan; | 1035 |  | W/m² | 0. | 1. | 14 | 0 | 1 | 14
0.1.15 | Exposed bare metal temperature; | +75 |  | °C | 0. | 1. | 15 | 0 | 1 | 15
0.1.16 | Altitude above see level; | 1600 |  | masl | 0. | 1. | 16 | 0 | 1 | 16
0.1.17 | Design altitude substations | 2000 |  |  | 0. | 1. | 17 | 0 | 1 | 17
0.1.18 | Altitude correction factor according to IEC60071-2 ≤200000 masl | 1.13 |  | - | 0. | 1. | 18 | 0 | 1 | 18
0.1.19 | Safety factor for outdoor insulation | 1.05 |  | - | 0. | 1. | 19 | 0 | 1 | 19
0.1.20 | Atmosphere pollutants | Medium/Dust |  | - | 0. | 1. | 20 | 0 | 1 | 20
0.1.21 | Seismic hazard (Mercalli scale); | VI to VII (strong-very strong) |  | - | 0. | 1. | 21 | 0 | 1 | 21
0.1.22 | Degree of protection, outdoor | IP56 |  | - | 0. | 1. | 22 | 0 | 1 | 22
0.1.23 | Degree of protection, indoor | IP54 |  | - | 0. | 1. | 23 | 0 | 1 | 23
[8 empty] | 0 | 1 | 24 | tom rad
0.2. | Main Design Data 330 kV, 2000 m.a.s.l |  |  |  | 0. | 2. |  | 0 | 2 | 18 | R2
[8 empty] | 0 | 2 | 19 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 0 | 2 | 20 | R3
0.2.1 | Nominal system voltage, Un; | 330 |  | kV r.m.s | 0. | 2. | 1 | 0 | 2 | 1
0.2.2 | Rated voltage, Ur; | 362 |  | kV r.m.s | 0. | 2. | 2 | 0 | 2 | 2
0.2.3 | Rated short time current (1 sec); | 40 |  | kA | 0. | 2. | 3 | 0 | 2 | 3
0.2.4 | Rated short-duration power frequency withstand voltage | 580 |  | kV r.m.s | 0. | 2. | 4 | 0 | 2 | 4
0.2.5 | Rated lightning impulse withstand voltage | 1245 |  | kVp | 0. | 2. | 5 | 0 | 2 | 5
0.2.6 | Rated switching impulse withstand voltage phase to earth | 1080 |  | kVp | 0. | 2. | 6 | 0 | 2 | 6
0.2.7 | Rated switching impulse withstand voltage, phase to phase ratio to the phase to earth peak value | 1.50 |  | - | 0. | 2. | 7 | 0 | 2 | 7
0.2.8 | Rated frequency, f; | 50 ±2.5% |  | Hz | 0. | 2. | 8 | 0 | 2 | 8
0.2.9 | Minimum insulator creepage distance (USCD); | 53.7 (class e , very heavy) |  | mm/kV | 0. | 2. | 9 | 0 | 2 | 9
0.2.10 | Minimum clearance, phase to phase; | 3842 |  | mm | 0. | 2. | 10 | 0 | 2 | 10
0.2.11 | Minimum clearance, phase to earth; | 3390 |  | mm | 0. | 2. | 11 | 0 | 2 | 11
0.2.12 | Safe working clearance (to the nearest live conductor in air); | 5932.5 |  | mm | 0. | 2. | 12 | 0 | 2 | 12
0.2.13 | Minimum height of support structure | 2825 |  | mm | 0. | 2. | 13 | 0 | 2 | 13
0.2.14 | Bay width; | 21000 |  | mm | 0. | 2. | 14 | 0 | 2 | 14
0.2.15 | Voltage quality | ±5 |  | % | 0. | 2. | 15 | 0 | 2 | 15
0.2.16 | Frequence quality | ±2.5 |  | % | 0. | 2. | 16 | 0 | 2 | 16
0.2.17 | System earthing; | Effectively grounded |  | - | 0. | 2. | 17 | 0 | 2 | 17
[8 empty] | 0 | 2 | 18 | tom rad
0.3. | Main Design Data 132(66) kV, 2000 m.a.s.l |  |  |  | 0. | 3. |  | 0 | 3 | 19 | R2
[8 empty] | 0 | 3 | 20 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 0 | 3 | 21 | R3
0.3.1 | Nominal system voltage, Un; | 66 |  | kV r.m.s | 0. | 3. | 1 | 0 | 3 | 1
0.3.2 | Rated voltage, Ur; | 145 |  | kV r.m.s | 0. | 3. | 2 | 0 | 3 | 2
0.3.3 | Rated short time current (3 sec); | 31.5 |  | kA | 0. | 3. | 3 | 0 | 3 | 3
0.3.4 | Rated short-duration power frequency withstand voltage | 311 |  | kV r.m.s | 0. | 3. | 4 | 0 | 3 | 4
0.3.5 | Rated lightning impulse withstand voltage | 735 |  | kV r.m.s | 0. | 3. | 5 | 0 | 3 | 5
0.3.6 | Rated switching impulse withstand voltage | 356 |  | kVp | 0. | 3. | 6 | 0 | 3 | 6
0.3.7 | Rated frequency, f; | 50 ±2.5% |  | Hz | 0. | 3. | 7 | 0 | 3 | 7
0.3.8 | Minimum insulator creepage distance (USCD); | 53.7 (class e , very heavy) |  | mm/kV | 0. | 3. | 8 | 0 | 3 | 8
0.3.9 | Minimum clearance, phase to phase; | 1773.75 |  | mm | 0. | 3. | 9 | 0 | 3 | 9
0.3.10 | Minimum clearance, phase to earth; | 1397.5 |  | mm | 0. | 3. | 10 | 0 | 3 | 10
0.3.11 | Safe working clearance (to the nearest live conductor in air); | 4945 |  | mm | 0. | 3. | 11 | 0 | 3 | 11
0.3.12 | Bay width; | 12200 |  | mm | 0. | 3. | 12 | 0 | 3 | 12
0.3.13 | Voltage quality | ±5 |  | % | 0. | 3. | 13 | 0 | 3 | 13
0.3.14 | Frequence quality | ±2.5 |  | % | 0. | 3. | 14 | 0 | 3 | 14
0.3.15 | System earthing; | Effectively grounded |  | - | 0. | 3. | 15 | 0 | 3 | 15
[8 empty] | 0 | 3 | 16 | tom rad
0.4. | Main Design Data 11 kV, 2000 m.a.s.l |  |  |  | 0. | 4. |  | 0 | 4 | 17 | R2
[8 empty] | 0 | 4 | 18 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 0 | 4 | 19 | R3
0.4.1 | Nominal system voltage, Un; | 11 |  | kV r.m.s | 0. | 4. | 1 | 0 | 4 | 1
0.4.2 | Rated voltage, Ur; | 12 |  | kV r.m.s | 0. | 4. | 2 | 0 | 4 | 2
0.4.3 | Rated short time current (3 sec); | 31.5 |  | kA | 0. | 4. | 3 | 0 | 4 | 3
0.4.4 | Rated short-duration power frequency withstand voltage (phase to earth and between phases); | 31.64 |  | kV r.m.s | 0. | 4. | 4 | 0 | 4 | 4
0.4.5 | Rated short-duration power frequency withstand voltage (across open breaker gap and/or isolating distance); | 31.64 |  | kV r.m.s | 0. | 4. | 5 | 0 | 4 | 5
0.4.6 | Rated lightning impulse withstand voltage (phase to earth and between phases); | 84.75 |  | kVp | 0. | 4. | 6 | 0 | 4 | 6
0.4.7 | Rated lightning impulse withstand voltage (across open breaker gap and/or isolating distance); | 84.75 |  | kVp | 0. | 4. | 7 | 0 | 4 | 7
0.4.8 | Rated frequency, f; | 50 ±2.5% |  | Hz | 0. | 4. | 8 | 0 | 4 | 8
0.4.9 | Minimum insulator creepage distance (USCD); | 53.7 (class e , very heavy) |  | mm/kV | 0. | 4. | 9 | 0 | 4 | 9
0.4.10 | Minimum clearance, phase to phase; | 305.1 |  | mm | 0. | 4. | 10 | 0 | 4 | 10
0.4.11 | Minimum clearance, phase to earth; | 226 |  | mm | 0. | 4. | 11 | 0 | 4 | 11
0.4.12 | Safe working clearance (to the nearest live conductor in air); | 2938 |  | mm | 0. | 4. | 12 | 0 | 4 | 12
0.4.13 | Voltage quality | ±10 |  | % | 0. | 4. | 13 | 0 | 4 | 13
0.4.14 | Frequence quality | ±2.5 |  | % | 0. | 4. | 14 | 0 | 4 | 14
0.4.15 | System earthing; | Effectively grounded |  | - | 0. | 4. | 15 | 0 | 4 | 15
[8 empty] | 0 | 4 | 16 | tom rad
0.5. | Main Design Data 0.4 kV, 2000 m.a.s.l |  |  |  | 0. | 5. |  | 0 | 5 | 17 | R2
[8 empty] | 0 | 5 | 18 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 0 | 5 | 19 | R3
0.5.1 | Nominal system voltage, Un; | 0.4 |  | kV r.m.s | 0. | 5. | 1 | 0 | 5 | 1
0.5.2 | Rated voltage, Ur; | 1 |  | kV r.m.s | 0. | 5. | 2 | 0 | 5 | 2
0.5.3 | Rated short time current (3 sec); | 7.5 |  | kA | 0. | 5. | 3 | 0 | 5 | 3
0.5.4 | Rated short-duration power frequency withstand voltage (phase to earth and between phases); | 2.26 |  | kV r.m.s | 0. | 5. | 4 | 0 | 5 | 4
0.5.5 | Rated short-duration power frequency withstand voltage (across open breaker gap and/or isolating distance); | 2.26 |  | kV r.m.s | 0. | 5. | 5 | 0 | 5 | 5
0.5.6 | Rated lightning impulse withstand voltage (phase to earth and between phases); | 7.91 |  | kVp | 0. | 5. | 6 | 0 | 5 | 6
0.5.7 | Rated lightning impulse withstand voltage (across open breaker gap and/or isolating distance); | 7.91 |  | kVp | 0. | 5. | 7 | 0 | 5 | 7
0.5.8 | Rated frequency, f; | 50 ±2.5% |  | Hz | 0. | 5. | 8 | 0 | 5 | 8
0.5.9 | Voltage quality | ±10 |  | % | 0. | 5. | 9 | 0 | 5 | 9
0.5.10 | Frequence quality | ±2.5 |  | % | 0. | 5. | 10 | 0 | 5 | 10
0.5.11 | System earthing; | Effectively grounded |  | - | 0. | 5. | 11 | 0 | 5 | 11
[8 empty] | 0 | 5 | 12 | tom rad
0.6. | Material |  |  |  | 0. | 6. |  | 0 | 6 | 13 | R2
[8 empty] | 0 | 6 | 14 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 0 | 6 | 15 | R3
0.6.1 | Cast iron |  |  |  | 0. | 6. | 1 | 0 | 6 | 1
0.6.2 | Malleable iron type | Black heart |  |  | 0. | 6. | 2 | 0 | 6 | 2
0.6.3 | Malleable iron strength | >330 |  | N/mm2 | 0. | 6. | 3 | 0 | 6 | 3
0.6.4 | Minimum tensile strength: | 140 |  | N/mm2 | 0. | 6. | 4 | 0 | 6 | 4
0.6.5 | Manufacturing from: | Best grey pig and scrap iron |  |  | 0. | 6. | 5 | 0 | 6 | 5
0.6.6 | Preparation: | Close grained, though and uniform in character |  |  | 0. | 6. | 6 | 0 | 6 | 6
0.6.7 |  |  |  |  | 0. | 6. | 7 | 0 | 6 | 7
0.6.8 |  |  |  |  | 0. | 6. | 8 | 0 | 6 | 8
0.6.9 |  |  |  |  | 0. | 6. | 9 | 0 | 6 | 9
[8 empty] | 0 | 6 | 10 | tom rad
0.7. | Galvanizing Minimum above ground |  |  |  | 0. | 7. |  | 0 | 7 | 11 | R2
[8 empty] | 0 | 7 | 12 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 0 | 7 | 13 | R3
0.7.1 | Steel > 6 mm local coating min | 505; 70 |  | g/m2; µm | 0. | 7. | 1 | 0 | 7 | 1
0.7.2 | Steel > 6 mm mean coating min | 610; 85 |  | g/m2; µm | 0. | 7. | 2 | 0 | 7 | 2
0.7.3 | Steel > 3 mm to u 6 mm local coating min | 395; 55 |  | g/m2; µm | 0. | 7. | 3 | 0 | 7 | 3
0.7.4 | Steel > 3 mm to u 6 mm mean coating min | 505; 70 |  | g/m2; µm | 0. | 7. | 4 | 0 | 7 | 4
0.7.5 | Steel W 1.5 mm to u 3 mm local coating min | 325; 45 |  | g/m2; µm | 0. | 7. | 5 | 0 | 7 | 5
0.7.6 | Steel W 1.5 mm to u 3 mm mean coating min | 395; 55 |  | g/m2; µm | 0. | 7. | 6 | 0 | 7 | 6
0.7.7 | Steel < 1.5 mm local coating min | 250; 35 |  | g/m2; µm | 0. | 7. | 7 | 0 | 7 | 7
0.7.8 | Steel < 1.5 mm mean coating min | 325; 45 |  | g/m2; µm | 0. | 7. | 8 | 0 | 7 | 8
0.7.9 | Castings W 6 mm local coating min | 505; 70 |  | g/m2; µm | 0. | 7. | 9 | 0 | 7 | 9
0.7.10 | Castings W 6 mm mean coating min | 575; 80 |  | g/m2; µm | 0. | 7. | 10 | 0 | 7 | 10
0.7.11 | Castings < 6 mm local coating min | 430; 60 |  | g/m2; µm | 0. | 7. | 11 | 0 | 7 | 11
0.7.12 | Castings < 6 mm mean coating min | 505; 70 |  | g/m2; µm | 0. | 7. | 12 | 0 | 7 | 12

## Particular
| Transmission Substations | [6 empty] | 0 | 0 | 1 | tom rad
1. | Conductor |  |  |  | 1. |  |  | 1 | 0 | 2 | R1
1.1. | Tarantula |  |  |  | 1. | 1. |  | 1 | 1 |  | R2
[8 empty] | 1 | 1 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 1 | 1 | R3
1.1.1 | Manufacturer | Bidder to state |  |  | 1. | 1. | 1 | 1 | 1 | 1
1.1.2 | Manufacturer's type and reference | Bidder to state |  |  | 1. | 1. | 2 | 1 | 1 | 2
1.1.3 | Country of origin | Bidder to state |  |  | 1. | 1. | 3 | 1 | 1 | 3
1.1.4 | Description | AAC |  |  | 1. | 1. | 4 | 1 | 1 | 4
1.1.5 | Standard specification applied | IEC 61089, EN 50341-1, 50341-1, 50852, 50182, 60889, BS 215 |  |  | 1. | 1. | 5 | 1 | 1 | 5
1.1.6 | Aluminum strands | 37 |  | Nos. | 1. | 1. | 6 | 1 | 1 | 6
1.1.7 | Aluminum strands diameter | 5.23 |  | mm | 1. | 1. | 7 | 1 | 1 | 7
1.1.8 | Overall conductor diameter | 36.6 |  | mm | 1. | 1. | 8 | 1 | 1 | 8
1.1.9 | Total conductor cross section | 794.6 |  | mm2 | 1. | 1. | 9 | 1 | 1 | 9
1.1.10 | Ultimate breaking strength of stranded conductor | 12600 |  | daN | 1. | 1. | 10 | 1 | 1 | 10
1.1.11 | DC resistance of conductor at 20°C (Guarantee Value) | 0.0363 |  | ohms/km | 1. | 1. | 11 | 1 | 1 | 11
1.1.12 | Weight per km of conductor | 2200 |  | Kg | 1. | 1. | 12 | 1 | 1 | 12
1.1.13 | Initial modulus of elasticity | 48250 |  | N/mm2 | 1. | 1. | 13 | 1 | 1 | 13
1.1.14 | Final modulus of elasticity | 58600 |  | N/mm2 | 1. | 1. | 14 | 1 | 1 | 14
1.1.15 | Coefficient of linear expansion | 23 |  | Per 10-6 Co | 1. | 1. | 15 | 1 | 1 | 15
1.1.16 | Length of conductor per drum | Bidder to state |  | m | 1. | 1. | 16 | 1 | 1 | 16
1.1.17 | Gross weight per drum | <1300 |  | kg | 1. | 1. | 17 | 1 | 1 | 17
1.1.18 | Material of drum | Wood/Steel |  | - | 1. | 1. | 18 | 1 | 1 | 18
1.1.19 | Diameter of drum core | Bidder to state |  | mm | 1. | 1. | 19 | 1 | 1 | 19
1.1.20 | Total diameter of drum | Bidder to state |  | mm | 1. | 1. | 20 | 1 | 1 | 20
1.1.21 | Total width of drum | Bidder to state |  | mm | 1. | 1. | 21 | 1 | 1 | 21
1.1.22 | Materials used for termite proofing of drums | IEC 60502 Clause 5.4 ISO 22190:2020 |  | - | 1. | 1. | 22 | 1 | 1 | 22
1.1.23 | Whether all tests in relevant standard specification will be carried out? | Yes |  | - | 1. | 1. | 23 | 1 | 1 | 23
[8 empty] | 1 | 1 | 24 | tom rad
1.2. | LGKK-600 |  |  |  | 1. | 2. |  | 1 | 2 | 25 | R2
[8 empty] | 1 | 2 | 26 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 2 | 27 | R3
1.2.1 | Manufacturer | Bidder to state |  |  | 1. | 2. | 1 | 1 | 2 | 1
1.2.2 | Manufacturer's type and reference | Bidder to state |  |  | 1. | 2. | 2 | 1 | 2 | 2
1.2.3 | Country of origin | Bidder to state |  |  | 1. | 2. | 3 | 1 | 2 | 3
1.2.4 | Description | AAC |  |  | 1. | 2. | 4 | 1 | 2 | 4
1.2.5 | Standard specification applied | IEC 61089, EN 50341-1, 50341-1, 50852, 50182, 60889, BS 215 |  |  | 1. | 2. | 5 | 1 | 2 | 5
1.2.6 | Aluminum strands | 35 |  | Nos. | 1. | 2. | 6 | 1 | 2 | 6
1.2.7 | Aluminum strands diameter | 3 |  | mm | 1. | 2. | 7 | 1 | 2 | 7
1.2.8 | Overall conductor diameter | 51 |  | mm | 1. | 2. | 8 | 1 | 2 | 8
1.2.9 | Aluminium conductor cross section | 587 |  | mm2 | 1. | 2. | 9 | 1 | 2 | 9
1.2.10 | Ultimate breaking strength of stranded conductor | 149 |  | kN | 1. | 2. | 10 | 1 | 2 | 10
1.2.11 | DC resistance of conductor at 20°C (Guarantee Value) | 0.0397 |  | ohms/km | 1. | 2. | 11 | 1 | 2 | 11
1.2.12 | Weight per km of conductor | 2520 |  | Kg | 1. | 2. | 12 | 1 | 2 | 12
1.2.13 | Initial modulus of elasticity | Bidder to state |  | N/mm2 | 1. | 2. | 13 | 1 | 2 | 13
1.2.14 | Final modulus of elasticity | Bidder to state |  | N/mm2 | 1. | 2. | 14 | 1 | 2 | 14
1.2.15 | Coefficient of linear expansion | 19.91 |  | Per 10-6 Co | 1. | 2. | 15 | 1 | 2 | 15
1.2.16 | Length of conductor per drum | Bidder to state |  | m | 1. | 2. | 16 | 1 | 2 | 16
1.2.17 | Gross weight per drum | <1300 |  | kg | 1. | 2. | 17 | 1 | 2 | 17
1.2.18 | Material of drum | Wood/Steel |  | - | 1. | 2. | 18 | 1 | 2 | 18
1.2.19 | Diameter of drum core | Bidder to state |  | mm | 1. | 2. | 19 | 1 | 2 | 19
1.2.20 | Total diameter of drum | Bidder to state |  | mm | 1. | 2. | 20 | 1 | 2 | 20
1.2.21 | Total width of drum | Bidder to state |  | mm | 1. | 2. | 21 | 1 | 2 | 21
1.2.22 | Materials used for termite proofing of drums | IEC 60502 Clause 5.4 ISO 22190:2020 |  | - | 1. | 2. | 22 | 1 | 2 | 22
1.2.23 | Whether all tests in relevant standard specification will be carried out? | Yes |  | - | 1. | 2. | 23 | 1 | 2 | 23
[8 empty] | 1 | 2 | 24 | tom rad
1.3. | Bison |  |  |  | 1. | 3. |  | 1 | 3 | 25 | R2
[8 empty] | 1 | 3 | 26 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 3 | 27 | R3
1.3.1 | Manufacturer | Bidder to state |  |  | 1. | 3. | 1 | 1 | 3 | 1
1.3.2 | Manufacturer's type and reference | Bidder to state |  |  | 1. | 3. | 2 | 1 | 3 | 2
1.3.3 | Country of origin | Bidder to state |  |  | 1. | 3. | 3 | 1 | 3 | 3
1.3.4 | Description | ASCR |  |  | 1. | 3. | 4 | 1 | 3 | 4
1.3.5 | Standard specification applied | IEC 61089, EN 50341-1, 50341-1, 50852, 50182, 60889, BS 215 |  |  | 1. | 3. | 5 | 1 | 3 | 5
1.3.6 | Aluminum strands | 54 |  | Nos. | 1. | 3. | 6 | 1 | 3 | 6
1.3.7 | Aluminum strands diameter | 3 |  | mm | 1. | 3. | 7 | 1 | 3 | 7
1.3.8 | Steel strands | 7 |  | Nos. | 1. | 3. | 8 | 1 | 3 | 8
1.3.8 | Steel strands diameter | 3 |  | mm | 1. | 3. | 8 | 1 | 3 | 8
1.3.9 | Overall conductor diameter | 27 |  | mm | 1. | 3. | 9 | 1 | 3 | 9
1.3.10 | Aluminium conductor cross section | 381.7 |  | mm2 | 1. | 3. | 10 | 1 | 3 | 10
1.3.11 | Steel conductor cross section | 49.5 |  | mm2 | 1. | 3. | 11 | 1 | 3 | 11
1.3.12 | Ultimate breaking strength of stranded conductor | 120 |  | kN | 1. | 3. | 12 | 1 | 3 | 12
1.3.13 | DC resistance of conductor at 20°C (Guarantee Value) | 0.07573 |  | ohms/km | 1. | 3. | 13 | 1 | 3 | 13
1.3.14 | Weight per km of conductor | 1444 |  | Kg | 1. | 3. | 14 | 1 | 3 | 14
1.3.15 | Initial modulus of elasticity | 47600 |  | N/mm2 | 1. | 3. | 15 | 1 | 3 | 15
1.3.16 | Final modulus of elasticity | 73200 |  | N/mm2 | 1. | 3. | 16 | 1 | 3 | 16
1.3.17 | Coefficient of linear expansion | 19.91 |  | Per 10-6 Co | 1. | 3. | 17 | 1 | 3 | 17
1.3.18 | Permanent elongation due to creep after 10 years | Bidder to state |  | m/m | 1. | 3. | 18 | 1 | 3 | 18
1.3.19 | Length of conductor per drum | Bidder to state |  | m | 1. | 3. | 19 | 1 | 3 | 19
1.3.20 | Gross weight per drum | Bidder to state |  | kg | 1. | 3. | 20 | 1 | 3 | 20
1.3.21 | Material of drum | Wood/Steel |  | - | 1. | 3. | 21 | 1 | 3 | 21
1.3.22 | Diameter of drum core | Bidder to state |  | mm | 1. | 3. | 22 | 1 | 3 | 22
1.3.23 | Total diameter of drum | Bidder to state |  | mm | 1. | 3. | 23 | 1 | 3 | 23
1.3.24 | Total width of drum | Bidder to state |  | mm | 1. | 3. | 24 | 1 | 3 | 24
1.3.25 | Materials used for termite proofing of drums | IEC 60502 Clause 5.4 ISO 22190:2020 |  | - | 1. | 3. | 25 | 1 | 3 | 25
1.3.26 | Whether all tests in relevant standard specification will be carried out? | Yes |  | - | 1. | 3. | 26 | 1 | 3 | 26
[8 empty] | 1 | 3 | 27 | tom rad
1.4. | ACS 7/4.11 Shield Wire |  |  |  | 1 | 4 |  | 1 | 4 | 28 | R2
[8 empty] | 1 | 4 | 29 | tom rad
Item | Description | Required | Offered | Unit |  |  |  | 1 | 4 | 30 | R3
1.4.1 | Description | ACS 7/4.11 AWG |  |  | 1 | 4 | 1 | 1 | 4 | 1
1.4.2 | Standard | ASTM B415, ASTM B416 |  |  | 1 | 4 | 2 | 1 | 4 | 2
1.4.3 | Minimum UTS | 101 |  | kN | 1 | 4 | 3 | 1 | 4 | 3
1.4.4 | Total cross section | 93.1 |  | mm2 | 1 | 4 | 4 | 1 | 4 | 4
1.4.5 | Number of wires | 7 |  | nos | 1 | 4 | 5 | 1 | 4 | 5
1.4.6 | Wire diameter | 4.11 |  | mm | 1 | 4 | 6 | 1 | 4 | 6
1.4.7 | Overall diameter | 12.3 |  | mm | 1 | 4 | 7 | 1 | 4 | 7
1.4.8 | Ultimate tensile strength | 101.14 |  | kN | 1 | 4 | 8 | 1 | 4 | 8
1.4.9 | Modulus of elasticity | 158620 |  | N/mm² | 1 | 4 | 9 | 1 | 4 | 9
1.4.10 | Coefficient of linear thermal expansion | 13 |  | 10-6/°C | 1 | 4 | 10 | 1 | 4 | 10
1.4.11 | DC resistance at 20°C | 0.922 |  | Ohms/km | 1 | 4 | 11 | 1 | 4 | 11
1.4.12 | Weight | 619 |  | kg/km | 1 | 4 | 12 | 1 | 4 | 12
[8 empty] | 1 | 4 | 13 | tom rad
1.5. | Tension insulator set |  |  |  | 1 | 5 |  | 1 | 5 | 14 | R2
[8 empty] | 1 | 5 | 15 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 5 | 16 | R3
1.5.1 | Manufacturer | Bidder to state |  | - | 1 | 5 | 1 | 1 | 5 | 1
1.5.2 | Manufacturer's type and reference | Bidder to state |  | - | 1. | 5. | 2 | 1 | 5 | 2
1.5.3 | Country of origin | Bidder to state |  | - | 1. | 5. | 3 | 1 | 5 | 3
1.5.4 | Description | Brown glased porcelin |  | - | 1. | 5. | 4 | 1 | 5 | 4
1.5.5 | Standard specification applied | IEC 60120, 60305, 60372, 60375, 60383 |  | - | 1. | 5. | 5 | 1 | 5 | 5
1.5.6 | Nominal voltage | 330/132 |  | kV | 1. | 5. | 6 | 1 | 5 | 6
1.5.7 | Highest system voltage | 362/145 |  | kV | 1. | 5. | 7 | 1 | 5 | 7
1.5.8 | Nominal disc diameter | 280 |  | mm | 1. | 5. | 8 | 1 | 5 | 8
1.5.9 | Related electro-mechanical strength | 160 |  | kN | 1. | 5. | 9 | 1 | 5 | 9
1.5.10 | Sacrificial zinc sleeve on pin | Yes |  | - | 1. | 5. | 10 | 1 | 5 | 10
1.5.11 | Mechanicalroutine test load | 80 |  | kN | 1. | 5. | 11 | 1 | 5 | 11
1.5.12 | Lightning dry impulse withstand | 75 |  | kV | 1. | 5. | 12 | 1 | 5 | 12
1.5.13 | Short duration dry power frequency withstand voltage | 110 |  | kV | 1. | 5. | 13 | 1 | 5 | 13
1.5.14 | Overall creepage distance for a set at 330/132 kV | 13,316 / 5,334 |  | mm | 1. | 5. | 14 | 1 | 5 | 14
1.5.15 | Number of strings per phase | 1 |  | No. | 1. | 5. | 15 | 1 | 5 | 15
1.5.16 | Lightning impulse withstand voltage pos/neg 330/132kV | 1245/735 |  | kV | 1. | 5. | 16 | 1 | 5 | 16
1.5.17 | Switching impulse withstand wer voltage 330/132kV | 1080/356 |  | kV | 1. | 5. | 17 | 1 | 5 | 17
1.5.18 | Wet power frequency withstand Voltage 330/132kV | 580/311 |  | kV | 1. | 5. | 18 | 1 | 5 | 18
1.5.19 | Corona Inception Voltage | >230 |  | kV | 1. | 5. | 19 | 1 | 5 | 19
1.5.20 | Radio Interference Voltage | 220 |  | kV | 1. | 5. | 20 | 1 | 5 | 20
1.5.21 | Radio Interference | 45 |  | dB/1µV | 1. | 5. | 21 | 1 | 5 | 21
1.5.22 | Electro-mechanical failing load | 2*160 |  | kN | 1. | 5. | 22 | 1 | 5 | 22
1.5.23 | Shielding Rings | Yes |  | - | 1. | 5. | 23 | 1 | 5 | 23
1.5.24 | Grading Rings | Yes |  | - | 1. | 5. | 24 | 1 | 5 | 24
1.5.25 | Length of complete set including fittings | Bidder to state |  | mm | 1. | 5. | 25 | 1 | 5 | 25
1.5.26 | Weight of complete set | Bidder to state |  | kg | 1. | 5. | 26 | 1 | 5 | 26
1.5.27 | Corona voltage | Bidder to state |  |  | 1. | 5. | 27 | 1 | 5 | 27
[8 empty] | 1 | 5 | 28 | tom rad
1.6. | Suspension insulator set |  |  |  | 1. | 6. |  | 1 | 6 | 29 | R2
[8 empty] | 1 | 6 | 30 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 6 | 31 | R3
1.6.1 | Manufacturer | Bidder to state |  | - | 1. | 6. | 1 | 1 | 6 | 1
1.6.2 | Manufacturer's type and reference | Bidder to state |  | - | 1. | 6. | 2 | 1 | 6 | 2
1.6.3 | Country of origin | Bidder to state |  | - | 1. | 6. | 3 | 1 | 6 | 3
1.6.4 | Description | Brown glased porcelin |  | - | 1. | 6. | 4 | 1 | 6 | 4
1.6.5 | Standard specification applied | IEC 60120, 60305, 60372, 60375, 60383 |  | - | 1. | 6. | 5 | 1 | 6 | 5
1.6.6 | Nominal voltage | 330/132 |  | kV | 1. | 6. | 6 | 1 | 6 | 6
1.6.7 | Highest system voltage | 362/145 |  | kV | 1. | 6. | 7 | 1 | 6 | 7
1.6.8 | Nominal disc diameter | 280 |  | mm | 1. | 6. | 8 | 1 | 6 | 8
1.6.9 | Related electro-mechanical strength | 160 |  | kN | 1. | 6. | 9 | 1 | 6 | 9
1.6.10 | Sacrificial zinc sleeve on pin | Yes |  | - | 1. | 6. | 10 | 1 | 6 | 10
1.6.11 | Mechanicalroutine test load | 80 |  | kN | 1. | 6. | 11 | 1 | 6 | 11
1.6.12 | Lightning dry impulse withstand | 75 |  | kV | 1. | 6. | 12 | 1 | 6 | 12
1.6.13 | Short duration dry power frequency withstand voltage | 110 |  | kV | 1. | 6. | 13 | 1 | 6 | 13
1.6.14 | Overall creepage distance for a set at 330/132/66 kV | 13,316 / 5,334 |  | mm | 1. | 6. | 14 | 1 | 6 | 14
1.6.15 | Number of strings per phase | 1 |  | - | 1. | 6. | 15 | 1 | 6 | 15
1.6.16 | Lightning impulse withstand voltage pos/neg 330/132kV | 1245/735 |  | kV | 1. | 6. | 16 | 1 | 6 | 16
1.6.17 | Switching impulse withstand wer voltage 330/132kV | 1080/356 |  | kV | 1. | 6. | 17 | 1 | 6 | 17
1.6.18 | Wet power frequency withstand Voltage 330/132kV | 580/311 |  | kV | 1. | 6. | 18 | 1 | 6 | 18
1.6.19 | Corona Inception Voltage | >230 |  | kV | 1. | 6. | 19 | 1 | 6 | 19
1.6.20 | Radio Interference Voltage | 220 |  | kV | 1. | 6. | 20 | 1 | 6 | 20
1.6.21 | Radio Interference | 45 |  | dB/1µV | 1. | 6. | 21 | 1 | 6 | 21
1.6.22 | Electro-mechanical failing load | 2*160 |  | kN | 1. | 6. | 22 | 1 | 6 | 22
1.6.23 | Shielding Rings | Yes |  | - | 1. | 6. | 23 | 1 | 6 | 23
1.6.24 | Grading Rings | Yes |  | - | 1. | 6. | 24 | 1 | 6 | 24
1.6.25 | Length of complete set including fittings | Bidder to state |  | mm | 1. | 6. | 25 | 1 | 6 | 25
1.6.26 | Weight of complete set | Bidder to state |  | kg | 1. | 6. | 26 | 1 | 6 | 26
1.6.27 | Corona voltage | Bidder to state |  |  | 1. | 6. | 27 | 1 | 6 | 27
[8 empty] | 1 | 6 | 28 | tom rad
1.7. | Post insulator |  |  |  | 1. | 7. |  | 1 | 7 | 29 | R2
[8 empty] | 1 | 7 | 30 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 7 | 31 | R3
1.7.1 | Manufacturer | Bidder to state |  | - | 1. | 7. | 1 | 1 | 7 | 1
1.7.2 | Manufacturer's type and reference | Bidder to state |  | - | 1. | 7. | 2 | 1 | 7 | 2
1.7.3 | Country of origin | Bidder to state |  | - | 1. | 7. | 3 | 1 | 7 | 3
1.7.4 | Description | Brown porcelin |  | - | 1. | 7. | 4 | 1 | 7 | 4
1.7.5 | Standard specification applied | IEC60168, 60273 |  | - | 1. | 7. | 5 | 1 | 7 | 5
1.7.6 | Lightning impulse withstand 330/132 kV | 1245/735 |  | kV | 1. | 7. | 6 | 1 | 7 | 6
1.7.7 | Short duration power frequency withstand voltage 330/132 kV | 580/311 |  | kV | 1. | 7. | 7 | 1 | 7 | 7
1.7.8 | Overall creepage distance for a set at 330/132 kV | 13,316 / 5,334 |  | mm | 1. | 7. | 8 | 1 | 7 | 8
1.7.9 | Specified Mechanical Failing Load | Bidder to state |  | kN | 1. | 7. | 9 | 1 | 7 | 9
1.7.10 | Hight | Bidder to state |  | mm | 1. | 7. | 10 | 1 | 7 | 10
1.7.11 | Weight | Bidder to state |  | kg | 1. | 7. | 11 | 1 | 7 | 11
[8 empty] | 1 | 7 | 12 | tom rad
1.8. | Hardware and fitting for phase conductor |  |  |  | 1. | 8. |  | 1 | 8 | 13 | R2
[8 empty] | 1 | 8 | 14 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 8 | 15 | R3
1.8.1 | Manufacturer of tension clamps | To be stated by Bidder |  | - | 1. | 8. | 1 | 1 | 8 | 1
1.8.2 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 8. | 2 | 1 | 8 | 2
1.8.3 | Country of origin | To be stated by Bidder |  | - | 1. | 8. | 3 | 1 | 8 | 3
1.8.4 | Description | To be stated by Bidder |  | - | 1. | 8. | 4 | 1 | 8 | 4
1.8.5 | Standard specification applied | EN 50341 |  | - | 1. | 8. | 5 | 1 | 8 | 5
1.8.6 | Type of suspension clamps | To be stated by Bidder |  | - | 1. | 8. | 6 | 1 | 8 | 6
1.8.7 | Breaking strength of suspension clamps | 120 |  | kN | 1. | 8. | 7 | 1 | 8 | 7
1.8.8 | Slipping of suspension clamps (>95% of conductor ultimate strength) | To be stated by Bidder |  | kN | 1. | 8. | 8 | 1 | 8 | 8
1.8.9 | Manufacturer of tension joints | To be stated by Bidder |  | - | 1. | 8. | 9 | 1 | 8 | 9
1.8.10 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 8. | 10 | 1 | 8 | 10
1.8.11 | Country of origin | To be stated by Bidder |  | - | 1. | 8. | 11 | 1 | 8 | 11
1.8.12 | Description | To be stated by Bidder |  | - | 1. | 8. | 12 | 1 | 8 | 12
1.8.13 | Standard specification applied | EN 61284, EN 61897 |  | - | 1. | 8. | 13 | 1 | 8 | 13
1.8.14 | Single or two piece type of tension joint | To be stated by Bidder |  | - | 1. | 8. | 14 | 1 | 8 | 14
1.8.15 | Tensile strength of tension joint | To be stated by Bidder |  | kN | 1. | 8. | 15 | 1 | 8 | 15
1.8.16 | Slipping strength of tension joint | To be stated by Bidder |  | kN | 1. | 8. | 16 | 1 | 8 | 16
1.8.17 | Manufacturer of repair sleeves | To be stated by Bidder |  | - | 1. | 8. | 17 | 1 | 8 | 17
1.8.18 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 8. | 18 | 1 | 8 | 18
1.8.19 | Country of origin | To be stated by Bidder |  | - | 1. | 8. | 19 | 1 | 8 | 19
1.8.20 | Description | To be stated by Bidder |  | - | 1. | 8. | 20 | 1 | 8 | 20
1.8.21 | Standard specification applied | IEC, EN |  | - | 1. | 8. | 21 | 1 | 8 | 21
1.8.22 | Type of repair sleeve | To be stated by Bidder |  | - | 1. | 8. | 22 | 1 | 8 | 22
1.8.23 | Manufacturer of armour rods | To be stated by Bidder |  | - | 1. | 8. | 23 | 1 | 8 | 23
1.8.24 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 8. | 24 | 1 | 8 | 24
1.8.25 | Country of origin | To be stated by Bidder |  | - | 1. | 8. | 25 | 1 | 8 | 25
1.8.26 | Description | To be stated by Bidder |  | - | 1. | 8. | 26 | 1 | 8 | 26
1.8.27 | Standard specification applied | IEC, EN |  | - | 1. | 8. | 27 | 1 | 8 | 27
1.8.28 | Type of armour rods | To be stated by Bidder |  | - | 1. | 8. | 28 | 1 | 8 | 28
1.8.29 | Material of armour rods | To be stated by Bidder |  | - | 1. | 8. | 29 | 1 | 8 | 29
1.8.30 | Dimension of armour rods | To be stated by Bidder |  | - | 1. | 8. | 30 | 1 | 8 | 30
1.8.31 | Manufacturer of vibration dampers | To be stated by Bidder |  | - | 1. | 8. | 31 | 1 | 8 | 31
1.8.32 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 8. | 32 | 1 | 8 | 32
1.8.33 | Country of origin | To be stated by Bidder |  | - | 1. | 8. | 33 | 1 | 8 | 33
1.8.34 | Description | To be stated by Bidder |  | - | 1. | 8. | 34 | 1 | 8 | 34
1.8.35 | Standard specification applied | IEC, EN |  | - | 1. | 8. | 35 | 1 | 8 | 35
1.8.36 | Type of vibration damper | To be stated by Bidder |  | - | 1. | 8. | 36 | 1 | 8 | 36
1.8.37 | Weight of vibration damper | To be stated by Bidder |  | kg | 1. | 8. | 37 | 1 | 8 | 37
1.8.38 | Type of attachment of vibration damper | To be stated by Bidder |  | - | 1. | 8. | 38 | 1 | 8 | 38
1.8.39 | Whether all fitting suplied are hot dip galvanised | Yes |  | - | 1. | 8. | 39 | 1 | 8 | 39
[8 empty] | 1 | 8 | 40 | tom rad
1.9. | Hardware and fitting for Earth-wire |  |  |  | 1. | 9. |  | 1 | 9 | 41 | R2
[8 empty] | 1 | 9 | 42 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 9 | 43 | R3
1.9.1 | Manufacturer of tension clamps | To be stated by Bidder |  | - | 1. | 9. | 1 | 1 | 9 | 1
1.9.2 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 9. | 2 | 1 | 9 | 2
1.9.3 | Country of origin | To be stated by Bidder |  | - | 1. | 9. | 3 | 1 | 9 | 3
1.9.4 | Description | To be stated by Bidder |  | - | 1. | 9. | 4 | 1 | 9 | 4
1.9.5 | Standard specification applied | IEC, EN |  | - | 1. | 9. | 5 | 1 | 9 | 5
1.9.6 | Type of tension clamps | To be stated by Bidder |  | - | 1. | 9. | 6 | 1 | 9 | 6
1.9.7 | Breaking strength of tension clamps | To be stated by Bidder |  | kN | 1. | 9. | 7 | 1 | 9 | 7
1.9.8 | Slipping of tension clamps | To be stated by Bidder |  | kN | 1. | 9. | 8 | 1 | 9 | 8
1.9.9 | Manufacturer of repair sleeves | To be stated by Bidder |  | - | 1. | 9. | 9 | 1 | 9 | 9
1.9.10 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 9. | 10 | 1 | 9 | 10
1.9.11 | Country of origin | To be stated by Bidder |  | - | 1. | 9. | 11 | 1 | 9 | 11
1.9.12 | Description | To be stated by Bidder |  | - | 1. | 9. | 12 | 1 | 9 | 12
1.9.13 | Standard specification applied | IEC, EN |  | - | 1. | 9. | 13 | 1 | 9 | 13
1.9.14 | Type of repair sleeve | To be stated by Bidder |  | - | 1. | 9. | 14 | 1 | 9 | 14
1.9.15 | Manufacturer of armour rods | To be stated by Bidder |  | - | 1. | 9. | 15 | 1 | 9 | 15
1.9.16 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 9. | 16 | 1 | 9 | 16
1.9.17 | Country of origin | To be stated by Bidder |  | - | 1. | 9. | 17 | 1 | 9 | 17
1.9.18 | Description | To be stated by Bidder |  | - | 1. | 9. | 18 | 1 | 9 | 18
1.9.19 | Standard specification applied | IEC, EN |  | - | 1. | 9. | 19 | 1 | 9 | 19
1.9.20 | Type of armour rods | To be stated by Bidder |  | - | 1. | 9. | 20 | 1 | 9 | 20
1.9.21 | Material of armour rods | To be stated by Bidder |  | - | 1. | 9. | 21 | 1 | 9 | 21
1.9.22 | Dimension of armour rods | To be stated by Bidder |  | - | 1. | 9. | 22 | 1 | 9 | 22
1.9.23 | Manufacturer of vibration dampers | To be stated by Bidder |  | - | 1. | 9. | 23 | 1 | 9 | 23
1.9.24 | Manufacturer's type and reference | To be stated by Bidder |  | - | 1. | 9. | 24 | 1 | 9 | 24
1.9.25 | Country of origin | To be stated by Bidder |  | - | 1. | 9. | 25 | 1 | 9 | 25
1.9.26 | Description | To be stated by Bidder |  | - | 1. | 9. | 26 | 1 | 9 | 26
1.9.27 | Standard specification applied | IEC, EN |  | - | 1. | 9. | 27 | 1 | 9 | 27
1.9.28 | Type of vibration damper | To be stated by Bidder |  | - | 1. | 9. | 28 | 1 | 9 | 28
1.9.29 | Weight of vibration damper | To be stated by Bidder |  | kg | 1. | 9. | 29 | 1 | 9 | 29
1.9.30 | Type of attachment of vibration damper | To be stated by Bidder |  | - | 1. | 9. | 30 | 1 | 9 | 30
1.9.31 | Whether all fitting suplied are hot dip galvanised | Yes |  | - | 1. | 9. | 31 | 1 | 9 | 31
[8 empty] | 1 | 9 | 32 | tom rad
1.10. | Earthing Conductor for Substation |  |  |  | 1. | 10. |  | 1 | 10 | 33 | R2
[8 empty] | 1 | 9 | 33 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 10 | 34 | R3
1.10.1 | Material | Electrolytic copper (≥99.9%) |  |  | 1. | 10. | 1 | 1 | 10 | 1
1.10.2 | Conductor Type | Bare copper earth wire |  |  | 1. | 10. | 2 | 1 | 10 | 2
1.10.3 | Standard Compliance | IEC 62561-1, IEEE 80, BS 7430 |  |  | 1. | 10. | 3 | 1 | 10 | 3
1.10.4 | Minimum Cross-Section | Calculated per fault current (min. 120mm²) |  | mm² | 1. | 10. | 4 | 1 | 10 | 4
1.10.5 | Maximum Resistance (entire grid) | ≤0.5 |  | Ω | 1. | 10. | 5 | 1 | 10 | 5
1.10.6 | Fault Current Capacity | 10kA for 3s (250°C surface) |  | kA/s | 1. | 10. | 6 | 1 | 10 | 6
1.10.7 | Buried Conductor Temp Limit | 400°C (short-term) |  | °C | 1. | 10. | 7 | 1 | 10 | 7
1.10.8 | Conductor Spacing | Optimized for step/touch potential (per IEEE 80) |  | m | 1. | 10. | 8 | 1 | 10 | 8
1.10.9 | Connections | Exothermic welding (UG), compression lugs (AG) |  |  | 1. | 10. | 9 | 1 | 10 | 9
1.10.10 | Welding Standard | ASTM B828 / IEC 62561-1 |  |  | 1. | 10. | 10 | 1 | 10 | 10
1.10.11 | Corrosion Protection | Bitumen coating (UG), anti-oxidant paste (AG) |  |  | 1. | 10. | 11 | 1 | 10 | 11
1.10.12 | Riser Connections | Dual 70mm² min. per structure |  |  | 1. | 10. | 12 | 1 | 10 | 12
1.10.13 | Ground Rods | Copper-bonded steel, Ø19mm x 3m |  |  | 1. | 10. | 13 | 1 | 10 | 13
1.10.14 | Rod Spacing | min. 3 |  | m | 1. | 10. | 14 | 1 | 10 | 14
1.10.15 | Grid Perimeter Conductors | 70mm² stranded |  |  | 1. | 10. | 15 | 1 | 10 | 15
1.10.16 | Concrete Embedment | 100mm concrete cover |  | mm | 1. | 10. | 16 | 1 | 10 | 16
1.10.17 | Wall Penetrations | PVC sleeve + hydrophobic seal |  |  | 1. | 10. | 17 | 1 | 10 | 17
1.10.18 | Step/Touch Potential | Complies with IEEE 80 (fault duration 0.5s) |  | V | 1. | 10. | 18 | 1 | 10 | 18
1.10.19 | GPR Limit | ≤5kV under worst-case fault |  | kV | 1. | 10. | 19 | 1 | 10 | 19
1.10.20 | X/R Ratio | 10 (system specific) |  |  | 1. | 10. | 20 | 1 | 10 | 20
1.10.21 | Auto-Reclose Consideration | 1s delay accounted in design |  | s | 1. | 10. | 21 | 1 | 10 | 21
1.10.22 | Soil Resistivity Testing | 4-point Wenner method (IEC 60364-6) |  | Ω-m | 1. | 10. | 22 | 1 | 10 | 22
1.10.23 | Temporary Earth Points | M10 brass studs |  |  | 1. | 10. | 23 | 1 | 10 | 23
1.10.24 | Warranty | 20 years against corrosion |  | years | 1. | 10. | 24 | 1 | 10 | 24
[8 empty] | 1 | 10 | 25 | tom rad
1.11. | Lightning Protection |  |  |  | 1. | 11. |  | 1 | 11 | 26 | R2
[8 empty] | 1 | 10 | 26 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 1 | 11 | 27 | R3
1.11.1 | Type | Lightning Mast |  |  | 1. | 11. | 1 | 1 | 11 | 1
1.11.2 | Material | Stainless steel / Galvanized steel |  |  | 1. | 11. | 2 | 1 | 11 | 2
1.11.3 | Standard Compliance | IEC 62305/IEEE Std 998 |  |  | 1. | 11. | 3 | 1 | 11 | 3
1.11.4 | Mast Type | Tubular Steel / Lattice Steel / Composite |  |  | 1. | 11. | 4 | 1 | 11 | 4
1.11.5 | Mast Height (m) | Required height based on rolling-sphere analysis |  |  | 1. | 11. | 5 | 1 | 11 | 5
1.11.6 | Minimum Tip Diameter | Suitable for effective lightning interception |  |  | 1. | 11. | 6 | 1 | 11 | 6
1.11.7 | Base Plate Dimensions | To be provided by bidder |  |  | 1. | 11. | 7 | 1 | 11 | 7
1.11.8 | Wind Load Design | As per site conditions (provide calculations) |  |  | 1. | 11. | 8 | 1 | 11 | 8
1.11.9 | Corrosion Protection | HDG (Hot-dip galvanized) / Painted / Other |  |  | 1. | 11. | 9 | 1 | 11 | 9
1.11.10 | Mast Foundation Type | Pad & pedestal / Concrete block / Anchor bolts |  |  | 1. | 11. | 10 | 1 | 11 | 10
1.11.11 | Mast Earthing | Directly bonded to earthing grid |  |  | 1. | 11. | 11 | 1 | 11 | 11
1.11.12 | Minimum Cross-Section |  |  | mm2 | 1. | 11. | 12 | 1 | 11 | 12
1.11.13 | Type | Gantry Mounted Spike |  |  | 1. | 11. | 13 | 1 | 11 | 13
1.11.14 | Spike Length (mm) | Typically 500–1500 mm |  | mm | 1. | 11. | 14 | 1 | 11 | 14
1.11.15 | Material | Stainless steel / Galvanized steel |  |  | 1. | 11. | 15 | 1 | 11 | 15
1.11.16 | Mounting Arrangement | Mechanical & electrical bonding to gantry steel |  |  | 1. | 11. | 16 | 1 | 11 | 16
1.11.17 | Positioning | Highest elevation of gantry structure |  |  | 1. | 11. | 17 | 1 | 11 | 17
1.11.18 | Protection Zone | Must meet rolling-sphere and protective-angle criteria |  |  | 1. | 11. | 18 | 1 | 11 | 18
1.11.19 | Gantry-mounted spikes integrated into shielding model | Yes |  |  | 1. | 11. | 19 | 1 | 11 | 19
1.11.20 | Down-conductor Type | Galvanized steel / Copper / Structural steel path |  |  | 1. | 11. | 20 | 1 | 11 | 20
1.11.21 | Cross-sectional Area | Adequate for lightning current |  |  | 1. | 11. | 21 | 1 | 11 | 21
1.11.22 | Bonding to Mast / Spike | Low-impedance permanent bonding |  |  | 1. | 11. | 22 | 1 | 11 | 22
1.11.23 | Bonding to Earth Grid | Stainless/Galvanized clamps; exothermic weld preferred |  |  | 1. | 11. | 23 | 1 | 11 | 23
1.11.24 | Separation Distances | As per internal LPS requirements |  |  | 1. | 11. | 24 | 1 | 11 | 24
1.11.25 | Termination | Direct integration into main earth grid |  |  | 1. | 11. | 25 | 1 | 11 | 25
1.11.26 | Earth Resistance Target | <0.5 |  | Ω | 1. | 11. | 26 | 1 | 11 | 26
[8 empty] | 1 | 9 | 32 | tom rad
2. | 330 kV Equipment |  |  |  | 2. |  |  | 2 | 9 | 33 | R1
2.1. | 330 kV Circuit Breaker |  |  |  | 2. | 1. |  | 2 | 1 |  | R2
[8 empty] | 2 | 1 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 2 | 1 | 1 | R3
2.1.1 | Maker’s name | To be stated by Bidder |  | - | 2. | 1. | 1 | 2 | 1 | 1
2.1.2 | Maker’s type and reference | To be stated by Bidder |  | - | 2. | 1. | 2 | 2 | 1 | 2
2.1.3 | Country of origin | To be stated by Bidder |  | - | 2. | 1. | 3 | 2 | 1 | 3
2.1.4 | Description | To be stated by Bidder |  | - | 2. | 1. | 4 | 2 | 1 | 4
2.1.5 | Type | SF6 |  | - | 2. | 1. | 5 | 2 | 1 | 5
2.1.6 | Number of poles | 3 |  | Nos. | 2. | 1. | 6 | 2 | 1 | 6
2.1.7 | Single/three-phase operation | Single-phase |  | - | 2. | 1. | 7 | 2 | 1 | 7
2.1.8 | Type test | Authority, year, Doc.no |  | - | 2. | 1. | 8 | 2 | 1 | 8
2.1.9 | Standards | IEC 62271-100 |  | - | 2. | 1. | 9 | 2 | 1 | 9
2.1.10 | Class | Outdoor |  | - | 2. | 1. | 10 | 2 | 1 | 10
2.1.11 | Classification | C2-M2 |  | - | 2. | 1. | 11 | 2 | 1 | 11
2.1.12 | Insulation material | Brown glazed porcelain |  | - | 2. | 1. | 12 | 2 | 1 | 12
2.1.13 | Minimum Creepage distance | 13316.4963 |  | mm | 2. | 1. | 13 | 2 | 1 | 13
2.1.14 | Rated normal current | 4000 |  | A | 2. | 1. | 14 | 2 | 1 | 14
2.1.15 | Rated peak withstand current | 100 |  | kA peak | 2. | 1. | 15 | 2 | 1 | 15
2.1.16 | Rated short-circuit breaking current (3s) | 40 |  | kA | 2. | 1. | 16 | 2 | 1 | 16
2.1.17 | Rated short-time withstand current | 50 |  | kA | 2. | 1. | 17 | 2 | 1 | 17
2.1.18 | First pole to clear factor | 1.3 |  | - | 2. | 1. | 18 | 2 | 1 | 18
2.1.19 | Capacitive voltage factor | 1.2 |  | - | 2. | 1. | 19 | 2 | 1 | 19
2.1.20 | Total break time | ≤45 |  | ms | 2. | 1. | 20 | 2 | 1 | 20
2.1.21 | Maximum closing time | ≤80 |  | ms | 2. | 1. | 21 | 2 | 1 | 21
2.1.22 | Operating mechanism | Spring |  | - | 2. | 1. | 22 | 2 | 1 | 22
2.1.23 | Circuit for point-on wave relay | Yes |  | - | 2. | 1. | 23 | 2 | 1 | 23
2.1.24 | Operating sequence | O-0.3sec-CO-3min-CO |  | - | 2. | 1. | 24 | 2 | 1 | 24
2.1.25 | Interuption chambers in series per phase | 2 |  | Nos. | 2. | 1. | 25 | 2 | 1 | 25
2.1.26 | Interrupting chamber values of distribution elements | To be stated by Bidder |  | pF\Ω | 2. | 1. | 26 | 2 | 1 | 26
2.1.27 | Motor rated voltage | 110 |  | V DC | 2. | 1. | 27 | 2 | 1 | 27
2.1.28 | Operating coils closing / opening | 110 |  | V DC | 2. | 1. | 28 | 2 | 1 | 28
2.1.29 | (Deleted) | - |  | - | 2. | 1. | 29 | 2 | 1 | 29
2.1.30 | Number of trip coils | 2 |  | Nos. | 2. | 1. | 30 | 2 | 1 | 30
2.1.31 | SF6 Block and alarm | Yes |  | - | 2. | 1. | 31 | 2 | 1 | 31
2.1.32 | Auxiliary contacts (8NO+8NC) | 110/7.5 |  | V DC/A | 2. | 1. | 32 | 2 | 1 | 32
2.1.33 | Heating elements with hygrostate/Light/Outlet | 230 |  | V AC | 2. | 1. | 33 | 2 | 1 | 33
[8 empty] | 2 | 1 | 34 | tom rad
2.2. | 330 kV Disconnector Line |  |  |  | 2. | 2. |  | 2 | 2 | 35 | R2
[8 empty] | 2 | 2 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 2 | 2 | 1 | R3
2.2.1 | Maker’s name | To be stated by Bidder |  | - | 2. | 2. | 1 | 2 | 2 | 1
2.2.2 | Maker’s type and reference | To be stated by Bidder |  | - | 2. | 2. | 2 | 2 | 2 | 2
2.2.3 | Country of origin | To be stated by Bidder |  | - | 2. | 2. | 3 | 2 | 2 | 3
2.2.4 | Description | To be stated by Bidder |  | - | 2. | 2. | 4 | 2 | 2 | 4
2.2.5 | Type | Motor operated |  | - | 2. | 2. | 5 | 2 | 2 | 5
2.2.6 | Mode of opening/closing | Three-column, horizontal, center-rotating, double-break type |  | - | 2. | 2. | 6 | 2 | 2 | 6
2.2.7 | Execution of operation | Gang operated 3-phase |  | - | 2. | 2. | 7 | 2 | 2 | 7
2.2.8 | Rated normal current | 3150 |  | A | 2. | 2. | 8 | 2 | 2 | 8
2.2.9 | Rated short-time current (3s) | 40 |  | kA | 2. | 2. | 9 | 2 | 2 | 9
2.2.10 | Insulator | Brown glazed porcelin |  | - | 2. | 2. | 10 | 2 | 2 | 10
2.2.11 | Integrated Earthing Switch; Manually operated | On Line and Reactor disconnectors |  | - | 2. | 2. | 11 | 2 | 2 | 11
2.2.12 | Type test | Authority, year, Doc.no |  | - | 2. | 2. | 12 | 2 | 2 | 12
2.2.13 | Standards | IEC |  | - | 2. | 2. | 13 | 2 | 2 | 13
2.2.14 | Class | Outdoor |  | - | 2. | 2. | 14 | 2 | 2 | 14
2.2.15 | Minimum shear force | To be stated by Bidder |  | kN | 2. | 2. | 15 | 2 | 2 | 15
2.2.16 | Minimum torsional force of rotating insulators | To be stated by Bidder |  | kNm | 2. | 2. | 16 | 2 | 2 | 16
2.2.17 | Minimum creepage distance | 13316.4963 |  | mm | 2. | 2. | 17 | 2 | 2 | 17
2.2.18 | Closing/ opening time | To be stated by Bidder |  | sec | 2. | 2. | 18 | 2 | 2 | 18
2.2.19 | Operation motor rated voltage | 110 |  | V DC | 2. | 2. | 19 | 2 | 2 | 19
2.2.20 | Auxiliary Contacts (8NO+8NC) | 110/7.5 |  | V DC/A | 2. | 2. | 20 | 2 | 2 | 20
2.2.21 | Heating elementswith hygrostat | 230 |  | V AC | 2. | 2. | 21 | 2 | 2 | 21
[8 empty] | 2 | 2 | 22 | tom rad
2.3. | 330 kV Disconnector Transformer |  |  |  | 2. | 3. |  | 2 | 3 | 23 | R2
[8 empty] | 2 | 3 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 2 | 3 | 1 | R3
2.3.1 | Maker’s name | To be stated by Bidder |  | - | 2. | 3. | 1 | 2 | 3 | 1
2.3.2 | Maker’s type and reference | To be stated by Bidder |  | - | 2. | 3. | 2 | 2 | 3 | 2
2.3.3 | Country of origin | To be stated by Bidder |  | - | 2. | 3. | 3 | 2 | 3 | 3
2.3.4 | Description | To be stated by Bidder |  | - | 2. | 3. | 4 | 2 | 3 | 4
2.3.5 | Type | Motor operated |  | - | 2. | 3. | 5 | 2 | 3 | 5
2.3.6 | Mode of opening/closing | Three-column, horizontal, center-rotating, double-break type |  | - | 2. | 3. | 6 | 2 | 3 | 6
2.3.7 | Execution of operation | Gang operated 3-phase |  | - | 2. | 3. | 7 | 2 | 3 | 7
2.3.8 | Rated normal current | 3150 |  | A | 2. | 3. | 8 | 2 | 3 | 8
2.3.9 | Rated short-time current (3s) | 40 |  | kA | 2. | 3. | 9 | 2 | 3 | 9
2.3.10 | Insulator | Brown glazed porcelin |  | - | 2. | 3. | 10 | 2 | 3 | 10
2.3.11 | Integrated Earthing Switch; Manually operated | Yes |  | - | 2. | 3. | 11 | 2 | 3 | 11
2.3.12 | Type test | Authority, year, Doc.no |  | - | 2. | 3. | 12 | 2 | 3 | 12
2.3.13 | Standards | IEC |  | - | 2. | 3. | 13 | 2 | 3 | 13
2.3.14 | Class | Outdoor |  | - | 2. | 3. | 14 | 2 | 3 | 14
2.3.15 | Minimum shear force | To be stated by Bidder |  | kN | 2. | 3. | 15 | 2 | 3 | 15
2.3.16 | Minimum torsional force of rotating insulators | To be stated by Bidder |  | kNm | 2. | 3. | 16 | 2 | 3 | 16
2.3.17 | Minimum creepage distance | 13316.4963 |  | mm | 2. | 3. | 17 | 2 | 3 | 17
2.3.18 | Closing/ opening time | To be stated by Bidder |  | sec | 2. | 3. | 18 | 2 | 3 | 18
2.3.19 | Operation motor rated voltage | 110 |  | V DC | 2. | 3. | 19 | 2 | 3 | 19
2.3.20 | Auxiliary Contacts (8NO+8NC) | 110/7.5 |  | V DC/A | 2. | 3. | 20 | 2 | 3 | 20
2.3.21 | Heating elementswith hygrostat | 230 |  | V AC | 2. | 3. | 21 | 2 | 3 | 21
[8 empty] | 2 | 3 | 22 | tom rad
2.4. | 330 kV Earthing Switch at Disconnector |  |  |  | 2. | 4. |  | 2 | 4 | 23 | R2
[8 empty] | 2 | 4 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 2 | 4 | 1 | R3
2.4.1 | Maker’s name | To be stated by Bidder |  | - | 2. | 4. | 1 | 2 | 4 | 1
2.4.2 | Maker’s type and reference | To be stated by Bidder |  | - | 2. | 4. | 2 | 2 | 4 | 2
2.4.3 | Country of origin | To be stated by Bidder |  | - | 2. | 4. | 3 | 2 | 4 | 3
2.4.4 | Description | At disconnector |  | - | 2. | 4. | 4 | 2 | 4 | 4
2.4.5 | Type | Manual |  | - | 2. | 4. | 5 | 2 | 4 | 5
2.4.6 | Rated short time current (3s) | 40 |  | kA | 2. | 4. | 6 | 2 | 4 | 6
2.4.7 | Type test | Authority, year, Doc.no |  | - | 2. | 4. | 7 | 2 | 4 | 7
2.4.8 | Standards | IEC |  | - | 2. | 4. | 8 | 2 | 4 | 8
2.4.9 | Class | Outdoor |  | - | 2. | 4. | 9 | 2 | 4 | 9
2.4.10 | Auxiliary Contacts (8NO+8NC) | 110/7.5 |  | V DC/A | 2. | 4. | 10 | 2 | 4 | 10
2.4.11 | Heating element with hygrostat | 230 |  | V AC | 2. | 4. | 11 | 2 | 4 | 11
[8 empty] | 2 | 4 | 12 | tom rad
2.5. | 330 kV Current Transformer Line Feeder Bay |  |  |  | 2. | 5. |  | 2 | 5 | 13 | R2
[8 empty] | 2 | 5 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 2 | 5 | 1 | R3
2.5.1 | Maker’s name | To be stated by Bidder |  | - | 2. | 5. | 1 | 2 | 5 | 1
2.5.2 | Maker’s type and reference | To be stated by Bidder |  | - | 2. | 5. | 2 | 2 | 5 | 2
2.5.3 | Country of origin | To be stated by Bidder |  | - | 2. | 5. | 3 | 2 | 5 | 3
2.5.4 | Description | Transmission class |  | - | 2. | 5. | 4 | 2 | 5 | 4
2.5.5 | Type | Outdoor CT |  | - | 2. | 5. | 5 | 2 | 5 | 5
2.5.6 | Type test | Authority, year, Doc.no |  | - | 2. | 5. | 6 | 2 | 5 | 6
2.5.7 | Standards | IEC 61869, BS3938 |  | - | 2. | 5. | 7 | 2 | 5 | 7
2.5.8 | Class | Outdoor |  | - | 2. | 5. | 8 | 2 | 5 | 8
2.5.9 | Creepage distance | 13316.4963 |  | mm | 2. | 5. | 9 | 2 | 5 | 9
2.5.10 | Rated short time thermal current (3s) | 40 |  | kARMS | 2. | 5. | 10 | 2 | 5 | 10
2.5.11 | Number of secondary cores | 7 |  | Nos. | 2. | 5. | 11 | 2 | 5 | 11
2.5.12 | Nominal current | 1200-2400 |  | A | 2. | 5. | 12 | 2 | 5 | 12
2.5.13 | Secondary rated current PX | 1 |  | T | 2. | 5. | 13 | 2 | 5 | 13
2.5.14 | Secondary rated current 5P20 | 1 |  | A | 2. | 5. | 14 | 2 | 5 | 14
2.5.15 | Rating factor | 1.2 |  | - | 2. | 5. | 15 | 2 | 5 | 15
2.5.16 | Rated burden protection core 5P20 | 10 |  | VA | 2. | 5. | 16 | 2 | 5 | 16
2.5.17 | Rated burden measuring core | 5 |  | VA | 2. | 5. | 17 | 2 | 5 | 17
2.5.18 | Protective cores number and class | 1x 5P20 3 x class PX 0.5V/turn |  | - | 2. | 5. | 18 | 2 | 5 | 18
2.5.19 | Measuring cores number and class | 2 x 0.2s Fs<5 |  | - | 2. | 5. | 19 | 2 | 5 | 19
2.5.20 | Spare core | 1 x class PX 0.5V/turn |  | - | 2. | 5. | 20 | 2 | 5 | 20
[8 empty] | 2 | 5 | 21 | tom rad
2.6. | 330 kV Current Transformer - Transformer Bay |  |  |  | 2. | 6. |  | 2 | 6 | 22 | R2
[8 empty] | 2 | 6 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 2 | 6 | 1 | R3
2.6.1 | Maker’s name | To be stated by Bidder |  | - | 2. | 6. | 1 | 2 | 6 | 1
2.6.2 | Maker’s type and reference | To be stated by Bidder |  | - | 2. | 6. | 2 | 2 | 6 | 2
2.6.3 | Country of origin | To be stated by Bidder |  | - | 2. | 6. | 3 | 2 | 6 | 3
2.6.4 | Description | Transmission class |  | - | 2. | 6. | 4 | 2 | 6 | 4
2.6.5 | Type | Outdoor CT |  | - | 2. | 6. | 5 | 2 | 6 | 5
2.6.6 | Type test | Authority, year, Doc.no |  | - | 2. | 6. | 6 | 2 | 6 | 6
2.6.7 | Standards | IEC 61869, BS3938 |  | - | 2. | 6. | 7 | 2 | 6 | 7
2.6.8 | Class | Outdoor |  | - | 2. | 6. | 8 | 2 | 6 | 8
2.6.9 | Creepage distance | 13316.4963 |  | mm | 2. | 6. | 9 | 2 | 6 | 9
2.6.10 | Rated short time thermal current (3s) | 40 |  | kARMS | 2. | 6. | 10 | 2 | 6 | 10
2.6.11 | Number of secondary cores | 7 |  | Nos. | 2. | 6. | 11 | 2 | 6 | 11
2.6.12 | Nominal current | 100-200/300-600 |  | A | 2. | 6. | 12 | 2 | 6 | 12
2.6.13 | Secondary rated current PX | 1 |  | T | 2. | 6. | 13 | 2 | 6 | 13
2.6.14 | Secondary rated current 5P20 | 1 |  | A | 2. | 6. | 14 | 2 | 6 | 14
2.6.15 | Rating factor | 1.2 |  | - | 2. | 6. | 15 | 2 | 6 | 15
2.6.16 | Rated burden protection core 5P20 | 10 |  | VA | 2. | 6. | 16 | 2 | 6 | 16
2.6.17 | Rated burden measuring core | 5 |  | VA | 2. | 6. | 17 | 2 | 6 | 17
2.6.18 | Protective cores number and class | 1x 5P20 3 x class PX 0.5V/turn |  | - | 2. | 6. | 18 | 2 | 6 | 18
2.6.19 | Measuring cores number and class | 2 x 0.2s Fs<5 |  | - | 2. | 6. | 19 | 2 | 6 | 19
2.6.20 | Spare core | 1 x class PX 0.5V/turn |  | - | 2. | 6. | 20 | 2 | 6 | 20
[8 empty] | 2 | 6 | 20 | tom rad
2.7. | 330 kV Capacitive Voltage Transformers |  |  |  | 2. | 7. |  | 2 | 7 | 21 | R2
[8 empty] | 2 | 7 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 2 | 7 | 1 | R3
2.7.1 | Maker’s name | To be stated by Bidder |  | - | 2. | 7. | 1 | 2 | 7 | 1
2.7.2 | Maker’s type and reference | To be stated by Bidder |  | - | 2. | 7. | 2 | 2 | 7 | 2
2.7.3 | Country of origin | To be stated by Bidder |  | - | 2. | 7. | 3 | 2 | 7 | 3
2.7.4 | Description | Outdoor CVT |  | - | 2. | 7. | 4 | 2 | 7 | 4
2.7.5 | Type | Line bay |  | - | 2. | 7. | 5 | 2 | 7 | 5
2.7.6 | Type test | Authority, year, Doc.no |  | - | 2. | 7. | 6 | 2 | 7 | 6
2.7.7 | Standards | IEC |  | - | 2. | 7. | 7 | 2 | 7 | 7
2.7.8 | Class | T1 |  | - | 2. | 7. | 8 | 2 | 7 | 8
2.7.9 | Creepage distance | 13316.4963 |  | mm | 2. | 7. | 9 | 2 | 7 | 9
2.7.10 | Primary rated voltage | 330/√3 |  | kV | 2. | 7. | 10 | 2 | 7 | 10
2.7.11 | Secondary rated voltage | 2x 110/√3 |  | V | 2. | 7. | 11 | 2 | 7 | 11
2.7.12 | Secondary rated voltage Open Delta | 110/√3 |  | V | 2. | 7. | 12 | 2 | 7 | 12
2.7.13 | Rated short time thermal current (3s) | 40 |  | kARMS | 2. | 7. | 13 | 2 | 7 | 13
2.7.14 | Rated burden | 30 |  | VA | 2. | 7. | 14 | 2 | 7 | 14
2.7.15 | Voltage factor (continuous / 30sec); | 1.2 / 1.5 |  | - | 2. | 7. | 15 | 2 | 7 | 15
2.7.16 | Protection Class | 0.5(3P)/3P |  | - | 2. | 7. | 16 | 2 | 7 | 16
2.7.17 | Measurement Class | 0.2 |  | - | 2. | 7. | 17 | 2 | 7 | 17
2.7.18 | Max. Force on Terminal | >1000 |  | N | 2. | 7. | 18 | 2 | 7 | 18
2.7.19 | Gross Weight | To be stated by Bidder |  | kg | 2. | 7. | 19 | 2 | 7 | 19
2.7.20 | HV Terminal Type | To be stated by Bidder |  | - | 2. | 7. | 20 | 2 | 7 | 20
[8 empty] | 2 | 7 | 20 | tom rad
2.8. | 330 kV Surge Arresters |  |  |  | 2. | 8. |  | 2 | 8 | 21 | R2
[8 empty] | 2 | 8 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 2 | 8 | 1 | R3
2.8.1 | Maker’s name | To be stated by Bidder |  | - | 2. | 8. | 1 | 2 | 8 | 1
2.8.2 | Maker’s type and reference | To be stated by Bidder |  | - | 2. | 8. | 2 | 2 | 8 | 2
2.8.3 | Country of origin | To be stated by Bidder |  | - | 2. | 8. | 3 | 2 | 8 | 3
2.8.4 | Description | Outdoor |  | - | 2. | 8. | 4 | 2 | 8 | 4
2.8.5 | Type of arresters | Gapless ZnO |  | - | 2. | 8. | 5 | 2 | 8 | 5
2.8.6 | Type test | Authority, year, Doc.no |  | - | 2. | 8. | 6 | 2 | 8 | 6
2.8.7 | Standards | IEC60099 |  | - | 2. | 8. | 7 | 2 | 8 | 7
2.8.8 | Creepage distance | 13316.4963 |  | mm | 2. | 8. | 8 | 2 | 8 | 8
2.8.9 | Highest volage for equipment | 362 |  | kV | 2. | 8. | 9 | 2 | 8 | 9
2.8.10 | Rated voltage Ur | 264 |  | kV | 2. | 8. | 10 | 2 | 8 | 10
2.8.11 | Maximum continuos operating voltage Uc | ≤210 |  | kV | 2. | 8. | 11 | 2 | 8 | 11
2.8.12 | Nominal discharge current | 20 |  | kA peak | 2. | 8. | 12 | 2 | 8 | 12
2.8.13 | Line discharge class | 4 |  | - | 2. | 8. | 13 | 2 | 8 | 13
2.8.14 | Maximal residual voltage 8/20µs (10kA) | ≤660 |  | kV peak | 2. | 8. | 14 | 2 | 8 | 14
2.8.15 | Maximum steep current impulse residual voltage 1/20µs (10kA) | ≤700 |  | kV | 2. | 8. | 15 | 2 | 8 | 15
2.8.16 | Impulse withstand current (peak value) (8/20 µs) | 20 |  | kA | 2. | 8. | 16 | 2 | 8 | 16
2.8.17 | Long-wave surge current (2000 µs) | To be stated by Bidder |  | A | 2. | 8. | 17 | 2 | 8 | 17
2.8.18 | Leakage current | To be stated by Bidder |  | mA | 2. | 8. | 18 | 2 | 8 | 18
2.8.19 | Insulation material | Polymeric rubber |  | - | 2. | 8. | 19 | 2 | 8 | 19
2.8.20 | Surge counters per phase | Yes |  | - | 2. | 8. | 20 | 2 | 8 | 20
[8 empty] | 2 | 8 | 20 | tom rad
3. | 132 kV & 66kV Equipment |  |  |  | 3. |  |  | 3 | 1 | 1 | R1
3.1. | 132 kV Circuit Breaker |  |  |  | 3. | 1. |  | 3 | 1 |  | R2
[8 empty] | 3 | 1 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 3 | 1 | 1 | R3
3.1.1 | Maker’s name | To be stated by Bidder |  | - | 3. | 1. | 1 | 3 | 1 | 1
3.1.2 | Maker’s type and reference | To be stated by Bidder |  | - | 3. | 1. | 2 | 3 | 1 | 2
3.1.3 | Country of origin | To be stated by Bidder |  | - | 3. | 1. | 3 | 3 | 1 | 3
3.1.4 | Description | To be stated by Bidder |  | - | 3. | 1. | 4 | 3 | 1 | 4
3.1.5 | Type | SF6 |  | - | 3. | 1. | 5 | 3 | 1 | 5
3.1.6 | Number of poles | 3 |  | Nos. | 3. | 1. | 6 | 3 | 1 | 6
3.1.7 | 3-ph. Single/three-phase operation | Three-phase |  | - | 3. | 1. | 7 | 3 | 1 | 7
3.1.8 | Type test | Authority, year, Doc.no |  | - | 3. | 1. | 8 | 3 | 1 | 8
3.1.9 | Standards | IEC 62271-100 |  | - | 3. | 1. | 9 | 3 | 1 | 9
3.1.10 | Class | Outdoor |  | - | 3. | 1. | 10 | 3 | 1 | 10
3.1.11 | Classification | C2-M2 |  | - | 3. | 1. | 11 | 3 | 1 | 11
3.1.12 | Insulation material | Brown glazed porcelain |  | - | 3. | 1. | 12 | 3 | 1 | 12
3.1.13 | Minimum Creepage distance | 5334 |  | mm | 3. | 1. | 13 | 3 | 1 | 13
3.1.14 | Rated normal current | 2500 |  | A | 3. | 1. | 14 | 3 | 1 | 14
3.1.15 | Rated peak withstand current | 100 |  | kA peak | 3. | 1. | 15 | 3 | 1 | 15
3.1.16 | Rated short-circuit breaking current (3s) | 31.5 |  | kA | 3. | 1. | 16 | 3 | 1 | 16
3.1.17 | (Deleted) |  |  | - | 3. | 1. | 17 | 3 | 1 | 17
3.1.18 | First pole to clear factor | 1.5 |  | - | 3. | 1. | 18 | 3 | 1 | 18
3.1.19 | Capacitive voltage factor | 1.2 |  | - | 3. | 1. | 19 | 3 | 1 | 19
3.1.20 | Total break time | ≤50 |  | ms | 3. | 1. | 20 | 3 | 1 | 20
3.1.21 | Maximum closing time | ≤70 |  | ms | 3. | 1. | 21 | 3 | 1 | 21
3.1.22 | Operating mechanism | Spring |  | - | 3. | 1. | 22 | 3 | 1 | 22
3.1.23 | Operating sequence | O-0.3sec-CO-3min-CO |  | - | 3. | 1. | 23 | 3 | 1 | 23
3.1.24 | Interuption chambers in series per phase | To be stated by Bidder |  | Nos. | 3. | 1. | 24 | 3 | 1 | 24
3.1.25 | Interrupting chamber values of distribution elements | To be stated by Bidder |  | pF\Ω | 3. | 1. | 25 | 3 | 1 | 25
3.1.26 | Motor rated voltage | 110 |  | V DC | 3. | 1. | 26 | 3 | 1 | 26
3.1.27 | Operating coils closing / opening | 110 |  | V DC | 3. | 1. | 27 | 3 | 1 | 27
3.1.28 | (Deleted) |  |  | - | 3. | 1. | 28 | 3 | 1 | 28
3.1.29 | Number of trip coils | 2 |  | Nos. | 3. | 1. | 29 | 3 | 1 | 29
3.1.30 | SF6 Block and alarm | Yes |  | - | 3. | 1. | 30 | 3 | 1 | 30
3.1.31 | Auxiliary contacts (8NO+8NC) | 110/7.5 |  | V DC/A | 3. | 1. | 31 | 3 | 1 | 31
3.1.32 | Heating elements with hygrostate/Light/Outlet | 230 |  | V AC | 3. | 1. | 32 | 3 | 1 | 32
[8 empty] | 3 | 1 | 32 | tom rad
3.2. | 132 kV Disconnector |  |  |  | 3. | 2. |  | 3 | 2 | 33 | R2
[8 empty] | 3 | 2 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 3 | 2 | 1 | R3
3.2.1 | Maker’s name | To be stated by Bidder |  | - | 3. | 2. | 1 | 3 | 2 | 1
3.2.2 | Maker’s type and reference | To be stated by Bidder |  | - | 3. | 2. | 2 | 3 | 2 | 2
3.2.3 | Country of origin | To be stated by Bidder |  | - | 3. | 2. | 3 | 3 | 2 | 3
3.2.4 | Description | 3-phase |  | - | 3. | 2. | 4 | 3 | 2 | 4
3.2.5 | Type | Motor operated |  | - | 3. | 2. | 5 | 3 | 2 | 5
3.2.6 | Mode of opening/closing | Horizontal centre break |  | - | 3. | 2. | 6 | 3 | 2 | 6
3.2.7 | Integrated Earthing Switch; Manually operated | on line disconnectors |  | - | 3. | 2. | 7 | 3 | 2 | 7
3.2.8 | Type test | Authority, year, Doc.no |  | - | 3. | 2. | 8 | 3 | 2 | 8
3.2.9 | Standards | IEC |  | - | 3. | 2. | 9 | 3 | 2 | 9
3.2.10 | Class | Outdoor |  | - | 3. | 2. | 10 | 3 | 2 | 10
3.2.11 | Creepage distance | 5334 |  | mm | 3. | 2. | 11 | 3 | 2 | 11
3.2.12 | Rated Voltage | 132 |  | kV | 3. | 2. | 12 | 3 | 2 | 12
3.2.13 | Maximum service voltage | 145 |  | kV | 3. | 2. | 13 | 3 | 2 | 13
3.2.14 | Number of poles | 3 |  | Nos. | 3. | 2. | 14 | 3 | 2 | 14
3.2.15 | Rated normal current | 2000 |  | A | 3. | 2. | 15 | 3 | 2 | 15
3.2.16 | Rated short time current for isolator and earth switch | 31.5 |  | kA | 3. | 2. | 16 | 3 | 2 | 16
3.2.17 | Rated peak withstand current for isolator and earth switch | 100 |  | kApeak | 3. | 2. | 17 | 3 | 2 | 17
3.2.18 | One minute power frequency withstand voltage | 275 |  | kV | 3. | 2. | 18 | 3 | 2 | 18
3.2.19 | Lightning impulse withstand voltage, toearth & between poles | 650 |  | kV | 3. | 2. | 19 | 3 | 2 | 19
3.2.20 | Closing/ opening time | To be stated by Bidder |  | sec | 3. | 2. | 20 | 3 | 2 | 20
3.2.21 | Operation motor rated voltage | 110 |  | V DC | 3. | 2. | 21 | 3 | 2 | 21
3.2.22 | Auxiliary Contacts (8NO+8NC) | 110/7.5 |  | V DC/A | 3. | 2. | 22 | 3 | 2 | 22
3.2.23 | Heating elements with hygrostst | 230 |  | V AC | 3. | 2. | 23 | 3 | 2 | 23
[8 empty] | 3 | 2 | 23 | tom rad
3.3. | 132 kV Earthing Switch |  |  |  | 3. | 3. |  | 3 | 3 | 24 | R2
[8 empty] | 3 | 3 | 25 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 3 | 3 | 26 | R3
3.3.1 | Maker’s name | To be stated by Bidder |  | - | 3. | 3. | 1 | 3 | 3 | 1
3.3.2 | Maker’s type and reference | To be stated by Bidder |  | - | 3. | 3. | 2 | 3 | 3 | 2
3.3.3 | Country of origin | To be stated by Bidder |  | - | 3. | 3. | 3 | 3 | 3 | 3
3.3.4 | Description | At disconnector switch |  | - | 3. | 3. | 4 | 3 | 3 | 4
3.3.5 | Type | Manual |  | - | 3. | 3. | 5 | 3 | 3 | 5
3.3.6 | Type test | Authority, year, Doc.no |  | - | 3. | 3. | 6 | 3 | 3 | 6
3.3.7 | Standards | IEC |  | - | 3. | 3. | 7 | 3 | 3 | 7
3.3.8 | Class | Outdoor |  | - | 3. | 3. | 8 | 3 | 3 | 8
3.3.9 | Auxiliary Contacts (8NO+8NC) | 110/7.5 |  | V DC/A | 3. | 3. | 9 | 3 | 3 | 9
3.3.10 | Heating elements | 230 |  | V AC | 3. | 3. | 10 | 3 | 3 | 10
[8 empty] | 3 | 3 | 10 | tom rad
3.4. | 132 kV Current Transformers |  |  |  | 3. | 4. |  | 3 | 4 | 11 | R2
[8 empty] | 3 | 4 | 12 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 3 | 4 | 13 | R3
3.4.1 | Maker’s name | To be stated by Bidder |  | - | 3. | 4. | 1 | 3 | 4 | 1
3.4.2 | Maker’s type and reference | To be stated by Bidder |  | - | 3. | 4. | 2 | 3 | 4 | 2
3.4.3 | Country of origin | To be stated by Bidder |  | - | 3. | 4. | 3 | 3 | 4 | 3
3.4.4 | Description | Transmission class |  | - | 3. | 4. | 4 | 3 | 4 | 4
3.4.5 | Type | Outdoor CT |  | - | 3. | 4. | 5 | 3 | 4 | 5
3.4.6 | Type test | Authority, year, Doc.no |  | - | 3. | 4. | 6 | 3 | 4 | 6
3.4.7 | Standards | IEC60044, BS3938 |  | - | 3. | 4. | 7 | 3 | 4 | 7
3.4.8 | Class | Outdoor |  | - | 3. | 4. | 8 | 3 | 4 | 8
3.4.9 | Creepage distance | 5334 |  | mm | 3. | 4. | 9 | 3 | 4 | 9
3.4.10 | Rated short time thermal current (3s) | 31.5 |  | kA | 3. | 4. | 10 | 3 | 4 | 10
3.4.11 | Number of secondary cores | 7 |  | Nos. | 3. | 4. | 11 | 3 | 4 | 11
3.4.12 | Nominal current | 300-600/600-1200 |  | A | 3. | 4. | 12 | 3 | 4 | 12
3.4.13 | Secondary rated current PX | 1 |  | A | 3. | 4. | 13 | 3 | 4 | 13
3.4.14 | Secondary rated current 5P20 | 1 |  | A | 3. | 4. | 14 | 3 | 4 | 14
3.4.15 | Rating factor | 1.2 |  | - | 3. | 4. | 15 | 3 | 4 | 15
3.4.16 | Rated burden protection core 5P20 | 20 |  | VA | 3. | 4. | 16 | 3 | 4 | 16
3.4.17 | Rated burden measuring core | 15 |  | VA | 3. | 4. | 17 | 3 | 4 | 17
3.4.18 | Protective cores number and class | 1x 5P20 3 x class PX 0.5V/turn |  | - | 3. | 4. | 18 | 3 | 4 | 18
3.4.19 | Measuring cores number and class | 2 x 0.2s Fs<5 |  | - | 3. | 4. | 19 | 3 | 4 | 19
3.4.20 | Spare core | 1 x class PX 0.5V/turn |  | - | 3. | 4. | 20 | 3 | 4 | 20
[8 empty] | 3 | 4 | 20 | tom rad
3.5. | 132(66) kV Capacitive Voltage Transformers |  |  |  | 3. | 5. |  | 3 | 5 | 21 | R2
[8 empty] | 3 | 5 | 22 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 3 | 5 | 23 | R3
3.5.1 | Maker’s name | To be stated by Bidder |  | - | 3. | 5. | 1 | 3 | 5 | 1
3.5.2 | Maker’s type and reference | To be stated by Bidder |  | - | 3. | 5. | 2 | 3 | 5 | 2
3.5.3 | Country of origin | To be stated by Bidder |  | - | 3. | 5. | 3 | 3 | 5 | 3
3.5.4 | Description | Transmission class |  | - | 3. | 5. | 4 | 3 | 5 | 4
3.5.5 | Type | Outdoor CVT |  | - | 3. | 5. | 5 | 3 | 5 | 5
3.5.6 | Type test | Authority, year, Doc.no |  | - | 3. | 5. | 6 | 3 | 5 | 6
3.5.7 | Standards | IEC60044-5, BS3938 |  | - | 3. | 5. | 7 | 3 | 5 | 7
3.5.8 | Class | T1 |  | - | 3. | 5. | 8 | 3 | 5 | 8
3.5.9 | Creepage distance | 5334 |  | mm | 3. | 5. | 9 | 3 | 5 | 9
3.5.10 | Primary rated voltage (inteconnectable between two volage levels) | Interconnectable between 132/√3 and 66/√3 |  | kV | 3. | 5. | 10 | 3 | 5 | 10
3.5.11 | Capacitance | 3500, +10%-5% |  | F | 3. | 5. | 11 | 3 | 5 | 11
3.5.12 | Number of secondary windings | 3 |  | Nos. | 3. | 5. | 12 | 3 | 5 | 12
3.5.13 | Secondary rated voltage | 2x 110/√3 |  | V | 3. | 5. | 13 | 3 | 5 | 13
3.5.14 | Damping circuit of reactor provided | Yes |  | - | 3. | 5. | 14 | 3 | 5 | 14
3.5.15 | Rated burden each winding | 100 |  | VA | 3. | 5. | 15 | 3 | 5 | 15
3.5.16 | Voltage factor (continuous / 30sec); | 1.2 / 1.5 |  | - | 3. | 5. | 16 | 3 | 5 | 16
3.5.17 | Protection Class | 0.5(3P)/3P |  | - | 3. | 5. | 17 | 3 | 5 | 17
3.5.18 | Measurement Class | 0.2 |  | - | 3. | 5. | 18 | 3 | 5 | 18
3.5.19 | Max. Force on Terminal | >1000 |  | N | 3. | 5. | 19 | 3 | 5 | 19
3.5.20 | Gross Weight | To be stated by Bidder |  | kg | 3. | 5. | 20 | 3 | 5 | 20
3521 | HV Terminal Type | To be stated by Bidder |  | - | 3 | 5 | 21 | 3 | 5 | 21
[8 empty] | 3 | 5 | 21 | tom rad
3.6. | 66 kV Capacitive Voltage Transformers |  |  |  | 3 | 6 |  | 3 | 6 | 22 | R2
[8 empty] | 3 | 6 | 23 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 3 | 6 | 24 | R3
3.6.1 | Maker’s name | To be stated by Bidder |  |  | 3 | 6 | 1 | 3 | 6 | 1
3.6.2 | Maker’s type and reference | To be stated by Bidder |  |  | 3 | 6 | 2 | 3 | 6 | 2
3.6.3 | Country of origin | To be stated by Bidder |  |  | 3 | 6 | 3 | 3 | 6 | 3
3.6.4 | Description | CVT |  |  | 3 | 6 | 4 | 3 | 6 | 4
3.6.5 | Type | Oil filled |  |  | 3 | 6 | 5 | 3 | 6 | 5
3.6.6 | Type test | Authority, year, Doc.no |  |  | 3 | 6 | 6 | 3 | 6 | 6
3.6.7 | Standards | IEC, class T1 |  |  | 3 | 6 | 7 | 3 | 6 | 7
3.6.8 | Class | Outdoor |  |  | 3 | 6 | 8 | 3 | 6 | 8
3.6.9 | Insulation material | Brown glazed porcelain |  |  | 3 | 6 | 9 | 3 | 6 | 9
3.6.10 | Creepage distance | 2344 |  | mm | 3 | 6 | 10 | 3 | 6 | 10
3.6.11 | Primary rated voltage | 66 |  | kV | 3 | 6 | 11 | 3 | 6 | 11
3.6.12 | Secondary rated voltage | 3x 110/√3 |  | V | 3 | 6 | 12 | 3 | 6 | 12
3.6.13 | Rated burden | 20 |  | VA | 3 | 6 | 13 | 3 | 6 | 13
3.6.14 | Voltage factor (continuous / 30sec); | 1.2 / 1.5 |  |  | 3 | 6 | 14 | 3 | 6 | 14
3.6.15 | Protection Class | 3P |  |  | 3 | 6 | 15 | 3 | 6 | 15
3.6.16 | Measurement Class | 0.2 |  |  | 3 | 6 | 16 | 3 | 6 | 16
3.6.17 | Max. Force on Terminal | >1000 |  | N | 3 | 6 | 17 | 3 | 6 | 17
3.6.18 | Gross Weight | To be stated by Bidder |  | kg | 3 | 6 | 18 | 3 | 6 | 18
3.6.19 | HV Terminal Type | To be stated by Bidder |  |  | 3 | 6 | 19 | 3 | 6 | 19
[5 empty] | 3 | 6 | 20 | 3 | 6 | 20
[8 empty] | 3 | 6 | 20 | tom rad
37 | 66 kV Surge Arresters |  |  |  | 3 | 7 |  | 3 | 7 | 21 | R2
[8 empty] | 3 | 7 | 22 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 3 | 7 | 23 | R3
3.7.1 | Maker’s name | To be stated by Bidder |  |  | 3. | 7. | 1 | 3 | 7 | 1
3.7.2 | Maker’s type and reference | To be stated by Bidder |  |  | 3. | 7. | 2 | 3 | 7 | 2
3.7.3 | Country of origin | To be stated by Bidder |  |  | 3. | 7. | 3 | 3 | 7 | 3
3.7.4 | Description | Hollow core |  |  | 3. | 7. | 4 | 3 | 7 | 4
3.7.5 | Type of arresters | Gapless ZnO |  |  | 3. | 7. | 5 | 3 | 7 | 5
3.7.6 | Type test | Authority, year, Doc.no |  |  | 3. | 7. | 6 | 3 | 7 | 6
3.7.7 | Standards | IEC60099 |  |  | 3. | 7. | 7 | 3 | 7 | 7
3.7.8 | Rated voltage Ur | 60 |  | kV | 3. | 7. | 8 | 3 | 7 | 8
3.7.9 | Rated short-circuit current | 65 |  | kA | 3. | 7. | 9 | 3 | 7 | 9
3.7.10 | Nominal discharge current | 10 |  | kA peak | 3. | 7. | 10 | 3 | 7 | 10
3.7.11 | Line discharge class | 3 |  |  | 3. | 7. | 11 | 3 | 7 | 11
3.7.12 | Maximal residual voltage 8/20µs (10kA) | 201 |  | kV peak | 3. | 7. | 12 | 3 | 7 | 12
3.7.13 | Cont. operation voltage | 44 |  | kV | 3. | 7. | 13 | 3 | 7 | 13
3.7.14 | Energy absorbation capability | 8 |  | kJ/kV | 3. | 7. | 14 | 3 | 7 | 14
3.7.15 | Impulse withstand current (peak value) (4/10 µs) | 100 |  | kA | 3. | 7. | 15 | 3 | 7 | 15
3.7.16 | long duration current impulse | 1000 |  | A | 3. | 7. | 16 | 3 | 7 | 16
3.7.17 | Leakage current | To be stated by Bidder |  | mA | 3. | 7. | 17 | 3 | 7 | 17
3.7.18 | Insulation material | Silicon rubber |  |  | 3. | 7. | 18 | 3 | 7 | 18
3.7.19 | Surge counters per phase | Yes |  |  | 3. | 7. | 19 | 3 | 7 | 19
4. | Transformers |  |  |  | 4. |  |  | 4 | 6 | 2 | R1
4.1. | Power Transformer 330/132(66)/11 kV |  |  |  | 4. | 1. |  | 4 | 1 |  | R2
[8 empty] | 4 | 1 |  | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 4 | 1 | 1 | R3
4.1.1 | Rated power | 90/90/10 |  | MVA | 4. | 1. | 1 | 4 | 1 | 1
4.1.2 | Nominal primary voltage | 330 |  | kV | 4. | 1. | 2 | 4 | 1 | 2
4.1.3 | Nominal secondary voltage | interconnectable between 132 and 66 |  | kV | 4. | 1. | 3 | 4 | 1 | 3
4.1.4 | Nominal tertiary voltage | 11 |  | kV | 4. | 1. | 4 | 4 | 1 | 4
4.1.5 | Highest system voltage | 352/145/12 |  | kV | 4. | 1. | 5 | 4 | 1 | 5
4.1.6 | Vector group | YNyn0+d1 |  | - | 4. | 1. | 6 | 4 | 1 | 6
4.1.7 | Cooling | ONAN/ONAF |  | - | 4. | 1. | 7 | 4 | 1 | 7
4.1.8 | Power at ONAN, minimum of rated power | 75 |  | % | 4. | 1. | 8 | 4 | 1 | 8
4.1.9 | Colour | RAL7032 (Grey) |  | - | 4. | 1. | 9 | 4 | 1 | 9
4.1.10 | Maker's name | To be stated by Bidder |  | - | 4. | 1. | 10 | 4 | 1 | 10
4.1.11 | Maker's type and reference | To be stated by Bidder |  | - | 4. | 1. | 11 | 4 | 1 | 11
4.1.12 | Country of origin | To be stated by Bidder |  | - | 4. | 1. | 12 | 4 | 1 | 12
4.1.13 | Description | oil filled |  | - | 4. | 1. | 13 | 4 | 1 | 13
4.1.14 | Type | Power transformer |  | - | 4. | 1. | 14 | 4 | 1 | 14
4.1.15 | Type test | Authority, year, Doc.no |  | - | 4. | 1. | 15 | 4 | 1 | 15
4.1.16 | Standards | IEC60076 |  | - | 4. | 1. | 16 | 4 | 1 | 16
4.1.17 | Transformer Class | Outdoor |  | - | 4. | 1. | 17 | 4 | 1 | 17
4.1.18 | Single or three phase units | three phase |  | - | 4. | 1. | 18 | 4 | 1 | 18
4.1.19 | Type of core | grain oriented silicon steel |  | - | 4. | 1. | 19 | 4 | 1 | 19
4.1.20 | Type of tank | upper flange |  | - | 4. | 1. | 20 | 4 | 1 | 20
4.1.21 | Tank fully vacuum proof | Yes |  | - | 4. | 1. | 21 | 4 | 1 | 21
4.1.22 | Specification of oil (general) | IEC 60296, class II |  | - | 4. | 1. | 22 | 4 | 1 | 22
4.1.23 | Oil corrosive sulfur free | Yes |  | - | 4. | 1. | 23 | 4 | 1 | 23
4.1.24 | Oil PCB free (certification to be provided) | Yes |  | - | 4. | 1. | 24 | 4 | 1 | 24
4.1.25 | Supplier, type of oil | To be stated by Bidder |  | - | 4. | 1. | 25 | 4 | 1 | 25
4.1.26 | Tap changer | On-load |  | - | 4. | 1. | 26 | 4 | 1 | 26
4.1.27 | Tap changer make | MR Germany or comparable vacum type |  | - | 4. | 1. | 27 | 4 | 1 | 27
4.1.28 | Tapping range | +10 / -15 |  | % | 4. | 1. | 28 | 4 | 1 | 28
4.1.29 | Step range | 1.25 |  | %each | 4. | 1. | 29 | 4 | 1 | 29
4.1.30 | OLTC drive | Motor drive 3-ph 380-415 VAC |  | - | 4. | 1. | 30 | 4 | 1 | 30
4.1.31 | Operation contact life at rated through current | >300000 |  | Nos. | 4. | 1. | 31 | 4 | 1 | 31
4.1.32 | Mechanical tap position indicator | Yes |  | - | 4. | 1. | 32 | 4 | 1 | 32
4.1.33 | Impedance voltage at rated power, primary/secondary | 14 |  | % | 4. | 1. | 33 | 4 | 1 | 33
4.1.34 | Impedance voltage at rated power, primary/tertiary | 24 |  | % | 4. | 1. | 34 | 4 | 1 | 34
4.1.35 | Impedance voltage at rated power, secondary/tertiary | 8 |  | % | 4. | 1. | 35 | 4 | 1 | 35
4.1.36 | Zero sequence impedance at principal tapping | 166 (shorted secondary) |  | % | 4. | 1. | 36 | 4 | 1 | 36
4.1.37 | Temperature rise oil/top, maximum | 60 |  | K | 4. | 1. | 37 | 4 | 1 | 37
4.1.38 | Temperature rise winding, average, resistance method | 65 |  | K | 4. | 1. | 38 | 4 | 1 | 38
4.1.39 | Temperature rise winding, hot spot, resistance method | 78 |  | K | 4. | 1. | 39 | 4 | 1 | 39
4.1.40 | Bushing type | Porcelain |  | - | 4. | 1. | 40 | 4 | 1 | 40
4.1.41 | Continuous overload for bushings | 20 |  | % | 4. | 1. | 41 | 4 | 1 | 41
4.1.42 | Minimum creepage distance (USCD) | 53.7 |  | mm/kV | 4. | 1. | 42 | 4 | 1 | 42
4.1.43 | Neutral bushing fully insulated at nominal voltage | Yes |  | - | 4. | 1. | 43 | 4 | 1 | 43
4.1.44 | Neutral current transformer cores | 1 x 5P20 1 x class X |  | - | 4. | 1. | 44 | 4 | 1 | 44
4.1.45 | Load losses (75°C), Guarantee | To be stated by Bidder |  | kW | 4. | 1. | 45 | 4 | 1 | 45
4.1.46 | No load losses (75°C), Guarantee | To be stated by Bidder |  | kW | 4. | 1. | 46 | 4 | 1 | 46
4.1.47 | Insulation levels (prim/sec/tert) (not corrected for altitude): |  |  |  | 4. | 1. | 47 | 4 | 1 | 47
4.1.48 | - Power frequency withstand voltage (phase and neutral) | 570/275/28 |  | kV | 4. | 1. | 48 | 4 | 1 | 48
4.1.48(a) | HV -neutral | 85 |  | kV
4.1.48(b) | MV - neutral | 140 |  | kV
4.1.49 | - Lightning impulse level (phase and neutral) | 1300/650/95 |  | kV | 4. | 1. | 49 | 4 | 1 | 49
4.1.49(a) | HV -neutral | 185 |  | kV
4.1.49(b) | MV - neutral | 325 |  | kV
4.1.50 | Tests: |  |  |  | 4. | 1. | 50 | 4 | 1 | 50
4.1.51 | Routine tests according to IEC 60076 | on each unit |  | - | 4. | 1. | 51 | 4 | 1 | 51
4.1.52 | Type tests according to IEC 60076 | on one unit |  | - | 4. | 1. | 52 | 4 | 1 | 52
4.1.53 | All special tests according to IEC 60076 | on one unit |  | - | 4. | 1. | 53 | 4 | 1 | 53
4.1.54 | Dimensions total (length x width x height) | To be stated by Bidder |  | mm | 4. | 1. | 54 | 4 | 1 | 54
4.1.55 | Dimensions transport (length x width x height) | To be stated by Bidder |  | mm | 4. | 1. | 55 | 4 | 1 | 55
4.1.56 | Weight of oil | To be stated by Bidder |  | kg | 4. | 1. | 56 | 4 | 1 | 56
4.1.57 | Total weight of completely assembled transfomer | To be stated by Bidder |  | kg | 4. | 1. | 57 | 4 | 1 | 57
4.1.58 | Auxiliary power, control | 110 |  | V DC | 4. | 1. | 58 | 4 | 1 | 58
4.1.59 | Auxiliary power, tap changer motor | 3ph 400 |  | V AC | 4. | 1. | 59 | 4 | 1 | 59
4.1.60 | Auxiliary power, heater | 230 |  | V AC | 4. | 1. | 60 | 4 | 1 | 60
4.1.61 | Noise level, Guarantee | <78 |  | dB(A) | 4. | 1. | 61 | 4 | 1 | 61
[8 empty] | 4 | 1 | 62 | tom rad
5. | Reactor |  |  |  | 5. |  |  | 5 |  |  | R1
5.1. | Shunt Reactor 330 kV (10MVAr) |  |  |  | 5. | 1. |  | 5 | 1 | 1 | R2
[8 empty] | 5 | 1 | 2 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 5 | 1 | 3 | R3
5.1.1 | Maker's name | To be stated by Bidder |  | - | 5. | 1. | 1 | 5 | 1 | 1
5.1.2 | Maker's type and reference | To be stated by Bidder |  | - | 5. | 1. | 2 | 5 | 1 | 2
5.1.3 | Country of origin | To be stated by Bidder |  | - | 5. | 1. | 3 | 5 | 1 | 3
5.1.4 | Description | Shunt reactor |  | - | 5. | 1. | 4 | 5 | 1 | 4
5.1.5 | Type | Single phase |  | - | 5. | 1. | 5 | 5 | 1 | 5
5.1.6 | Rated power | 10 |  | MVAr | 5. | 1. | 6 | 5 | 1 | 6
5.1.7 | Nominal primary voltage (Un) | 330 |  | kV | 5. | 1. | 7 | 5 | 1 | 7
5.1.8 | Maximum continuous operating voltage (Um) | 362 |  | kV | 5. | 1. | 8 | 5 | 1 | 8
5.1.9 | Cooling | ONAN |  | - | 5. | 1. | 9 | 5 | 1 | 9
5.1.10 | Colour | RAL7032 (Grey) |  | - | 5. | 1. | 10 | 5 | 1 | 10
5.1.11 | Rated short-time current (3s) | 40 |  | kA | 5. | 1. | 11 | 5 | 1 | 11
5.1.12 | Type test | Authority, year, Doc.no |  | - | 5. | 1. | 12 | 5 | 1 | 12
5.1.13 | Standards | IEC |  | - | 5. | 1. | 13 | 5 | 1 | 13
5.1.14 | Class | Outdoor |  | - | 5. | 1. | 14 | 5 | 1 | 14
5.1.15 | Type of core | grain oriented silicon steel |  | - | 5. | 1. | 15 | 5 | 1 | 15
5.1.16 | Type of tank | upper bolted flange |  | - | 5. | 1. | 16 | 5 | 1 | 16
5.1.17 | Tank fully vacuum proof | Yes |  | - | 5. | 1. | 17 | 5 | 1 | 17
5.1.18 | Specification of oil (general) | IEC 60296, class II |  | - | 5. | 1. | 18 | 5 | 1 | 18
5.1.19 | Oil corrosive sulfur free | Yes |  | - | 5. | 1. | 19 | 5 | 1 | 19
5.1.20 | Oil PCB free (certification to be provided) | Yes |  | - | 5. | 1. | 20 | 5 | 1 | 20
5.1.21 | Supplier, type of oil | To be stated by Bidder |  | - | 5. | 1. | 21 | 5 | 1 | 21
5.1.22 | Insulation levels (prim/sec) (not corrected for altitude): |  |  |  | 5. | 1. | 22 | 5 | 1 | 22
5.1.23 | - Power frequency withstand voltage (phase and neutral) | 570/70 |  | kV | 5. | 1. | 23 | 5 | 1 | 23
5.1.24 | - Lightning impulse level (phase and neutral) | 1300/170 |  | kV | 5. | 1. | 24 | 5 | 1 | 24
5.1.25 | Overvoltage withstand capacity continuously | 1,1 x Un |  | - | 5. | 1. | 25 | 5 | 1 | 25
5.1.26 | Overvoltage withstand capacity for 1 minute | 1,25 x Um |  | - | 5. | 1. | 26 | 5 | 1 | 26
5.1.27 | Overvoltage withstand capacity for 5 seconds | 1,5 x Um |  | - | 5. | 1. | 27 | 5 | 1 | 27
5.1.28 | Overvoltage withstand capacity for 1 second | 1,75 x Um |  | - | 5. | 1. | 28 | 5 | 1 | 28
5.1.29 | Positive internal prassure withstand capability | >70 |  | kPa | 5. | 1. | 29 | 5 | 1 | 29
5.1.30 | Negative internal prassure withstand capability at empty tank | >50 |  | mmHg | 5. | 1. | 30 | 5 | 1 | 30
5.1.31 | Temperature rise oil/top, maximum, at 1000masl | 60 |  | K | 5. | 1. | 31 | 5 | 1 | 31
5.1.32 | Temperature rise winding, average, resistance method, at 1000masl | 65 |  | K | 5. | 1. | 32 | 5 | 1 | 32
5.1.33 | Temperature rise winding, hot spot, resistance method, at 1000masl | 78 |  | K | 5. | 1. | 33 | 5 | 1 | 33
5.1.34 | Bushing type | Porcelain |  | - | 5. | 1. | 34 | 5 | 1 | 34
5.1.35 | Continuous overload for bushings | 20 |  | % | 5. | 1. | 35 | 5 | 1 | 35
5.1.36 | Minimum creepage distance primary side (USCD) | 53.7 |  | mm/kV | 5. | 1. | 36 | 5 | 1 | 36
5.1.37 | Minimum creepage distance neutral side (USCD) | 53.7 |  | mm/kV | 5. | 1. | 37 | 5 | 1 | 37
5.1.38 | Losses (75°C), Guarantee maximum at 35°C ambient temperature | To be stated by Bidder |  | kW | 5. | 1. | 38 | 5 | 1 | 38
5.1.39 | Bushing current transformer primary side: |  |  |  | 5. | 1. | 39 | 5 | 1 | 39
5.1.40 | Number of cores | 5 |  | Nos. | 5. | 1. | 40 | 5 | 1 | 40
5.1.41 | Turn ratio | 1/800 |  | - | 5. | 1. | 41 | 5 | 1 | 41
5.1.42 | Secondary tappings turns ratios | 1/100/200 |  | - | 5. | 1. | 42 | 5 | 1 | 42
5.1.43 | Class | 0.2S/ 4 x PX |  | - | 5. | 1. | 43 | 5 | 1 | 43
5.1.44 | Rated burden protection core | 10 |  | VA | 5. | 1. | 44 | 5 | 1 | 44
5.1.45 | Rated burden measuring core | 5 |  | VA | 5. | 1. | 45 | 5 | 1 | 45
5.1.46 | Bushing current transformer neutral side: |  |  |  | 5. | 1. | 46 | 5 | 1 | 46
5.1.47 | Number of cores | 3 |  | - | 5. | 1. | 47 | 5 | 1 | 47
5.1.48 | Turn ratio | 1/800 |  | - | 5. | 1. | 48 | 5 | 1 | 48
5.1.49 | Secondary tappings turns ratios | 1/100/200 |  | - | 5. | 1. | 49 | 5 | 1 | 49
5.1.50 | Class | 0.2S/ 2 x PX |  | - | 5. | 1. | 50 | 5 | 1 | 50
5.1.51 | Rated burden protection core | 10 |  | VA | 5. | 1. | 51 | 5 | 1 | 51
5.1.52 | Rated burden measuring core | 5 |  | VA | 5. | 1. | 52 | 5 | 1 | 52
5.1.53 | Dimensions total (length x width x height) | To be stated by Bidder |  | mm | 5. | 1. | 53 | 5 | 1 | 53
5.1.54 | Dimensions transport (length x width x height) | To be stated by Bidder |  | mm | 5. | 1. | 54 | 5 | 1 | 54
5.1.55 | Weight of oil | To be stated by Bidder |  | kg | 5. | 1. | 55 | 5 | 1 | 55
5.1.56 | Total weight of completely assembled reactor | To be stated by Bidder |  | kg | 5. | 1. | 56 | 5 | 1 | 56
5.1.57 | Auxiliary power, control | 110 |  | V DC | 5. | 1. | 57 | 5 | 1 | 57
5.1.58 | Auxiliary power, heater in control box | 230 |  | V AC | 5. | 1. | 58 | 5 | 1 | 58
5.1.59 | Noise level | <75 |  | dB(A) | 5. | 1. | 59 | 5 | 1 | 59
[8 empty] | 5 | 1 | 59 | tom rad
5.2. | Neutral Compensating Reactor 35 kV |  |  |  | 5. | 2. |  | 5 | 2 | 60 | R2
[8 empty] | 5 | 2 | 61 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 5 | 2 | 62 | R3
5.2.1 | Maker's name | To be stated by Bidder |  | - | 5. | 2. | 1 | 5 | 2 | 1
5.2.2 | Maker's type and reference | To be stated by Bidder |  | - | 5. | 2. | 2 | 5 | 2 | 2
5.2.3 | Country of origin | To be stated by Bidder |  | - | 5. | 2. | 3 | 5 | 2 | 3
5.2.4 | Description | Neutral reactor |  | - | 5. | 2. | 4 | 5 | 2 | 4
5.2.5 | Type | Single phase |  | - | 5. | 2. | 5 | 5 | 2 | 5
5.2.6 | Rated power | 15 |  | kVAr | 5. | 2. | 6 | 5 | 2 | 6
5.2.7 | Nominal primary voltage | 35 |  | kV | 5. | 2. | 7 | 5 | 2 | 7
5.2.8 | Maximum continuous operating voltage | 42 |  | kV | 5. | 2. | 8 | 5 | 2 | 8
5.2.9 | Core type | Core |  | - | 5. | 2. | 9 | 5 | 2 | 9
5.2.10 | Cooling | ONAN |  | - | 5. | 2. | 10 | 5 | 2 | 10
5.2.11 | Colour | RAL7032 (Grey) |  | - | 5. | 2. | 11 | 5 | 2 | 11
5.2.12 | Rated short-time current (3s) | 40 |  | kA | 5. | 2. | 12 | 5 | 2 | 12
5.2.13 | Type test | Authority, year, Doc.no |  | - | 5. | 2. | 13 | 5 | 2 | 13
5.2.14 | Standards | IEC60076, 60137 |  | - | 5. | 2. | 14 | 5 | 2 | 14
5.2.15 | Class | Outdoor |  | - | 5. | 2. | 15 | 5 | 2 | 15
5.2.16 | Type of core | grain oriented silicon steel |  | - | 5. | 2. | 16 | 5 | 2 | 16
5.2.17 | Type of tank | upper flange |  | - | 5. | 2. | 17 | 5 | 2 | 17
5.2.18 | Tank fully vacuum proof | Yes |  | - | 5. | 2. | 18 | 5 | 2 | 18
5.2.19 | Specification of oil (general) | IEC 60296, class II |  | - | 5. | 2. | 19 | 5 | 2 | 19
5.2.20 | Oil corrosive sulfur free | Yes |  | - | 5. | 2. | 20 | 5 | 2 | 20
5.2.21 | Oil PCB free (certification to be provided) | Yes |  | - | 5. | 2. | 21 | 5 | 2 | 21
5.2.22 | Supplier, type of oil | To be stated by Bidder |  | - | 5. | 2. | 22 | 5 | 2 | 22
5.2.23 | Magnetizing linearity | 140 |  | % Vn | 5. | 2. | 23 | 5 | 2 | 23
5.2.24 | Current density at maximum load and rated voltage and rated voltage tap | To be stated by Bidder |  | A/mm2 | 5. | 2. | 24 | 5 | 2 | 24
5.2.25 | Direct impedance at rated voltage N-X1, X2, X3 | 997/904/815 |  | Ω | 5. | 2. | 25 | 5 | 2 | 25
5.2.26 | Zero-sequence impedance at rated voltage | To be stated by Bidder |  | Ω | 5. | 2. | 26 | 5 | 2 | 26
5.2.27 | Tolerance to be applied to the reactor impedance | 5 |  | % | 5. | 2. | 27 | 5 | 2 | 27
5.2.28 | RIV max. Voltage level (IEC 62271-1) at 0.5 MHZ and 230 kV test voltage (1.1 ur/√3) Maximum | 2500 |  | mV | 5. | 2. | 28 | 5 | 2 | 28
5.2.29 | HV bushing rated current | 362 |  | A | 5. | 2. | 29 | 5 | 2 | 29
5.2.30 | Neutral busching rated current | 123 |  | A | 5. | 2. | 30 | 5 | 2 | 30
5.2.31 | Lightning impulse level HV winding | 200 |  | kV | 5. | 2. | 31 | 5 | 2 | 31
5.2.32 | Lightning impulse level neutral | 75 |  | kV | 5. | 2. | 32 | 5 | 2 | 32
5.2.33 | Rated short-duration AC withstand voltage HV winding | 95 |  | kV | 5. | 2. | 33 | 5 | 2 | 33
5.2.34 | Rated short-duration AC withstand voltage neutral | 28 |  | kV | 5. | 2. | 34 | 5 | 2 | 34
5.2.35 | Temperature rise oil/top, maximum, Guarantee | 60 |  | °C(G) | 5. | 2. | 35 | 5 | 2 | 35
5.2.36 | Temperature rise winding, average, resistance method, Guarantee | 65 |  | °C(G) | 5. | 2. | 36 | 5 | 2 | 36
5.2.37 | Temperature rise winding, hot spot, resistance method, Guarantee | 78 |  | °C(G) | 5. | 2. | 37 | 5 | 2 | 37
5.2.38 | Bushing type | Porcelain |  | - | 5. | 2. | 38 | 5 | 2 | 38
5.2.39 | Continuous overload for bushings | 20 |  | % | 5. | 2. | 39 | 5 | 2 | 39
5.2.40 | Minimum creepage distance (USCD) | 53.7 |  | mm/kV | 5. | 2. | 40 | 5 | 2 | 40
5.2.41 | Total losses (75°C) | To be stated by Bidder |  | kW | 5. | 2. | 41 | 5 | 2 | 41
5.2.42 | Current transformers: |  |  |  | 5. | 2. | 42 | 5 | 2 | 42
5.2.43 | HV neutral |  |  |  | 5. | 2. | 43 | 5 | 2 | 43
5.2.44 | Number of cores | 3 |  | Nos. | 5. | 2. | 44 | 5 | 2 | 44
5.2.45 | Accuracy class | PX |  | - | 5. | 2. | 45 | 5 | 2 | 45
5.2.46 | Burden | 30 |  | VA | 5. | 2. | 46 | 5 | 2 | 46
5.2.47 | Rated current ratio | 100/1 |  | - | 5. | 2. | 47 | 5 | 2 | 47
5.2.48 | Dimensions total (length x width x height) | To be stated by Bidder |  | mm | 5. | 2. | 48 | 5 | 2 | 48
5.2.49 | Dimensions transport (length x width x height) | To be stated by Bidder |  | mm | 5. | 2. | 49 | 5 | 2 | 49
5.2.50 | Weight of oil | To be stated by Bidder |  | kg | 5. | 2. | 50 | 5 | 2 | 50
5.2.51 | Total weight of completely assembled transfomer | To be stated by Bidder |  | kg | 5. | 2. | 51 | 5 | 2 | 51
5.2.52 | Auxiliary power, heater | 230 |  | V AC | 5. | 2. | 52 | 5 | 2 | 52
5.2.53 | Noise level, Guarantee | <78 |  | dB(A) | 5. | 2. | 53 | 5 | 2 | 53
[8 empty] | 5 | 2 | 54 | tom rad
5.3. | 36kV Surge Arrester |  |  |  | 5. | 3. |  | 5 | 3 | 55 | R2
[8 empty] | 5 | 3 | 56 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 5 | 3 | 57 | R3
5.3.1 | Type |  |  |  | 5. | 3. | 1 | 5 | 3 | 1
5.3.2 | Rated voltage | 36 |  | kV | 5. | 3. | 2 | 5 | 3 | 2
5.3.3 | Continuous-running voltage | 22 |  | kV | 5. | 3. | 3 | 5 | 3 | 3
5.3.4 | Nominal discharge current | 10 |  | kA | 5. | 3. | 4 | 5 | 3 | 4
5.3.5 | Creepage Distance | 31 |  | (kV/mm) | 5. | 3. | 5 | 5 | 3 | 5
5.3.6 | Applicable Standard | IEC 60099-5 |  |  | 5. | 3. | 6 | 5 | 3 | 6
5.3.7 | DC 1mA reference voltage (not less than) | 51 |  | kV | 5. | 3. | 7 | 5 | 3 | 7
5.3.8 | Leakage current under 0.75 times DC 1mA the reference voltage | ≤50 |  | mA | 5. | 3. | 8 | 5 | 3 | 8
5.3.9 | Rated frequency | 50 |  | Hz | 5. | 3. | 9 | 5 | 3 | 9
5.3.10 | * Frequency Reference Voltage | ≥36 |  | kV | 5. | 3. | 10 | 5 | 3 | 10
5.3.11 | The maximum residual voltage under 500A operation impact powe（peak,not more than） | 90 |  | kV | 5. | 3. | 11 | 5 | 3 | 11
5.3.12 | The maximum residual voltage under 10kA lightning shock electrical flow（peak,not more than） | 108 |  | kV | 5. | 3. | 12 | 5 | 3 | 12
5.3.13 | The maximum residual voltage under 10kA steep shock wave（peak,not more than） | 115 |  | kV | 5. | 3. | 13 | 5 | 3 | 13
5.3.14 | Large current shock resistance ability，4/10ms2times | 65 |  | kA | 5. | 3. | 14 | 5 | 3 | 14
5.3.15 | Tolerance ability under long duration shock current: 2ms Square wave current impulse (peak) | 150 |  | A | 5. | 3. | 15 | 5 | 3 | 15
5.3.16 | Rated short circuit resistance current capability |  |  |  | 5. | 3. | 16 | 5 | 3 | 16
5.3.17 | large current | 16 |  | kA | 5. | 3. | 17 | 5 | 3 | 17
5.3.18 | low current | 800 |  | A | 5. | 3. | 18 | 5 | 3 | 18
5.3.19 | insulation and resistance strength of the shell |  |  |  | 5. | 3. | 19 | 5 | 3 | 19
5.3.20 | Rated lightning impulse withstand voltage（peak） | 185 |  | kV | 5. | 3. | 20 | 5 | 3 | 20
5.3.21 | Rated short-time power frequency withstand voltage (effective value) | 95/dry、80/wet |  |  | 5. | 3. | 21 | 5 | 3 | 21
5.3.22 | durability against pollution |  |  |  | 5. | 3. | 22 | 5 | 3 | 22
5.3.23 | Artificial contamination test with salt | 0.06 |  | mg/cm2 | 5. | 3. | 23 | 5 | 3 | 23
5.3.24 | the equivalent creepage distance | 31 |  | mm/kV | 5. | 3. | 24 | 5 | 3 | 24
5.3.25 | The largest amount in partial discharge | 10 |  | pC | 5. | 3. | 25 | 5 | 3 | 25
[8 empty] | 5 | 3 | 26 | tom rad
6. | 11 kV Equipment |  |  |  | 6. |  |  | 6 |  |  | R1
6.1. | 11 kV Indoor Compact Metal Clad Air Insulated Switchgear |  |  |  | 6. | 1. |  | 6 | 1 | 1 | R2
[8 empty] | 6 | 1 | 2 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 6 | 1 | 3 | R3
6.1.1 | Type | Compact AIS |  | - | 6. | 1. | 1 | 6 | 1 | 1
6.1.2 | Manufacturer | Bidder to state |  | - | 6. | 1. | 2 | 6 | 1 | 2
6.1.3 | Country of origin | Bidder to state |  | - | 6. | 1. | 3 | 6 | 1 | 3
6.1.4 | Manufacturer's type designation | Bidder to state |  | - | 6. | 1. | 4 | 6 | 1 | 4
6.1.5 | Standard | IEC 62271-200 |  | - | 6. | 1. | 5 | 6 | 1 | 5
6.1.6 | Type test report | Bidder to state |  | - | 6. | 1. | 6 | 6 | 1 | 6
6.1.7 | Rated voltage | 12 |  | kV | 6. | 1. | 7 | 6 | 1 | 7
6.1.8 | Maximum system voltage | 12 |  | kV | 6. | 1. | 8 | 6 | 1 | 8
6.1.9 | Lighting impulsewithstand voltage | 80.625 |  | kV | 6. | 1. | 9 | 6 | 1 | 9
6.1.10 | Power frequency withstand voltage (1 min) | 30.1 |  | kV | 6. | 1. | 10 | 6 | 1 | 10
6.1.11 | Rated frequency | 50 |  | Hz | 6. | 1. | 11 | 6 | 1 | 11
6.1.12 | Rated short circuit breaking current (3 sec) | 31.5 |  | kA | 6. | 1. | 12 | 6 | 1 | 12
6.1.13 | Rated peak short circuit current | 80 |  | kA | 6. | 1. | 13 | 6 | 1 | 13
6.1.14 | LSC-categori | LSC-2A |  | - | 6. | 1. | 14 | 6 | 1 | 14
6.1.15 | Internal arc classification | IAC AFLR |  | - | 6. | 1. | 15 | 6 | 1 | 15
6.1.16 | Insulation medium | Air |  | - | 6. | 1. | 16 | 6 | 1 | 16
6.1.17 | Degree of protection | - |  |  | 6. | 1. | 17 | 6 | 1 | 17
6.1.18 | - MV switchgear | IP41 |  | - | 6. | 1. | 18 | 6 | 1 | 18
6.1.19 | - LV compartment | IP41 |  | - | 6. | 1. | 19 | 6 | 1 | 19
6.1.20 | Feeder width | Bidder to state |  | mm | 6. | 1. | 20 | 6 | 1 | 20
6.1.21 | Busbar | - |  |  | 6. | 1. | 21 | 6 | 1 | 21
6.1.22 | Rated current at 20° C | 2000 |  | A | 6. | 1. | 22 | 6 | 1 | 22
6.1.23 | Conductor material | copper |  | - | 6. | 1. | 23 | 6 | 1 | 23
6.1.24 | Circuit Breaker | - |  |  | 6. | 1. | 24 | 6 | 1 | 24
6.1.25 | Type (Manufacturer's identification) | Bidder to state |  | - | 6. | 1. | 25 | 6 | 1 | 25
6.1.26 | Standard | IEC |  | - | 6. | 1. | 26 | 6 | 1 | 26
6.1.27 | Rated Current | 2000 |  | A | 6. | 1. | 27 | 6 | 1 | 27
6.1.28 | Rated short circuit breaking current | 31.5 |  | kA | 6. | 1. | 28 | 6 | 1 | 28
6.1.29 | Rated short circuit making current | Bidder to state |  | kA | 6. | 1. | 29 | 6 | 1 | 29
6.1.30 | Rated frequency | 50 |  | Hz | 6. | 1. | 30 | 6 | 1 | 30
6.1.31 | Rated operation sequence | O-0.3sec-CO-3min-CO |  | - | 6. | 1. | 31 | 6 | 1 | 31
6.1.32 | Closing time | <35 |  | ms | 6. | 1. | 32 | 6 | 1 | 32
6.1.33 | Break time | Bidder to state |  | ms | 6. | 1. | 33 | 6 | 1 | 33
6.1.34 | Make time | Bidder to state |  | ms | 6. | 1. | 34 | 6 | 1 | 34
6.1.35 | Arcing time | Bidder to state |  | ms | 6. | 1. | 35 | 6 | 1 | 35
6.1.36 | Life span for contacts (number of operations) | - | - |  | 6. | 1. | 36 | 6 | 1 | 36
6.1.37 | - at rated current | Bidder to state |  | Nos | 6. | 1. | 37 | 6 | 1 | 37
6.1.38 | - at rated breaking current | Bidder to state |  | Nos | 6. | 1. | 38 | 6 | 1 | 38
6.1.39 | Arc quenching medium | vacuum |  | - | 6. | 1. | 39 | 6 | 1 | 39
6.1.40 | Auxiliary contacts | - | - |  | 6. | 1. | 40 | 6 | 1 | 40
6.1.41 | - number of NO | 12 |  | Nos | 6. | 1. | 41 | 6 | 1 | 41
6.1.42 | - number of NC | 12 |  | Nos | 6. | 1. | 42 | 6 | 1 | 42
6.1.43 | - Voltage / current | 110/7.5 |  | V/A DC | 6. | 1. | 43 | 6 | 1 | 43
6.1.44 | Operation mechanism for opening / closing | spring/spring |  | - | 6. | 1. | 44 | 6 | 1 | 44
6.1.45 | Spring charging motor | 110 |  | V DC | 6. | 1. | 45 | 6 | 1 | 45
6.1.46 | Number of tripping coils | 1 |  | - | 6. | 1. | 46 | 6 | 1 | 46
6.1.47 | Earthing switch/Disconnector |  |  |  | 6. | 1. | 47 | 6 | 1 | 47
6.1.48 | Type (Manufacturer’s identification) | Bidder to state |  | - | 6. | 1. | 48 | 6 | 1 | 48
6.1.49 | Standard | IEC |  | - | 6. | 1. | 49 | 6 | 1 | 49
6.1.50 | Rated current | 2000 |  | A | 6. | 1. | 50 | 6 | 1 | 50
6.1.51 | Rated short circuit withstand current (3 s) | 31.5 |  | kA | 6. | 1. | 51 | 6 | 1 | 51
6.1.52 | Rated peak short circuit current | 80 |  | kA | 6. | 1. | 52 | 6 | 1 | 52
6.1.53 | Current Transformer | - | - |  | 6. | 1. | 53 | 6 | 1 | 53
6.1.54 | Type (Manufacturer’s identification) | Bidder to state |  | - | 6. | 1. | 54 | 6 | 1 | 54
6.1.55 | Manufacturer | Bidder to state |  | - | 6. | 1. | 55 | 6 | 1 | 55
6.1.56 | Country of origin | Bidder to state |  | - | 6. | 1. | 56 | 6 | 1 | 56
6.1.57 | Standard | IEC |  | - | 6. | 1. | 57 | 6 | 1 | 57
6.1.58 | Rated primary current cable feeder | 50 |  | A | 6. | 1. | 58 | 6 | 1 | 58
6.1.59 | Rated primary current transformer feeder | 150 |  | A | 6. | 1. | 59 | 6 | 1 | 59
6.1.60 | Rated secondary current | 1 |  | A | 6. | 1. | 60 | 6 | 1 | 60
6.1.61 | Rated burden | 10 |  | VA | 6. | 1. | 61 | 6 | 1 | 61
6.1.62 | Protective cores number and class | 2 x 5P20 1 x class X |  | - | 6. | 1. | 62 | 6 | 1 | 62
6.1.63 | Measuring cores number and class | 1 x 0.2s Fs<5 |  | - | 6. | 1. | 63 | 6 | 1 | 63
6.1.64 | Rated short time withstand current | 31.5 |  | kA | 6. | 1. | 64 | 6 | 1 | 64
6.1.65 | Rated peak short circuit current | 80.625 |  | kA | 6. | 1. | 65 | 6 | 1 | 65
6.1.66 | Impulse withstand voltage (peak) | 30.1 |  | kA | 6. | 1. | 66 | 6 | 1 | 66
6.1.67 | Permanent overload factor | 1.2 |  | - | 6. | 1. | 67 | 6 | 1 | 67
6.1.68 | Insulation material | Bidder to state |  | - | 6. | 1. | 68 | 6 | 1 | 68
6.1.69 | Voltage Transformer |  |  |  | 6. | 1. | 69 | 6 | 1 | 69
6.1.70 | Type (Manufacturer’s identification) | Bidder to state |  | - | 6. | 1. | 70 | 6 | 1 | 70
6.1.71 | Manufacturer | Bidder to state |  | - | 6. | 1. | 71 | 6 | 1 | 71
6.1.72 | Country of origin | Bidder to state |  | - | 6. | 1. | 72 | 6 | 1 | 72
6.1.73 | Standard | IEC |  | - | 6. | 1. | 73 | 6 | 1 | 73
6.1.74 | Impulse withstand voltage (peak) | 80.625 |  | kV | 6. | 1. | 74 | 6 | 1 | 74
6.1.75 | Power frequency withstand voltage (1 min) | 30.1 |  | kV | 6. | 1. | 75 | 6 | 1 | 75
6.1.76 | Rated frequency | 50 |  | Hz | 6. | 1. | 76 | 6 | 1 | 76
6.1.77 | Rated primary voltage | 11/√3 |  | kV | 6. | 1. | 77 | 6 | 1 | 77
6.1.78 | Rated secondary voltage | 2x110/√3 |  | V | 6. | 1. | 78 | 6 | 1 | 78
6.1.79 | Accuracy class | 0.5 |  | Class | 6. | 1. | 79 | 6 | 1 | 79
6.1.80 | Output | 10 |  | VA | 6. | 1. | 80 | 6 | 1 | 80
6.1.81 | Permanent overload factor continuous | 1.2 |  | - | 6. | 1. | 81 | 6 | 1 | 81
6.1.82 | Insulation material | Bidder to state |  | - | 6. | 1. | 82 | 6 | 1 | 82
6.1.83 | Surge Arresters (if installed in AIS swgr) | - | - |  | 6. | 1. | 83 | 6 | 1 | 83
6.1.84 | Maximum system voltage | 12 |  | kV | 6. | 1. | 84 | 6 | 1 | 84
6.1.85 | Nominal operating voltage | 11 |  | kV | 6. | 1. | 85 | 6 | 1 | 85
6.1.86 | Frequency | 50 |  | Hz | 6. | 1. | 86 | 6 | 1 | 86
6.1.87 | MO type | Bidder to state |  | - | 6. | 1. | 87 | 6 | 1 | 87
6.1.88 | Standards | IEC60099 |  | - | 6. | 1. | 88 | 6 | 1 | 88
6.1.89 | Rated voltage Ur | 10 |  | kV | 6. | 1. | 89 | 6 | 1 | 89
6.1.90 | Nominal discharge current | 10 |  | kA peak | 6. | 1. | 90 | 6 | 1 | 90
6.1.91 | Line discharge class | class 1 |  | - | 6. | 1. | 91 | 6 | 1 | 91
6.1.92 | Maximal residual voltage 8/20µs (10kA) | 40 |  | kV peak | 6. | 1. | 92 | 6 | 1 | 92
6.1.93 | Maximum cont. operation voltage | 7.3 |  | kV | 6. | 1. | 93 | 6 | 1 | 93
6.1.94 | Maximum steep current impulse residual voltage 1/20µs (10kA) | 50 |  | kV | 6. | 1. | 94 | 6 | 1 | 94
6.1.95 | Impulse withstand current (peak value) (4/10 µs) | 100 |  | kA | 6. | 1. | 95 | 6 | 1 | 95
6.1.96 | Long-wave surge current (2000 µs) | 250 |  | A | 6. | 1. | 96 | 6 | 1 | 96
[8 empty] | 6 | 1 | 97 | tom rad
6.2. | 11 kV Surge Arresters |  |  |  | 6. | 2. |  | 6 | 2 | 98 | R2
[8 empty] | 6 | 2 | 99 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 6 | 2 | 100 | R3
6.2.1 | Maker’s name | Bidder to state |  | - | 6. | 2. | 1 | 6 | 2 | 1
6.2.2 | Maker’s type and reference | Bidder to state |  | - | 6. | 2. | 2 | 6 | 2 | 2
6.2.3 | Country of origin | Bidder to state |  | - | 6. | 2. | 3 | 6 | 2 | 3
6.2.4 | Description | Outdoor |  | - | 6. | 2. | 4 | 6 | 2 | 4
6.2.5 | Type of arresters | Gapless ZnO |  | - | 6. | 2. | 5 | 6 | 2 | 5
6.2.6 | Type test | Authority, year, Doc.no |  | - | 6. | 2. | 6 | 6 | 2 | 6
6.2.7 | Standards | IEC60099 |  | - | 6. | 2. | 7 | 6 | 2 | 7
6.2.8 | Rated voltage Ur (phase-earth / neutral-earth) | 10 |  | kV | 6. | 2. | 8 | 6 | 2 | 8
6.2.9 | Nominal discharge current | 10 |  | kA peak | 6. | 2. | 9 | 6 | 2 | 9
6.2.10 | Line discharge class | class 1 |  | - | 6. | 2. | 10 | 6 | 2 | 10
6.2.11 | Maximal residual voltage 8/20µs (10kA) | 40 |  | kV peak | 6. | 2. | 11 | 6 | 2 | 11
6.2.12 | Maximum cont. operation voltage (phase-earth / neutral-earth) | 7.3 / 5.4 |  | kV | 6. | 2. | 12 | 6 | 2 | 12
6.2.13 | Maximum steep current impulse residual voltage 1/20µs (10kA) | 50 |  | kV | 6. | 2. | 13 | 6 | 2 | 13
6.2.14 | Impulse withstand current (peak value) (4/10 µs) | 100 |  | kA | 6. | 2. | 14 | 6 | 2 | 14
6.2.15 | Long-wave surge current (2000 µs) | 250 |  | A | 6. | 2. | 15 | 6 | 2 | 15
6.2.16 | Leakage current | Bidder to state |  | mA | 6. | 2. | 16 | 6 | 2 | 16
6.2.17 | Insulation material | Silicon rubber |  | - | 6. | 2. | 17 | 6 | 2 | 17
6.2.18 | Surge counters per phase | No |  | - | 6. | 2. | 18 | 6 | 2 | 18
[8 empty] | 6 | 2 | 19 | tom rad
7. | Power Cables |  |  |  | 7. |  |  | 7 |  |  | R1
7.1. | 11 kV Power Cable |  |  |  | 7. | 1. |  | 7 | 1 | 1 | R2
[8 empty] | 7 | 1 | 2 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 7 | 1 | 3 | R3
7.1.1 | Type | 3-core+screen |  | - | 7. | 1. | 1 | 7 | 1 | 1
7.1.2 | Manufacturer | Bidder to state |  | - | 7. | 1. | 2 | 7 | 1 | 2
7.1.3 | Country of origin | Bidder to state |  | - | 7. | 1. | 3 | 7 | 1 | 3
7.1.4 | Manufacturer's type designation | Bidder to state |  | - | 7. | 1. | 4 | 7 | 1 | 4
7.1.5 | Type test | Authority, year, Doc.no |  | - | 7. | 1. | 5 | 7 | 1 | 5
7.1.6 | Standard | IEC 60502/SANS 1339 |  | - | 7. | 1. | 6 | 7 | 1 | 6
7.1.7 | Cross section areas | 70 |  | mm² | 7. | 1. | 7 | 7 | 1 | 7
7.1.8 | Conductor material | CU |  | - | 7. | 1. | 8 | 7 | 1 | 8
7.1.9 | Rated voltage Uo/U | 11/6.35 |  | kV | 7. | 1. | 9 | 7 | 1 | 9
7.1.10 | Highest system voltage Um | 12 |  | kV | 7. | 1. | 10 | 7 | 1 | 10
7.1.11 | Impulse withstand voltage | 95 |  | kV | 7. | 1. | 11 | 7 | 1 | 11
7.1.12 | Conductor longitudinal water sealing system | Bidder to state |  | - | 7. | 1. | 12 | 7 | 1 | 12
7.1.13 | Conductor screen | Bidder to state |  | - | 7. | 1. | 13 | 7 | 1 | 13
7.1.14 | Conductor screen thickness | Bidder to state |  | mm | 7. | 1. | 14 | 7 | 1 | 14
7.1.15 | Insulation type | XLPE |  | - | 7. | 1. | 15 | 7 | 1 | 15
7.1.16 | Insulation thickness | Bidder to state |  | mm | 7. | 1. | 16 | 7 | 1 | 16
7.1.17 | Insulation screen type | Bidder to state |  | - | 7. | 1. | 17 | 7 | 1 | 17
7.1.18 | Insulation screen thickness | Bidder to state |  | mm | 7. | 1. | 18 | 7 | 1 | 18
7.1.19 | Screen longitudinal water sealing system | Bidder to state |  | - | 7. | 1. | 19 | 7 | 1 | 19
7.1.20 | Cu wire screen cross section area | Bidder to state |  | mm² | 7. | 1. | 20 | 7 | 1 | 20
7.1.21 | Oversheath type | HDPE |  | - | 7. | 1. | 21 | 7 | 1 | 21
7.1.22 | Oversheath colour | Black |  | - | 7. | 1. | 22 | 7 | 1 | 22
7.1.23 | Oversheath thickness | Bidder to state |  | mm | 7. | 1. | 23 | 7 | 1 | 23
7.1.24 | Complete cable diameter | Bidder to state |  | mm | 7. | 1. | 24 | 7 | 1 | 24
7.1.25 | Complete cable weight | Bidder to state |  | kg/m | 7. | 1. | 25 | 7 | 1 | 25
7.1.26 | Maximum continuous conductor temperature at normal operation | Bidder to state |  | °C | 7. | 1. | 26 | 7 | 1 | 26
7.1.27 | DC resistance | Bidder to state |  | Ohm/km | 7. | 1. | 27 | 7 | 1 | 27
7.1.28 | Capacitance | Bidder to state |  | µF/km | 7. | 1. | 28 | 7 | 1 | 28
7.1.29 | Current carrying capacity in ground | Bidder to state |  | A | 7. | 1. | 29 | 7 | 1 | 29
7.1.30 | Current carrying capacity in air | Bidder to state |  | A | 7. | 1. | 30 | 7 | 1 | 30
7.1.31 | Short-circuit current capacity, start temperature 90 °C, end temperature 250 °C, 1 s | Bidder to state |  | kA | 7. | 1. | 31 | 7 | 1 | 31
7.1.32 | Manufacturer's specification | Bidder to state |  | - | 7. | 1. | 32 | 7 | 1 | 32
[8 empty] | 7 | 1 | 33 | tom rad
7.2. | 11 kV Cable Terminations |  |  |  | 7. | 2. |  | 7 | 2 | 34 | R2
[8 empty] | 7 | 2 | 35 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 7 | 2 | 36 | R3
7.2.1 | Type | Bidder to state |  | - | 7. | 2. | 1 | 7 | 2 | 1
7.2.2 | Manufacturer | Bidder to state |  | - | 7. | 2. | 2 | 7 | 2 | 2
7.2.3 | Country of origin | Bidder to state |  | - | 7. | 2. | 3 | 7 | 2 | 3
7.2.4 | Manufacturer's type designation | Bidder to state |  | - | 7. | 2. | 4 | 7 | 2 | 4
7.2.5 | Type test | Authority, year, Doc.no |  | - | 7. | 2. | 5 | 7 | 2 | 5
7.2.6 | Standard | IEC 60502/SANS 1339 |  | - | 7. | 2. | 6 | 7 | 2 | 6
7.2.7 | Cross section | 70 |  | mm² | 7. | 2. | 7 | 7 | 2 | 7
7.2.8 | Rated voltage Uo/U | 11/6.35 |  | kV | 7. | 2. | 8 | 7 | 2 | 8
7.2.9 | Highest system voltage Um | 12 |  | kV | 7. | 2. | 9 | 7 | 2 | 9
7.2.10 | Impulse withstand voltage | 95 |  | kV | 7. | 2. | 10 | 7 | 2 | 10
7.2.11 | Current carrying capacity | see related cable |  | A | 7. | 2. | 11 | 7 | 2 | 11
7.2.12 | Manufacturer's specification | Bidder to provide |  | - | 7. | 2. | 12 | 7 | 2 | 12
[8 empty] | 7 | 2 | 13 | tom rad
8. | Auxiliary Systems |  |  |  | 8. |  |  | 8 | 2 | 14 | R1
8.1. | 11/0.4 kV Substation Auxiliary Transformer |  |  |  | 8. | 1. |  | 8 | 1 | 15 | R2
[8 empty] | 8 | 1 | 16 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 8 | 1 | 17 | R3
8.1.1 | Type | 3-phase oil immersed |  | - | 8. | 1. | 1 | 8 | 1 | 1
8.1.2 | Manufacturer | Bidder to state |  | - | 8. | 1. | 2 | 8 | 1 | 2
8.1.3 | Country of origin | Bidder to state |  | - | 8. | 1. | 3 | 8 | 1 | 3
8.1.4 | Manufacturer's type designation | Bidder to state |  | - | 8. | 1. | 4 | 8 | 1 | 4
8.1.5 | Standard | IEC 60076, EN HD 428, EN 50216 |  | - | 8. | 1. | 5 | 8 | 1 | 5
8.1.6 | Type test report | Authority, year, Doc.no |  | - | 8. | 1. | 6 | 8 | 1 | 6
8.1.7 | Installation | Outdoor |  | - | 8. | 1. | 7 | 8 | 1 | 7
8.1.8 | Rated power | 500 |  | kVA | 8. | 1. | 8 | 8 | 1 | 8
8.1.9 | Rated voltage | 11/0.4 |  | kV | 8. | 1. | 9 | 8 | 1 | 9
8.1.10 | Off-circuit tap changer | ± 2 x 2,5 % |  | - | 8. | 1. | 10 | 8 | 1 | 10
8.1.11 | Impedance | 4 |  | % | 8. | 1. | 11 | 8 | 1 | 11
8.1.12 | Connection | Dyn11 |  | - | 8. | 1. | 12 | 8 | 1 | 12
8.1.13 | Short-circuit voltage | Bidder to state |  | % | 8. | 1. | 13 | 8 | 1 | 13
8.1.14 | Zero-sequence impedance | Bidder to state |  | ohm | 8. | 1. | 14 | 8 | 1 | 14
8.1.15 | No-load losses | Bidder to state |  | W | 8. | 1. | 15 | 8 | 1 | 15
8.1.16 | Load losses | Bidder to state |  | W | 8. | 1. | 16 | 8 | 1 | 16
8.1.17 | Temperature rise, oil | 50 |  | K | 8. | 1. | 17 | 8 | 1 | 17
8.1.18 | Temperature rise, winding | 55 |  | K | 8. | 1. | 18 | 8 | 1 | 18
8.1.19 | Type of cooling | ONAN |  | - | 8. | 1. | 19 | 8 | 1 | 19
8.1.20 | Sound level | Bidder to state |  | dB(A) | 8. | 1. | 20 | 8 | 1 | 20
8.1.21 | Type of tank | Sealed, bolted lid |  | - | 8. | 1. | 21 | 8 | 1 | 21
8.1.22 | Type of core | Core |  | - | 8. | 1. | 22 | 8 | 1 | 22
8.1.23 | Total weight | Bidder to state |  | kg | 8. | 1. | 23 | 8 | 1 | 23
8.1.24 | Dimensions (length x width x height) | Bidder to state |  | mm | 8. | 1. | 24 | 8 | 1 | 24
[8 empty] | 8 | 1 | 25 | tom rad
8.2. | Stand-by Diesel Generator |  |  |  | 8. | 2. |  | 8 | 2 | 26 | R2
[8 empty] | 8 | 2 | 27 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 8 | 2 | 28 | R3
8.2.1 | Type | Bidder to state |  | - | 8. | 2. | 1 | 8 | 2 | 1
8.2.2 | Manufacturer | Bidder to state |  | - | 8. | 2. | 2 | 8 | 2 | 2
8.2.3 | Country of origin | Bidder to state |  | - | 8. | 2. | 3 | 8 | 2 | 3
8.2.4 | Manufacturer's type designation | Bidder to state |  | - | 8. | 2. | 4 | 8 | 2 | 4
8.2.5 | Motor brand/designation | Bidder to state |  | - | 8. | 2. | 5 | 8 | 2 | 5
8.2.6 | Generator brand/designation | Bidder to state |  | - | 8. | 2. | 6 | 8 | 2 | 6
8.2.7 | Control panel brand/designation | Bidder to state |  | - | 8. | 2. | 7 | 8 | 2 | 7
8.2.8 | Standard | ISO8528 |  | - | 8. | 2. | 8 | 8 | 2 | 8
8.2.9 | Type test report | Bidder to include |  | - | 8. | 2. | 9 | 8 | 2 | 9
8.2.10 | Installation | Outdoor |  | - | 8. | 2. | 10 | 8 | 2 | 10
8.2.11 | Design temperature | -10 to + 70 |  | OC | 8. | 2. | 11 | 8 | 2 | 11
8.2.12 | Mechanical structure | Soundproofed |  | - | 8. | 2. | 12 | 8 | 2 | 12
8.2.13 | Rated voltage | 400/230 |  | V | 8. | 2. | 13 | 8 | 2 | 13
8.2.14 | Voltage stability | ±1 |  | % | 8. | 2. | 14 | 8 | 2 | 14
8.2.15 | Standby power | 250 / 200 |  | kVA / kW | 8. | 2. | 15 | 8 | 2 | 15
8.2.16 | Prime power | 227 / 182 |  | kVA / kW | 8. | 2. | 16 | 8 | 2 | 16
8.2.17 | Zero-sequence impedance Xo | Bidder to state |  | % | 8. | 2. | 17 | 8 | 2 | 17
8.2.18 | Battery | Bidder to state |  | V DC | 8. | 2. | 18 | 8 | 2 | 18
8.2.19 | Performance class | G3 |  | - | 8. | 2. | 19 | 8 | 2 | 19
8.2.20 | EPA exhaust emission | EPA3 or similar |  | - | 8. | 2. | 20 | 8 | 2 | 20
8.2.21 | Acoustic pressure LpA | <71 |  | dB(A) a7 | 8. | 2. | 21 | 8 | 2 | 21
8.2.22 | Acoustic power LwA | <97 |  | dB(A) | 8. | 2. | 22 | 8 | 2 | 22
8.2.23 | Fuel tank capactity | >400 |  | litres | 8. | 2. | 23 | 8 | 2 | 23
8.2.24 | Empty weight | Bidder to state |  | kg | 8. | 2. | 24 | 8 | 2 | 24
8.2.25 | Dimensions (length x width x height) | Bidder to state |  | mm | 8. | 2. | 25 | 8 | 2 | 25
[8 empty] | 8 | 2 | 26 | tom rad
8.3. | Battery 110 V DC |  |  |  | 8. | 3. |  | 8 | 3 | 27 | R2
[8 empty] | 8 | 3 | 28 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 8 | 3 | 29 | R3
8.3.1 | Maker’s type and reference | Bidder to state |  | - | 8. | 3. | 1 | 8 | 3 | 1
8.3.2 | Manufacturer | Bidder to state |  | - | 8. | 3. | 2 | 8 | 3 | 2
8.3.3 | Country of origin | Bidder to state |  | - | 8. | 3. | 3 | 8 | 3 | 3
8.3.4 | Description | Station control supply |  | - | 8. | 3. | 4 | 8 | 3 | 4
8.3.5 | Type test | Authority, year, Doc.no |  | - | 8. | 3. | 5 | 8 | 3 | 5
8.3.6 | Standards | IEC |  | - | 8. | 3. | 6 | 8 | 3 | 6
8.3.7 | Type | Maintenance-free VRLA GEL Long life |  | - | 8. | 3. | 7 | 8 | 3 | 7
8.3.8 | Nominal voltage | 110 |  | V DC | 8. | 3. | 8 | 8 | 3 | 8
8.3.9 | Service voltage | Bidder to state |  | V DC | 8. | 3. | 9 | 8 | 3 | 9
8.3.10 | Number of cells | Bidder to state |  | Nos | 8. | 3. | 10 | 8 | 3 | 10
8.3.11 | Capacity at 10 h discharge time | Bidder to state |  | Ah | 8. | 3. | 11 | 8 | 3 | 11
8.3.12 | Reference ambient temperature | Bidder to state |  | °C | 8. | 3. | 12 | 8 | 3 | 12
8.3.13 | Voltage per cell fully charged | Bidder to state |  | V DC | 8. | 3. | 13 | 8 | 3 | 13
8.3.14 | Voltage per cell fully discharged | Bidder to state |  | V DC | 8. | 3. | 14 | 8 | 3 | 14
8.3.15 | Quantity of electrolyte per cell | Bidder to state |  | cm³ | 8. | 3. | 15 | 8 | 3 | 15
8.3.16 | Dimensions of complete battery (height x width x depth) | Bidder to state |  | mm | 8. | 3. | 16 | 8 | 3 | 16
8.3.17 | Erected in cubicle | Yes/No |  | - | 8. | 3. | 17 | 8 | 3 | 17
8.3.18 | Mass o f complete battery | Bidder to state |  | kg | 8. | 3. | 18 | 8 | 3 | 18
[8 empty] | 8 | 3 | 19 | tom rad
8.4. | Battery Chargers 110 V DC |  |  |  | 8. | 4. |  | 8 | 4 | 20 | R2
[8 empty] | 8 | 4 | 21 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 8 | 4 | 22 | R3
8.4.1 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 4. | 1 | 8 | 4 | 1
8.4.2 | Manufacturer | To be stated by Bidder |  | - | 8. | 4. | 2 | 8 | 4 | 2
8.4.3 | Country of origin | To be stated by Bidder |  | - | 8. | 4. | 3 | 8 | 4 | 3
8.4.4 | Description | Station control supply |  | - | 8. | 4. | 4 | 8 | 4 | 4
8.4.5 | Type test | Authority, year, Doc.no |  | - | 8. | 4. | 5 | 8 | 4 | 5
8.4.6 | Standards | IEC |  | - | 8. | 4. | 6 | 8 | 4 | 6
8.4.7 | Nominal voltage | 110 |  | V DC | 8. | 4. | 7 | 8 | 4 | 7
8.4.8 | Service voltage | To be stated by Bidder |  | V DC | 8. | 4. | 8 | 8 | 4 | 8
8.4.9 | Rated voltage on float charge | To be stated by Bidder |  | V | 8. | 4. | 9 | 8 | 4 | 9
8.4.10 | Rated voltage on boost charge | To be stated by Bidder |  | V | 8. | 4. | 10 | 8 | 4 | 10
8.4.11 | Rated voltage absorption charge | To be stated by Bidder |  | V | 8. | 4. | 11 | 8 | 4 | 11
8.4.12 | Charging characteristic | To be stated by Bidder |  | - | 8. | 4. | 12 | 8 | 4 | 12
8.4.13 | Accuracy of output voltage | To be stated by Bidder |  | +/- % | 8. | 4. | 13 | 8 | 4 | 13
8.4.14 | Rated max. output boost charge | To be stated by Bidder |  | A | 8. | 4. | 14 | 8 | 4 | 14
8.4.15 | Rated input | To be stated by Bidder |  | kVA | 8. | 4. | 15 | 8 | 4 | 15
8.4.16 | Max. Ripple (without the battery connected in parallel) | To be stated by Bidder |  | V | 8. | 4. | 16 | 8 | 4 | 16
8.4.17 | Reference ambient temperature | To be stated by Bidder |  | V | 8. | 4. | 17 | 8 | 4 | 17
8.4.18 | Stability of the output voltage | To be stated by Bidder |  | % | 8. | 4. | 18 | 8 | 4 | 18
8.4.19 | Main and standby function | Yes |  | - | 8. | 4. | 19 | 8 | 4 | 19
8.4.20 | Dimensions (w x d x h) | To be stated by Bidder |  | mm | 8. | 4. | 20 | 8 | 4 | 20
8.4.21 | Total mass | To be stated by Bidder |  | kg | 8. | 4. | 21 | 8 | 4 | 21
[8 empty] | 8 | 4 | 22 | tom rad
8.5. | Battery 48 V DC |  |  |  | 8. | 5. |  | 8 | 5 | 23 | R2
[8 empty] | 8 | 5 | 24 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 8 | 5 | 25 | R3
8.5.1 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 5. | 1 | 8 | 5 | 1
8.5.2 | Manufacturer | To be stated by Bidder |  | - | 8. | 5. | 2 | 8 | 5 | 2
8.5.3 | Country of origin | To be stated by Bidder |  | - | 8. | 5. | 3 | 8 | 5 | 3
8.5.4 | Description | Telecom system |  | - | 8. | 5. | 4 | 8 | 5 | 4
8.5.5 | Type test | Authority, year, Doc.no |  | - | 8. | 5. | 5 | 8 | 5 | 5
8.5.6 | Standards | IEC, ITU |  | - | 8. | 5. | 6 | 8 | 5 | 6
8.5.7 | Type | Lithium ion |  | - | 8. | 5. | 7 | 8 | 5 | 7
8.5.8 | Nominal voltage | 48 |  | V DC | 8. | 5. | 8 | 8 | 5 | 8
8.5.9 | Service voltage | To be stated by Bidder |  | V DC | 8. | 5. | 9 | 8 | 5 | 9
8.5.10 | Number of cells | To be stated by Bidder |  | Nos | 8. | 5. | 10 | 8 | 5 | 10
8.5.11 | Capacity at 10 h discharge time | To be stated by Bidder |  | Ah | 8. | 5. | 11 | 8 | 5 | 11
8.5.12 | Reference ambient temperature | To be stated by Bidder |  | °C | 8. | 5. | 12 | 8 | 5 | 12
8.5.13 | Voltage per cell fully charged | To be stated by Bidder |  | V DC | 8. | 5. | 13 | 8 | 5 | 13
8.5.14 | Voltage per cell fully discharged | To be stated by Bidder |  | V DC | 8. | 5. | 14 | 8 | 5 | 14
8.5.15 | Dimensions of complete battery (height x width x depth) | To be stated by Bidder |  | mm | 8. | 5. | 15 | 8 | 5 | 15
8.5.16 | Erected in cubicle | Yes/No |  | - | 8. | 5. | 16 | 8 | 5 | 16
8.5.17 | Mass o f complete battery | To be stated by Bidder |  | kg | 8. | 5. | 17 | 8 | 5 | 17
[8 empty] | 8 | 5 | 18 | tom rad
8.6. | Battery Chargers 48 V DC |  |  |  | 8. | 6. |  | 8 | 6 | 19 | R2
[8 empty] | 8 | 6 | 20 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 8 | 6 | 21 | R3
8.6.1 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 6. | 1 | 8 | 6 | 1
8.6.2 | Manufacturer | To be stated by Bidder |  | - | 8. | 6. | 2 | 8 | 6 | 2
8.6.3 | Country of origin | To be stated by Bidder |  | - | 8. | 6. | 3 | 8 | 6 | 3
8.6.4 | Description | Telecom system |  | - | 8. | 6. | 4 | 8 | 6 | 4
8.6.5 | Type test | Authority, year, Doc.no |  | - | 8. | 6. | 5 | 8 | 6 | 5
8.6.6 | Standards | IEC, ITU |  | - | 8. | 6. | 6 | 8 | 6 | 6
8.6.7 | Nominal voltage | 48 |  | V DC | 8. | 6. | 7 | 8 | 6 | 7
8.6.8 | Service voltage | To be stated by Bidder |  | V DC | 8. | 6. | 8 | 8 | 6 | 8
8.6.9 | Rated voltage on float charge | To be stated by Bidder |  | V | 8. | 6. | 9 | 8 | 6 | 9
8.6.10 | Rated voltage on boost charge | To be stated by Bidder |  | V | 8. | 6. | 10 | 8 | 6 | 10
8.6.11 | Rated voltage absorption charge | To be stated by Bidder |  | V | 8. | 6. | 11 | 8 | 6 | 11
8.6.12 | Charging characteristic | To be stated by Bidder |  | - | 8. | 6. | 12 | 8 | 6 | 12
8.6.13 | Accuracy of output voltage | To be stated by Bidder |  | +/- % | 8. | 6. | 13 | 8 | 6 | 13
8.6.14 | Rated max. output boost charge | To be stated by Bidder |  | A | 8. | 6. | 14 | 8 | 6 | 14
8.6.15 | Rated input | To be stated by Bidder |  | kVA | 8. | 6. | 15 | 8 | 6 | 15
8.6.16 | Max. Ripple | To be stated by Bidder |  | V | 8. | 6. | 16 | 8 | 6 | 16
8.6.17 | Reference ambient temperature | To be stated by Bidder |  | V | 8. | 6. | 17 | 8 | 6 | 17
8.6.18 | Stability of the output voltage | To be stated by Bidder |  | % | 8. | 6. | 18 | 8 | 6 | 18
8.6.19 | Main and standby function | No |  | - | 8. | 6. | 19 | 8 | 6 | 19
8.6.20 | Dimensions (w x d x h) | To be stated by Bidder |  | mm | 8. | 6. | 20 | 8 | 6 | 20
8.6.21 | Protection degree | 54 |  | IP | 8. | 6. | 21 | 8 | 6 | 21
8.6.22 | Total mass | To be stated by Bidder |  | kg | 8. | 6. | 22 | 8 | 6 | 22
[8 empty] | 8 | 6 | 23 | tom rad
8.7. | CCTV Surveillance System and Access Control |  |  |  | 8. | 7. |  | 8 | 7 | 24 | R2
[8 empty] | 8 | 7 | 25 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 8 | 7 | 26 | R3
8.7.1 | IP Bullet camera complete with accessories |  |  |  | 8. | 7. | 1 | 8 | 7 | 1
8.7.2 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 2 | 8 | 7 | 2
8.7.3 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 3 | 8 | 7 | 3
8.7.4 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 4 | 8 | 7 | 4
8.7.5 | Video interface | ONVIF |  | - | 8. | 7. | 5 | 8 | 7 | 5
8.7.6 | Profile for broadcast and storage | H.2064 High profile |  | - | 8. | 7. | 6 | 8 | 7 | 6
8.7.7 | Resolution | Full HD with 1080p@30fps |  | - | 8. | 7. | 7 | 8 | 7 | 7
8.7.8 | Built-in IR | Effective distance ≥80 |  | m | 8. | 7. | 8 | 8 | 7 | 8
8.7.9 | Image enhancement | Digital Wide Dynamic Range |  | - | 8. | 7. | 9 | 8 | 7 | 9
8.7.10 | Image quality | Tru day/night with mechanical IR cut filter |  | - | 8. | 7. | 10 | 8 | 7 | 10
8.7.11 | Resolution/Quality | 4Megapixel (1920x1080) |  | - | 8. | 7. | 11 | 8 | 7 | 11
8.7.12 | Zome/Focus | Remote |  | - | 8. | 7. | 12 | 8 | 7 | 12
8.7.13 | Lens type | Motorised vari-focal |  | - | 8. | 7. | 13 | 8 | 7 | 13
8.7.14 | Focal length | 2.7-12 |  | mm | 8. | 7. | 14 | 8 | 7 | 14
8.7.15 | Time | Embedded real-time clock, NTP Client |  | - | 8. | 7. | 15 | 8 | 7 | 15
8.7.16 | Ingress Protection & Vandal Resistance rating | IP67, IK10 |  | - | 8. | 7. | 16 | 8 | 7 | 16
8.7.17 | Support smart function |  |  |  | 8. | 7. | 17 | 8 | 7 | 17
8.7.18 | Intrusion detection | Yes |  | - | 8. | 7. | 18 | 8 | 7 | 18
8.7.19 | Line crossing detection | Yes |  | - | 8. | 7. | 19 | 8 | 7 | 19
8.7.20 | Motion detection human and vehicle targets classification) | Yes |  | - | 8. | 7. | 20 | 8 | 7 | 20
8.7.21 | Video tampering alarm | Yes |  | - | 8. | 7. | 21 | 8 | 7 | 21
8.7.22 | Exception alarm | Yes |  | - | 8. | 7. | 22 | 8 | 7 | 22
8.7.23 | Face detection | Yes |  | - | 8. | 7. | 23 | 8 | 7 | 23
8.7.24 | Event Linkage: |  |  |  | 8. | 7. | 24 | 8 | 7 | 24
8.7.25 | Upload to FTP/memory card/NAS | Yes |  | - | 8. | 7. | 25 | 8 | 7 | 25
8.7.26 | Notify surveillance centre | Yes |  | - | 8. | 7. | 26 | 8 | 7 | 26
8.7.27 | Trigger recording | Yes |  | - | 8. | 7. | 27 | 8 | 7 | 27
8.7.28 | Trigger capture | Yes |  | - | 8. | 7. | 28 | 8 | 7 | 28
8.7.29 | Send email | Yes |  | - | 8. | 7. | 29 | 8 | 7 | 29
8.7.30 | Voltage | 12±25% |  | VDC | 8. | 7. | 30 | 8 | 7 | 30
8.7.31 | Load | 0.92 |  | A | 8. | 7. | 31 | 8 | 7 | 31
8.7.32 | Power Maximum | 11 |  | W | 8. | 7. | 32 | 8 | 7 | 32
8.7.33 | Connection | Coaxial power plug |  | - | 8. | 7. | 33 | 8 | 7 | 33
8.7.34 | Connection security | Revers polarity protection |  | - | 8. | 7. | 34 | 8 | 7 | 34
8.7.35 | PoE | 802.3af, Class 3, 36-57V, 0.35-0.22A, max 12.5W |  | - | 8. | 7. | 35 | 8 | 7 | 35
8.7.36 | Ethernet interface | 1 RJ45 10 m/100 M self-adaptive Ethernet port |  | - | 8. | 7. | 36 | 8 | 7 | 36
8.7.37 | User/Host | Up to 32 users |  | Nos. | 8. | 7. | 37 | 8 | 7 | 37
8.7.38 | User levels | Administrator+Operator+User |  | - | 8. | 7. | 38 | 8 | 7 | 38
8.7.39 | Security | Password protection, complicated password, HTTPS encryption, IP address filter, Security Audit Log, basic and digest authentication for HTTP/HTTPS, TLS 1.1/1.2, WSSE and digest authentication for Open Network Video Interface |  | - | 8. | 7. | 39 | 8 | 7 | 39
8.7.40 | Network storage | NAS (NFS, SMB/CIFS), auto network replenishment (ANR) or trickle back technology |  | - | 8. | 7. | 40 | 8 | 7 | 40
8.7.41 | On-board storage | Built-in memory card slot, support micro SD card, up to 256 GB |  | - | 8. | 7. | 41 | 8 | 7 | 41
8.7.42 | SNR | ≥52 |  | dB | 8. | 7. | 42 | 8 | 7 | 42
8.7.43 | Image enhancement | BLC, HLC, 3D DNR |  | - | 8. | 7. | 43 | 8 | 7 | 43
8.7.44 | Dome Camera complete with accessories |  |  |  | 8. | 7. | 44 | 8 | 7 | 44
8.7.45 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 45 | 8 | 7 | 45
8.7.46 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 46 | 8 | 7 | 46
8.7.47 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 47 | 8 | 7 | 47
8.7.48 | Video interface | ONVIF |  | - | 8. | 7. | 48 | 8 | 7 | 48
8.7.49 | Resolution | Full frame rate, full color, H.264/MJPEG, up to 30fps |  | - | 8. | 7. | 49 | 8 | 7 | 49
8.7.50 | Built-in IR | Effective distance ≥30 |  | - | 8. | 7. | 50 | 8 | 7 | 50
8.7.51 | Image enhancement | Digital Wide Dynamic Range |  | - | 8. | 7. | 51 | 8 | 7 | 51
8.7.52 | Image quality | Tru day/night with mechanical IR cut filter |  | - | 8. | 7. | 52 | 8 | 7 | 52
8.7.53 | Resolution/Quality | 4Megapixel (1920x1080) |  | - | 8. | 7. | 53 | 8 | 7 | 53
8.7.54 | Zome/Focus | Remote |  | - | 8. | 7. | 54 | 8 | 7 | 54
8.7.55 | Lens type | Motorised vari-focal |  | - | 8. | 7. | 55 | 8 | 7 | 55
8.7.56 | Focal length | 2.7-12 |  | mm | 8. | 7. | 56 | 8 | 7 | 56
8.7.57 | Time | Embedded real-time clock, NTP Client |  | - | 8. | 7. | 57 | 8 | 7 | 57
8.7.58 | Ingress Protection & Vandal Resistance rating | IP67, IK10 |  | - | 8. | 7. | 58 | 8 | 7 | 58
8.7.59 | Support smart function |  |  |  | 8. | 7. | 59 | 8 | 7 | 59
8.7.60 | Intrusion detection | Yes |  | - | 8. | 7. | 60 | 8 | 7 | 60
8.7.61 | Line crossing detection | Yes |  | - | 8. | 7. | 61 | 8 | 7 | 61
8.7.62 | Motion detection human and vehicle targets classification) | Yes |  | - | 8. | 7. | 62 | 8 | 7 | 62
8.7.63 | Video tampering alarm | Yes |  | - | 8. | 7. | 63 | 8 | 7 | 63
8.7.64 | Exception alarm | Yes |  | - | 8. | 7. | 64 | 8 | 7 | 64
8.7.65 | Face detection | Yes |  | - | 8. | 7. | 65 | 8 | 7 | 65
8.7.66 | Scene change detection | Yes |  | - | 8. | 7. | 66 | 8 | 7 | 66
8.7.67 | Audio exception detection | Yes |  | - | 8. | 7. | 67 | 8 | 7 | 67
8.7.68 | Dynamic analysis as alarm trigging function | Yes |  | - | 8. | 7. | 68 | 8 | 7 | 68
8.7.69 | Pan Tilt Zoom (PTZ) Camera complete with accessories |  |  |  | 8. | 7. | 69 | 8 | 7 | 69
8.7.70 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 70 | 8 | 7 | 70
8.7.71 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 71 | 8 | 7 | 71
8.7.72 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 72 | 8 | 7 | 72
8.7.73 | Video interface | ONVIF |  | - | 8. | 7. | 73 | 8 | 7 | 73
8.7.74 | Focal length | 6.0 - 252 |  | mm | 8. | 7. | 74 | 8 | 7 | 74
8.7.75 | IR light MTBF reach | Up to 30 000 |  | h | 8. | 7. | 75 | 8 | 7 | 75
8.7.76 | IR mode | Smart |  | - | 8. | 7. | 76 | 8 | 7 | 76
8.7.77 | Minimum illumination | 0 |  | lx | 8. | 7. | 77 | 8 | 7 | 77
8.7.78 | Supplement light type | IR |  | - | 8. | 7. | 78 | 8 | 7 | 78
8.7.79 | Supplement light range | 400 |  | m | 8. | 7. | 79 | 8 | 7 | 79
8.7.80 | Defog | Optical defog |  | - | 8. | 7. | 80 | 8 | 7 | 80
8.7.81 | Basic event |  |  | - | 8. | 7. | 81 | 8 | 7 | 81
8.7.82 | Motion detection | Yes |  | - | 8. | 7. | 82 | 8 | 7 | 82
8.7.83 | Video tampering alarm | Yes |  | - | 8. | 7. | 83 | 8 | 7 | 83
8.7.84 | Alarm input and output | Yes |  | - | 8. | 7. | 84 | 8 | 7 | 84
8.7.85 | Exception alarm | Yes |  | - | 8. | 7. | 85 | 8 | 7 | 85
8.7.86 | Smart event |  |  |  | 8. | 7. | 86 | 8 | 7 | 86
8.7.87 | Line crossing detection | Yes |  | - | 8. | 7. | 87 | 8 | 7 | 87
8.7.88 | Region entrance detection | Yes |  | - | 8. | 7. | 88 | 8 | 7 | 88
8.7.89 | Unattended baggage detection | Yes |  | - | 8. | 7. | 89 | 8 | 7 | 89
8.7.90 | Object removal detection | Yes |  | - | 8. | 7. | 90 | 8 | 7 | 90
8.7.91 | Intrusiondetection | Yes |  | - | 8. | 7. | 91 | 8 | 7 | 91
8.7.92 | Region exiting detection | Yes |  | - | 8. | 7. | 92 | 8 | 7 | 92
8.7.93 | Vandal-proof alarm | Yes |  | - | 8. | 7. | 93 | 8 | 7 | 93
8.7.94 | Audio exception detection | Yes |  | - | 8. | 7. | 94 | 8 | 7 | 94
8.7.95 | Smart tracking |  |  |  | 8. | 7. | 95 | 8 | 7 | 95
8.7.96 | Manual tracking | Yes |  | - | 8. | 7. | 96 | 8 | 7 | 96
8.7.97 | Auto-tracking | Yes |  | - | 8. | 7. | 97 | 8 | 7 | 97
8.7.98 | Tracking takeover linked tracking capture | Yes |  | - | 8. | 7. | 98 | 8 | 7 | 98
8.7.99 | Alarm linkage, Alarm actions |  |  |  | 8. | 7. | 99 | 8 | 7 | 99
8.7.100 | Preset | Yes |  | - | 8. | 7. | 100 | 8 | 7 | 100
8.7.101 | Patrol scan | Yes |  | - | 8. | 7. | 101 | 8 | 7 | 101
8.7.102 | Pattern scan | Yes |  | - | 8. | 7. | 102 | 8 | 7 | 102
8.7.103 | Memory Card Video Record | Yes |  | - | 8. | 7. | 103 | 8 | 7 | 103
8.7.104 | Trigger recording | Yes |  | - | 8. | 7. | 104 | 8 | 7 | 104
8.7.105 | Notify surveillance center | Yes |  | - | 8. | 7. | 105 | 8 | 7 | 105
8.7.106 | Upload to FTP/Memory card/NAS | Yes |  | - | 8. | 7. | 106 | 8 | 7 | 106
8.7.107 | Send email | Yes |  | - | 8. | 7. | 107 | 8 | 7 | 107
8.7.108 | 3D intelligent positioning function | Yes |  | - | 8. | 7. | 108 | 8 | 7 | 108
8.7.109 | Ingress protection and vandal resistance rating | IP67, IK10 |  | - | 8. | 7. | 109 | 8 | 7 | 109
8.7.110 | Power-off memory function | Restore PTZ & Lens status after reeboot |  | - | 8. | 7. | 110 | 8 | 7 | 110
8.7.111 | Thermal & Optical Bi-spectrum Stable PTZ Camera |  |  |  | 8. | 7. | 111 | 8 | 7 | 111
8.7.112 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 112 | 8 | 7 | 112
8.7.113 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 113 | 8 | 7 | 113
8.7.114 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 114 | 8 | 7 | 114
8.7.115 | Thermal | 640x512, 17 µm |  | - | 8. | 7. | 115 | 8 | 7 | 115
8.7.116 | Optical | 1920x1080 |  | - | 8. | 7. | 116 | 8 | 7 | 116
8.7.117 | Thermal | 75 / 100 / 30-150 / 45-180 |  | mm | 8. | 7. | 117 | 8 | 7 | 117
8.7.118 | Optical | H (5.6-208) / C(6.7-330) / E(12.5-775) |  | mm | 8. | 7. | 118 | 8 | 7 | 118
8.7.119 | VCA |  |  |  | 8. | 7. | 119 | 8 | 7 | 119
8.7.120 | Line crossing detection | Yes |  | - | 8. | 7. | 120 | 8 | 7 | 120
8.7.121 | Intrusion detection | Yes |  | - | 8. | 7. | 121 | 8 | 7 | 121
8.7.122 | Region entrance detection | Yes |  | - | 8. | 7. | 122 | 8 | 7 | 122
8.7.123 | Region exiting detection | Yes |  | - | 8. | 7. | 123 | 8 | 7 | 123
8.7.124 | Smart tracking linkage (Thermal+Optical) | Yes |  | - | 8. | 7. | 124 | 8 | 7 | 124
8.7.125 | Fire detection | Yes |  | - | 8. | 7. | 125 | 8 | 7 | 125
8.7.126 | Temperature measurement range | -20-150 |  | OC | 8. | 7. | 126 | 8 | 7 | 126
8.7.127 | Working temperature | -40-65 |  | OC | 8. | 7. | 127 | 8 | 7 | 127
8.7.128 | Ingess protection | IP66 |  | - | 8. | 7. | 128 | 8 | 7 | 128
8.7.129 | Management Software |  |  |  | 8. | 7. | 129 | 8 | 7 | 129
8.7.130 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 130 | 8 | 7 | 130
8.7.131 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 131 | 8 | 7 | 131
8.7.132 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 132 | 8 | 7 | 132
8.7.133 | PTZ control | turn remote pan/tilt up, down, left or right, adjust lens aperture and focal length |  | - | 8. | 7. | 133 | 8 | 7 | 133
8.7.134 | Multiple PTZ control modes | use mouse or PC keyboard to make PTZ control; users can choose according their preferences |  | - | 8. | 7. | 134 | 8 | 7 | 134
8.7.135 | PTZ contension | the system allocates contention privileges to users at the same level to ensure one camera is under the control of one user at one time |  | - | 8. | 7. | 135 | 8 | 7 | 135
8.7.136 | 3D positioning | users can drag the mouse on the surveillance image to control the camera surveillance direction and view angle, zoom in/out or focus on an object |  | - | 8. | 7. | 136 | 8 | 7 | 136
8.7.137 | Camera parameter configuration | configure parameters of remote cameras such as video parameters (resolution, code stream, frame rate) and alarm parameters (motion detection, privacy mask) |  | - | 8. | 7. | 137 | 8 | 7 | 137
8.7.138 | One-screen surveillance | multiple remote sites or multiple areas of one site are under real-time surveillance on one screen; 1/4/9 picture and full screen browsing are available |  | - | 8. | 7. | 138 | 8 | 7 | 138
8.7.139 | Panorama video browsing | click primary equipment or a component on the plane figure to open the real-time videos of its interlinked cameras |  | - | 8. | 7. | 139 | 8 | 7 | 139
8.7.140 | Dual-service view | both surveillance view (primary equipment view) and maintenance view (site view) are available for direct operations |  | - | 8. | 7. | 140 | 8 | 7 | 140
8.7.141 | Patrol | all accessed cameras shall support video patrol function with configurable parameters |  | - | 8. | 7. | 141 | 8 | 7 | 141
8.7.142 | Preset and home preset | each surveillance spot (if only the camera supports preset function) is able to invoke presets during linkage, patrol and video browsing; home preset function is available, that means the pan/tilt returns to its home preset position after a preset timespan |  | - | 8. | 7. | 142 | 8 | 7 | 142
8.7.143 | Device tree | the device tree function helps in directly locating the surveillance spots and shows device status such as offline, alarm, etc. |  | - | 8. | 7. | 143 | 8 | 7 | 143
8.7.144 | Video recovery | after checking other functions and users shift back to the real-time surveillance interface, the system shall recover the real-time videos |  | - | 8. | 7. | 144 | 8 | 7 | 144
8.7.145 | Manual video storage | : users can store real-time videos while browsing if necessary, to save important clues and evidences |  | - | 8. | 7. | 145 | 8 | 7 | 145
8.7.146 | All-day storage | Important scenarios shall need 24/7 surveillance footages for future investigation and review |  | - | 8. | 7. | 146 | 8 | 7 | 146
8.7.147 | Timing storage | users can store videos within some specific timespan to save storage space |  | - | 8. | 7. | 147 | 8 | 7 | 147
8.7.148 | Alarm-storage linkage | external alarms or internal alarms like motion detection alarm will trigger the video recording to keep evidences; It shall be possible to pre-record 5~180s prior to the alarm to keep the whole activity before and after for analysis; pre-record time shall be configurable |  | - | 8. | 7. | 148 | 8 | 7 | 148
8.7.149 | Footage query | It shall be possible to query footages by surveillance spot, surveillance location, motion/activity, footage storage path, date/time, alarm or combined conditions and to play the wanted footage when it is fetched |  | - | 8. | 7. | 149 | 8 | 7 | 149
8.7.150 | Video playback | It shall be possible to play video online or after downloading them to the local system according to alarm index, normal play, fast play, slow play, frame play, drag, pause, snapshot or multi-shot the footages |  | - | 8. | 7. | 150 | 8 | 7 | 150
8.7.151 | Network Switch |  |  |  | 8. | 7. | 151 | 8 | 7 | 151
8.7.152 | Rackmount Switches |  |  |  | 8. | 7. | 152 | 8 | 7 | 152
8.7.153 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 153 | 8 | 7 | 153
8.7.154 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 154 | 8 | 7 | 154
8.7.155 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 155 | 8 | 7 | 155
8.7.156 | Rackmount Managed Gigabit Ethernet/Fibre Optic Switch | Yes |  | - | 8. | 7. | 156 | 8 | 7 | 156
8.7.157 | Industriel design and compliance | Yes |  | - | 8. | 7. | 157 | 8 | 7 | 157
8.7.158 | 10/100/1000 | Yes |  | Mbps | 8. | 7. | 158 | 8 | 7 | 158
8.7.159 | Support for SFP modules provide uplink connectivety supporting | 100BASE-LX, 100BASE-FX, 1000-SX, 1000BASE-LX, 1000BASE-ZX |  | - | 8. | 7. | 159 | 8 | 7 | 159
8.7.160 | Transparante IT integration with support of Layer 3 functionality in IP Service software | Yes |  | - | 8. | 7. | 160 | 8 | 7 | 160
8.7.161 | DIN rail Mount Switches |  |  |  | 8. | 7. | 161 | 8 | 7 | 161
8.7.162 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 162 | 8 | 7 | 162
8.7.163 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 163 | 8 | 7 | 163
8.7.164 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 164 | 8 | 7 | 164
8.7.165 | Rugged switches in robust industrial design | Yes |  | - | 8. | 7. | 165 | 8 | 7 | 165
8.7.166 | Built for harsh environments and temperature range | -40-75 |  | OC | 8. | 7. | 166 | 8 | 7 | 166
8.7.167 | Convection cooled without fans or moving parts | Yes |  | - | 8. | 7. | 167 | 8 | 7 | 167
8.7.168 | Hardened for vibration, shock and surge, and electric noisee immunity | Yes |  | - | 8. | 7. | 168 | 8 | 7 | 168
8.7.169 | Complies with multi-industry specifications for automation and substation | Yes |  | - | 8. | 7. | 169 | 8 | 7 | 169
8.7.170 | Improves uptime, performance, and safety of industrial systems and equipment | Yes |  | - | 8. | 7. | 170 | 8 | 7 | 170
8.7.171 | Operator Workstation PC |  |  |  | 8. | 7. | 171 | 8 | 7 | 171
8.7.172 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 172 | 8 | 7 | 172
8.7.173 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 173 | 8 | 7 | 173
8.7.174 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 174 | 8 | 7 | 174
8.7.175 | Processor | Intel Core i/, 9th Generation |  | - | 8. | 7. | 175 | 8 | 7 | 175
8.7.176 | RAM | 16 |  | GB | 8. | 7. | 176 | 8 | 7 | 176
8.7.177 | Operating software | Windows 10 Pro, 64 bit |  | - | 8. | 7. | 177 | 8 | 7 | 177
8.7.178 | OS Hard Disk | 256 GB SSD plus 4 TB 3.5 inch SATA |  | - | 8. | 7. | 178 | 8 | 7 | 178
8.7.179 | Minimum Dual Graphic Display | Yes |  | - | 8. | 7. | 179 | 8 | 7 | 179
8.7.180 | Graphic memory | 4 |  | GB | 8. | 7. | 180 | 8 | 7 | 180
8.7.181 | HDMI Outputs | 4 |  | Nos. | 8. | 7. | 181 | 8 | 7 | 181
8.7.182 | Keyboard and Mouse | Cordless |  | - | 8. | 7. | 182 | 8 | 7 | 182
8.7.183 | Network interface | 100/1000 BaseT RJ45 |  | - | 8. | 7. | 183 | 8 | 7 | 183
8.7.184 | Workstation monitor | 24 inch |  | - | 8. | 7. | 184 | 8 | 7 | 184
8.7.185 | CCTV Surveillance Keyboard |  |  |  | 8. | 7. | 185 | 8 | 7 | 185
8.7.186 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 186 | 8 | 7 | 186
8.7.187 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 187 | 8 | 7 | 187
8.7.188 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 188 | 8 | 7 | 188
8.7.189 | ONVIF compliant complete with DC power supply and communication cable | Yes |  | - | 8. | 7. | 189 | 8 | 7 | 189
8.7.190 | Seamless control of live and recorded video | Yes |  | - | 8. | 7. | 190 | 8 | 7 | 190
8.7.191 | Desktop keyboard with 3 axis joystick for pan/tilt and zoom | Yes |  | - | 8. | 7. | 191 | 8 | 7 | 191
8.7.192 | Full variable PTZ control of PTZ domes | Yes |  | - | 8. | 7. | 192 | 8 | 7 | 192
8.7.193 | Full control of Controle Center virtual matrix | Yes |  | - | 8. | 7. | 193 | 8 | 7 | 193
8.7.194 | Multi-function keys | Yes |  | - | 8. | 7. | 194 | 8 | 7 | 194
8.7.195 | LCD graphic display | Yes |  | - | 8. | 7. | 195 | 8 | 7 | 195
8.7.196 | Display Screen |  |  |  | 8. | 7. | 196 | 8 | 7 | 196
8.7.197 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 197 | 8 | 7 | 197
8.7.198 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 198 | 8 | 7 | 198
8.7.199 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 199 | 8 | 7 | 199
8.7.200 | CCTV Display | 55 inch UHD |  | - | 8. | 7. | 200 | 8 | 7 | 200
8.7.201 | Input | HDMI |  | - | 8. | 7. | 201 | 8 | 7 | 201
8.7.202 | Resolution | 1920x1080 |  | - | 8. | 7. | 202 | 8 | 7 | 202
8.7.203 | Speakers | 2 |  | Nos. | 8. | 7. | 203 | 8 | 7 | 203
8.7.204 | Connectivity | HDMI, USB |  | - | 8. | 7. | 204 | 8 | 7 | 204
8.7.205 | System Controller |  |  |  | 8. | 7. | 205 | 8 | 7 | 205
8.7.206 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 206 | 8 | 7 | 206
8.7.207 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 207 | 8 | 7 | 207
8.7.208 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 208 | 8 | 7 | 208
8.7.209 | Each system controller/cluster controller shall be capable of storing | 10000 |  | tags | 8. | 7. | 209 | 8 | 7 | 209
8.7.210 | Each system controller/cluster controller shall be capable of buffering | 100000 |  | transactions | 8. | 7. | 210 | 8 | 7 | 210
8.7.211 | The ACS System Controller shall support physical devices connected via RS485 terminal communication bus, TCP/IP or property solution | 64 |  | Nos. | 8. | 7. | 211 | 8 | 7 | 211
8.7.212 | Door Controler |  |  |  | 8. | 7. | 212 | 8 | 7 | 212
8.7.213 | Shall have the following, or a combination of the following, components built in to facilitate the opening of doors and the monitoring of doors |  |  |  | 8. | 7. | 213 | 8 | 7 | 213
8.7.214 | Dry contact relays. | Yes |  | - | 8. | 7. | 214 | 8 | 7 | 214
8.7.215 | Digital inputs. | Yes |  | - | 8. | 7. | 215 | 8 | 7 | 215
8.7.216 | Ports for connection to ACS readers. | Yes |  | - | 8. | 7. | 216 | 8 | 7 | 216
8.7.217 | Communications port for 3rd Party readers. | Yes |  | - | 8. | 7. | 217 | 8 | 7 | 217
8.7.218 | RS485 and SBUS connectivity | Yes |  | - | 8. | 7. | 218 | 8 | 7 | 218
8.7.219 | Each Door Controller shall support card readers | 2 |  | Nos. | 8. | 7. | 219 | 8 | 7 | 219
8.7.220 | The ACS shall support the following connectivity options between System Controllers |  |  |  | 8. | 7. | 220 | 8 | 7 | 220
8.7.221 | RS485 – with connectivity speed | 38400 |  | Baud | 8. | 7. | 221 | 8 | 7 | 221
8.7.222 | Ethernet connectivity support | 100 |  | Mbps | 8. | 7. | 222 | 8 | 7 | 222
8.7.223 | Serial BUS connectivity speed | 9600 |  | Baud | 8. | 7. | 223 | 8 | 7 | 223
8.7.224 | Electro-magnetic Lock |  |  |  | 8. | 7. | 224 | 8 | 7 | 224
8.7.225 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 225 | 8 | 7 | 225
8.7.226 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 226 | 8 | 7 | 226
8.7.227 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 227 | 8 | 7 | 227
8.7.228 | Holding force | 300 |  | kg | 8. | 7. | 228 | 8 | 7 | 228
8.7.229 | Ingress protection | Designed to resist ingress of water |  | - | 8. | 7. | 229 | 8 | 7 | 229
8.7.230 | Power supply | 2025-12-24 |  | VDC | 8. | 7. | 230 | 8 | 7 | 230
8.7.231 | Status LED indicator | Green-Locked, Red-Unlocked |  | - | 8. | 7. | 231 | 8 | 7 | 231
8.7.232 | Abrasion-proof material | Yes |  | - | 8. | 7. | 232 | 8 | 7 | 232
8.7.233 | Equipped with internal voltage dependent resistor (MOV) | Yes |  | - | 8. | 7. | 233 | 8 | 7 | 233
8.7.234 | Unlock method | Current interruption |  | - | 8. | 7. | 234 | 8 | 7 | 234
8.7.235 | Suitable for | wooden, Glass, Metal and Fireproof doors |  | - | 8. | 7. | 235 | 8 | 7 | 235
8.7.236 | Proximity Card Reader |  |  |  | 8. | 7. | 236 | 8 | 7 | 236
8.7.237 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 237 | 8 | 7 | 237
8.7.238 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 238 | 8 | 7 | 238
8.7.239 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 239 | 8 | 7 | 239
8.7.240 | Read range Indoor/Outdoor | 5/30 |  | cm | 8. | 7. | 240 | 8 | 7 | 240
8.7.241 | Input voltage | 5-17 |  | VDC | 8. | 7. | 241 | 8 | 7 | 241
8.7.242 | Key Features |  |  |  | 8. | 7. | 242 | 8 | 7 | 242
8.7.243 | Single bi-coloured red/green status LED | Yes |  | - | 8. | 7. | 243 | 8 | 7 | 243
8.7.244 | Read/Write Tag capability for various Tag types | Slim Tags (Read Only), Omega Tags (Read Only), WriTag 128 (Read/Write) and WriTag 2048 (Read/Write) |  | - | 8. | 7. | 244 | 8 | 7 | 244
8.7.245 | Card Enrollere |  |  |  | 8. | 7. | 245 | 8 | 7 | 245
8.7.246 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 246 | 8 | 7 | 246
8.7.247 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 247 | 8 | 7 | 247
8.7.248 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 248 | 8 | 7 | 248
8.7.249 | Contactless passive card writer | Yes |  | - | 8. | 7. | 249 | 8 | 7 | 249
8.7.250 | Blank check function | Yes |  | - | 8. | 7. | 250 | 8 | 7 | 250
8.7.251 | Direct connection to Personal Computer | Yes |  | - | 8. | 7. | 251 | 8 | 7 | 251
8.7.252 | Card Drop Box Unit |  |  |  | 8. | 7. | 252 | 8 | 7 | 252
8.7.253 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 253 | 8 | 7 | 253
8.7.254 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 254 | 8 | 7 | 254
8.7.255 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 255 | 8 | 7 | 255
8.7.256 | Connects directly to the RS485 Terminal Bus | Yes |  | - | 8. | 7. | 256 | 8 | 7 | 256
8.7.257 | Stainless steel, powder coated frame | Yes |  | - | 8. | 7. | 257 | 8 | 7 | 257
8.7.258 | Unit Includes |  |  |  | 8. | 7. | 258 | 8 | 7 | 258
8.7.259 | Tag capture unit | Yes |  | - | 8. | 7. | 259 | 8 | 7 | 259
8.7.260 | Lockable door | Yes |  | - | 8. | 7. | 260 | 8 | 7 | 260
8.7.261 | Internal 125kHz reader | Yes |  | - | 8. | 7. | 261 | 8 | 7 | 261
8.7.262 | 2 x Relays | Yes |  | - | 8. | 7. | 262 | 8 | 7 | 262
8.7.263 | 4 x Digital inputs (2 x Door Open sensor inputs and 2 x Request to Enter/Exit input) | Yes |  | - | 8. | 7. | 263 | 8 | 7 | 263
8.7.264 | Buzzer | Yes |  | - | 8. | 7. | 264 | 8 | 7 | 264
8.7.265 | A second Antenna Reader can be connected for permanent tag holders | Yes |  | - | 8. | 7. | 265 | 8 | 7 | 265
8.7.266 | Key Futures |  |  |  | 8. | 7. | 266 | 8 | 7 | 266
8.7.267 | Reads selected third party Credit Card Tags. | Yes |  | - | 8. | 7. | 267 | 8 | 7 | 267
8.7.268 | Reads Read/Write Tags. | Yes |  | - | 8. | 7. | 268 | 8 | 7 | 268
8.7.269 | Connection to ONE Antenna Reader, to "Reader 2", | Yes |  | - | 8. | 7. | 269 | 8 | 7 | 269
8.7.270 | An excellent user interface consisting of 9 LED "Diagnostic Indicators" | Yes |  | - | 8. | 7. | 270 | 8 | 7 | 270
8.7.271 | An external RS485 Terminal Communications Bus Interface. | Yes |  | - | 8. | 7. | 271 | 8 | 7 | 271
8.7.272 | A software utility to upgrade Firmware while installed on-site, without removal of the drop box | Yes |  | - | 8. | 7. | 272 | 8 | 7 | 272
8.7.273 | Proximity Card |  |  |  | 8. | 7. | 273 | 8 | 7 | 273
8.7.274 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 274 | 8 | 7 | 274
8.7.275 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 275 | 8 | 7 | 275
8.7.276 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 276 | 8 | 7 | 276
8.7.277 | ISO Credit card size and thickness | Yes |  | - | 8. | 7. | 277 | 8 | 7 | 277
8.7.278 | Printing company logo with graphics (front & rear) | Yes |  | - | 8. | 7. | 278 | 8 | 7 | 278
8.7.279 | Read Range: Indoor/Outdoor | 5/30 |  | cm | 8. | 7. | 279 | 8 | 7 | 279
8.7.280 | Working Temperature | -5-65 |  | OC | 8. | 7. | 280 | 8 | 7 | 280
8.7.281 | Manual Over-rider key switch |  |  |  | 8. | 7. | 281 | 8 | 7 | 281
8.7.282 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 282 | 8 | 7 | 282
8.7.283 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 283 | 8 | 7 | 283
8.7.284 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 284 | 8 | 7 | 284
8.7.285 | Double pole on/off key switch | Yes |  | - | 8. | 7. | 285 | 8 | 7 | 285
8.7.286 | Key removable in on and off positions. | Yes |  | - | 8. | 7. | 286 | 8 | 7 | 286
8.7.287 | Radial Key Switch, on/off, opposing double poles | Yes |  | - | 8. | 7. | 287 | 8 | 7 | 287
8.7.288 | Slim-line key box (25 mm) for easy installation on narrow door frames | 25 |  | mm | 8. | 7. | 288 | 8 | 7 | 288
8.7.289 | On/off LED indication | Yes |  | - | 8. | 7. | 289 | 8 | 7 | 289
8.7.290 | Request to enter/exit button |  |  |  | 8. | 7. | 290 | 8 | 7 | 290
8.7.291 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 291 | 8 | 7 | 291
8.7.292 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 292 | 8 | 7 | 292
8.7.293 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 293 | 8 | 7 | 293
8.7.294 | No touch exit sensor |  |  |  | 8. | 7. | 294 | 8 | 7 | 294
8.7.295 | Operating Voltage | 12 |  | VDC | 8. | 7. | 295 | 8 | 7 | 295
8.7.296 | Contacts | NO and NC |  | - | 8. | 7. | 296 | 8 | 7 | 296
8.7.297 | Touch to exit | Yes |  | - | 8. | 7. | 297 | 8 | 7 | 297
8.7.298 | Ingress protection | IP68 |  | - | 8. | 7. | 298 | 8 | 7 | 298
8.7.299 | Sensitive distance | 3-15 |  | cm | 8. | 7. | 299 | 8 | 7 | 299
8.7.300 | Puch exit button |  |  |  | 8. | 7. | 300 | 8 | 7 | 300
8.7.301 | Heavy duty | Yes |  | - | 8. | 7. | 301 | 8 | 7 | 301
8.7.302 | Normally open, pulsed push button | Yes |  | - | 8. | 7. | 302 | 8 | 7 | 302
8.7.303 | Emergency door release |  |  |  | 8. | 7. | 303 | 8 | 7 | 303
8.7.304 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 304 | 8 | 7 | 304
8.7.305 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 305 | 8 | 7 | 305
8.7.306 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 306 | 8 | 7 | 306
8.7.307 | Green Call Point | Resettable |  | - | 8. | 7. | 307 | 8 | 7 | 307
8.7.308 | Mechanical emergency door release switch | Yes |  | - | 8. | 7. | 308 | 8 | 7 | 308
8.7.309 | Surface mount box with conduit knockout | Yes |  | - | 8. | 7. | 309 | 8 | 7 | 309
8.7.310 | Manual key resettable actuator | Yes |  | - | 8. | 7. | 310 | 8 | 7 | 310
8.7.311 | Push-point activation | Yes |  | - | 8. | 7. | 311 | 8 | 7 | 311
8.7.312 | Includes hinged, clear plastic protective cover | Yes |  | - | 8. | 7. | 312 | 8 | 7 | 312
8.7.313 | Colour | Green |  | - | 8. | 7. | 313 | 8 | 7 | 313
8.7.314 | Turnstile |  |  |  | 8. | 7. | 314 | 8 | 7 | 314
8.7.315 | Maker’s type and reference | To be stated by Bidder |  | - | 8. | 7. | 315 | 8 | 7 | 315
8.7.316 | Manufacturer | To be stated by Bidder |  | - | 8. | 7. | 316 | 8 | 7 | 316
8.7.317 | Country of origin | To be stated by Bidder |  | - | 8. | 7. | 317 | 8 | 7 | 317
8.7.318 | Power supply | 230 |  | VAC | 8. | 7. | 318 | 8 | 7 | 318
8.7.319 | Protection rating | IP40 |  | - | 8. | 7. | 319 | 8 | 7 | 319
8.7.320 | Operating temperatures | -20-55 |  | OC | 8. | 7. | 320 | 8 | 7 | 320
8.7.321 | Automatic Sliding Gate Motor |  |  |  | 8. | 7. | 321 | 8 | 7 | 321
8.7.322 | Input Voltage | 240 ±10% |  | VAC | 8. | 7. | 322 | 8 | 7 | 322
8.7.323 | Frequency | 50 |  | Hz | 8. | 7. | 323 | 8 | 7 | 323
8.7.324 | Current consumption | 250 |  | mA | 8. | 7. | 324 | 8 | 7 | 324
8.7.325 | Battery charger voltage output | 27±1% |  | VDC | 8. | 7. | 325 | 8 | 7 | 325
8.7.326 | Battery charger current output | 1.8 |  | A | 8. | 7. | 326 | 8 | 7 | 326
8.7.327 | Minimum number of operations per day | 350 |  | Nos. | 8. | 7. | 327 | 8 | 7 | 327
8.7.328 | Duty cycle - Mains present | 45 |  | % | 8. | 7. | 328 | 8 | 7 | 328
8.7.329 | Motor voltage | 24 |  | VDC | 8. | 7. | 329 | 8 | 7 | 329
8.7.330 | Battery for Motor power supply, Voltage | 2x12 |  | VDC | 8. | 7. | 330 | 8 | 7 | 330
8.7.331 | Battery for Motor power supply, Capacity | 7.2 |  | Ah | 8. | 7. | 331 | 8 | 7 | 331
8.7.332 | Current consumption (motor at rated load) | 8 |  | A | 8. | 7. | 332 | 8 | 7 | 332
8.7.333 | Motor push force – starting | 40 |  | kgf | 8. | 7. | 333 | 8 | 7 | 333
8.7.334 | Motor push force – rated | 30 |  | kgf | 8. | 7. | 334 | 8 | 7 | 334
8.7.335 | Gate mass – maximum | 1000 |  | kg | 8. | 7. | 335 | 8 | 7 | 335
[8 empty] | 8 | 7 | 336 | tom rad
9. | Control and Protection Equipment |  |  |  | 9. |  |  | 9 | 7 | 337 | R1
9.1. | Three Phase Programmable Meter |  |  |  | 9. | 1. |  | 9 | 1 | 338 | R2
[8 empty] | 9 | 1 | 339 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 1 | 340 | R3
9.1.1 | Maker’s name | Bidder to state |  | - | 9. | 1. | 1 | 9 | 1 | 1
9.1.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 1. | 2 | 9 | 1 | 2
9.1.3 | Country of origin | Bidder to state |  | - | 9. | 1. | 3 | 9 | 1 | 3
9.1.4 | Description | Energy meter |  | - | 9. | 1. | 4 | 9 | 1 | 4
9.1.5 | Meter type | Landis + Gyr (E880) or CEWE Prometer 540 or equivalent |  | - | 9. | 1. | 5 | 9 | 1 | 5
9.1.6 | Meter type for interconnector line | Microstar P2000-T or compatible |  | - | 9. | 1. | 6 | 9 | 1 | 6
9.1.7 | Standard | IEC61850 compliant |  | - | 9. | 1. | 7 | 9 | 1 | 7
9.1.8 | Current Rating, In | 0,01 -1A OR 0,05-5A User programmable to any CT ratio |  | - | 9. | 1. | 8 | 9 | 1 | 8
9.1.9 | Accuracy Class | Class 0.2s or better |  | - | 9. | 1. | 9 | 9 | 1 | 9
9.1.10 | Auxiliary Supply | 40 – 240AC, 40 – 300DC |  | V | 9. | 1. | 10 | 9 | 1 | 10
9.1.11 | Capabilities | Import and Export measuring of; MWh, MVAh, MVArh and the Maximum Demands (MVA, MW, MVAr) with date & time of occurrence |  | - | 9. | 1. | 11 | 9 | 1 | 11
9.1.12 | Data logging/profiling | YES |  | - | 9. | 1. | 12 | 9 | 1 | 12
9.1.13 | Register Type | LCD (8 digit electronic display) |  | - | 9. | 1. | 13 | 9 | 1 | 13
9.1.14 | CT Polarity reversal | Able to detect and record date of occurrence and restoration with phase identification |  | - | 9. | 1. | 14 | 9 | 1 | 14
9.1.15 | Installation | At least two seals |  | - | 9. | 1. | 15 | 9 | 1 | 15
9.1.16 | Integrity | Inaccessible without breaking seals |  | - | 9. | 1. | 16 | 9 | 1 | 16
9.1.17 | Communication Interface | Optical interface, Ethernet |  | - | 9. | 1. | 17 | 9 | 1 | 17
9.1.18 | Protocol | IEC 62056/IEC 61850 |  | - | 9. | 1. | 18 | 9 | 1 | 18
9.1.19 | Bi-directional and protocol to be of type | Flag as per IEC 62056-21, |  | - | 9. | 1. | 19 | 9 | 1 | 19
9.1.20 | Port for remote communication. | Ethernet, RS485/GPRS/GSM |  | - | 9. | 1. | 20 | 9 | 1 | 20
9.1.21 | Communication module | IEC 61850 and 4G |  | - | 9. | 1. | 21 | 9 | 1 | 21
9.1.22 | Applicable electronic Meter software with optical probe | Windows based software for programming and downloading. The3meter should be fully user programmable and downloadable. |  | - | 9. | 1. | 22 | 9 | 1 | 22
9.1.23 | Time of Use Capabilities | YES |  | - | 9. | 1. | 23 | 9 | 1 | 23
9.1.24 | Historical Data | >12 months of sets of historical data |  | - | 9. | 1. | 24 | 9 | 1 | 24
9.1.25 | Quality Assurance Certificate | To be provided with the Quotation |  | - | 9. | 1. | 25 | 9 | 1 | 25
9.1.26 | Applicable standards | IEC 62052-11, 62053-21, 62053-22, 62053-23, 62053-61; 62056, 61850 |  | - | 9. | 1. | 26 | 9 | 1 | 26
9.1.27 | Must be easily Integrated into existing system | YES |  | - | 9. | 1. | 27 | 9 | 1 | 27
[8 empty] | 9 | 1 | 28 | tom rad
9.2. | Three Phase Power Quality Meter |  |  |  | 9. | 2. |  | 9 | 2 | 29 | R2
[8 empty] | 9 | 2 | 30 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 2 | 31 | R3
9.2.1 | Maker’s name | Bidder to state |  | - | 9. | 2. | 1 | 9 | 2 | 1
9.2.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 2. | 2 | 9 | 2 | 2
9.2.3 | Country of origin | Bidder to state |  | - | 9. | 2. | 3 | 9 | 2 | 3
9.2.4 | Description | PQM |  | - | 9. | 2. | 4 | 9 | 2 | 4
9.2.5 | Meter type | Power quality meter as Unipower 2210 or equivalent |  | - | 9. | 2. | 5 | 9 | 2 | 5
9.2.6 | Accuracy Class | Class 0.2s or better |  | - | 9. | 2. | 6 | 9 | 2 | 6
9.2.7 | Capabilities | Import and Export measuring of; MWh, MVAh, MVArh and the Maximum Demands (MVA, MW, MVAr) with date & time of occurrence |  | - | 9. | 2. | 7 | 9 | 2 | 7
9.2.8 | Data logging/profiling | YES |  | - | 9. | 2. | 8 | 9 | 2 | 8
9.2.9 | Register Type | LCD (8 digit electronic display) |  | - | 9. | 2. | 9 | 9 | 2 | 9
9.2.10 | Integration Period | User programmable (1 to 60 minutes) |  | - | 9. | 2. | 10 | 9 | 2 | 10
9.2.11 | System/Circuit Type | 3P3W or 3P4W Programmable |  | - | 9. | 2. | 11 | 9 | 2 | 11
9.2.12 | CT Polarity reversal | Able to detect and record date of occurrence and restoration with phase identification |  | - | 9. | 2. | 12 | 9 | 2 | 12
9.2.13 | Installation | At least two seals |  | - | 9. | 2. | 13 | 9 | 2 | 13
9.2.14 | Integrity | Inaccessible without breaking seals |  | - | 9. | 2. | 14 | 9 | 2 | 14
9.2.15 | Protocol | IEC 62056/IEC 61850 |  | - | 9. | 2. | 15 | 9 | 2 | 15
9.2.16 | Communication Interface | Optical interface, Ethernet |  | - | 9. | 2. | 16 | 9 | 2 | 16
9.2.17 | Bi-directional and protocol to be of type | Flag as per IEC 62056-21, |  | - | 9. | 2. | 17 | 9 | 2 | 17
9.2.18 | Port for remote communication | Ethernet, RS485/GPRS/GSM |  | - | 9. | 2. | 18 | 9 | 2 | 18
9.2.19 | Communication module | IEC 61850 and 4G |  | - | 9. | 2. | 19 | 9 | 2 | 19
9.2.20 | Applicable electronic Meter software with optical probe | Windows based software for programming and downloading. The meter should be fully user programmable and downloadable. |  | - | 9. | 2. | 20 | 9 | 2 | 20
9.2.21 | Time of Use Capabilities | YES |  | - | 9. | 2. | 21 | 9 | 2 | 21
9.2.22 | Historical Data | >12 months of sets of historical data |  | - | 9. | 2. | 22 | 9 | 2 | 22
9.2.23 | Quality Assurance Certificate | To be provided with the Bid |  | - | 9. | 2. | 23 | 9 | 2 | 23
9.2.24 | Applicable standards | IEC 62052-11, 62053-21, 62053-22, 62053-23, 62053-61, 62056, 61850 |  | - | 9. | 2. | 24 | 9 | 2 | 24
9.2.25 | Must be easily Integrated into existing system | YES |  | - | 9. | 2. | 25 | 9 | 2 | 25
[8 empty] | 9 | 2 | 26 | tom rad
9.3. | Metering Workingstation and Automatic Meter Infrastructure |  |  |  | 9. | 3. |  | 9 | 3 | 27 | R2
[8 empty] | 9 | 3 | 28 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 3 | 29 | R3
9.3.1 | Maker’s name | Bidder to state |  | - | 9. | 3. | 1 | 9 | 3 | 1
9.3.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 3. | 2 | 9 | 3 | 2
9.3.3 | Country of origin | Bidder to state |  | - | 9. | 3. | 3 | 9 | 3 | 3
9.3.4 | Description | AMI |  | - | 9. | 3. | 4 | 9 | 3 | 4
9.3.5 | Workstation Make | Bidder to state |  | - | 9. | 3. | 5 | 9 | 3 | 5
9.3.6 | Single Unit Packaging | Bidder to state |  | - | 9. | 3. | 6 | 9 | 3 | 6
9.3.7 | Efficient Chassis | Bidder to state |  | - | 9. | 3. | 7 | 9 | 3 | 7
9.3.8 | Microsoft Windows 11 Ultimate Edition 64bit OS UK | Yes |  | - | 9. | 3. | 8 | 9 | 3 | 8
9.3.9 | Supported OS lifecycle | Bidder to state |  |  | 9. | 3. | 9 | 9 | 3 | 9
9.3.10 | Latest version of Windows professional 64 Bit Factory Image Recovery | Yes |  | - | 9. | 3. | 10 | 9 | 3 | 10
9.3.11 | Intel Xeon E5-1603 2.80Ghz 10MB 1066 4C CPU | Yes |  | - | 9. | 3. | 11 | 9 | 3 | 11
9.3.12 | 32GB DDR3-1600 ECC (3x2GB) RAM | Yes |  | - | 9. | 3. | 12 | 9 | 3 | 12
9.3.13 | NVIDIA NVS 310 512MB Graphics | Yes |  | - | 9. | 3. | 13 | 9 | 3 | 13
9.3.14 | NVIDIA NVS 310 512MB 2nd Graphics | Yes |  | - | 9. | 3. | 14 | 9 | 3 | 14
9.3.15 | 2TB Drive | Yes |  | - | 9. | 3. | 15 | 9 | 3 | 15
9.3.16 | USB Standard Keyboard | Yes |  | - | 9. | 3. | 16 | 9 | 3 | 16
9.3.17 | USB Optical Scroll Mouse | Yes |  | - | 9. | 3. | 17 | 9 | 3 | 17
9.3.18 | 16X SuperMulti DVDRW SATA 1st ODD | Yes |  | - | 9. | 3. | 18 | 9 | 3 | 18
9.3.19 | Intel CT x1 PCIe NIC | Yes |  | - | 9. | 3. | 19 | 9 | 3 | 19
9.3.20 | 3/3/3 Warranty EURO | Yes |  | - | 9. | 3. | 20 | 9 | 3 | 20
9.3.21 | Country Kit | Yes |  | - | 9. | 3. | 21 | 9 | 3 | 21
9.3.22 | Processor Air Cooling Kit | Yes |  | - | 9. | 3. | 22 | 9 | 3 | 22
9.3.23 | Operating system | Yes |  | - | 9. | 3. | 23 | 9 | 3 | 23
9.3.24 | Latest version of Windows Professional is included in HW above. | Yes |  | - | 9. | 3. | 24 | 9 | 3 | 24
9.3.25 | Latest Version of Microsoft Office | Yes |  | - | 9. | 3. | 25 | 9 | 3 | 25
9.3.26 | McAfee, 1 year SW updates included | Yes |  | - | 9. | 3. | 26 | 9 | 3 | 26
9.3.27 | Monitors: HP ZR2440w 61 cm (24") LED Backlit IPS Monitor | Yes |  |  | 9. | 3. | 27 | 9 | 3 | 27
9.3.28 | Patching policy, hardening and cybersecurity requirements aligned with the IT security requirements | Yes |  |  | 9. | 3. | 28 | 9 | 3 | 28
9.3.29 | Secure storage of billing data, automated export to ZESCO corporate systems and provision of settlement data to ZESCO | Yes |  |  | 9. | 3. | 29 | 9 | 3 | 29
9.3.30 | Functions for data validation, estimation and editing (VEE) and audit trails consistent with revenue metering practice | Yes |  | - | 9. | 3. | 30 | 9 | 3 | 30
[8 empty] | 9 | 3 | 31 | tom rad
9.4. | Station Servers |  |  |  | 9. | 4. |  | 9 | 4 | 32 | R2
[8 empty] | 9 | 4 | 33 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 4 | 34 | R3
9.4.1 | Maker’s name | Bidder to state |  | - | 9. | 4. | 1 | 9 | 4 | 1
9.4.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 4. | 2 | 9 | 4 | 2
9.4.3 | Country of origin | Bidder to state |  | - | 9. | 4. | 3 | 9 | 4 | 3
9.4.4 | Description | SAS HMI Server/Client |  | - | 9. | 4. | 4 | 9 | 4 | 4
9.4.5 | Redundancy | 1+1 Hot standby |  | - | 9. | 4. | 5 | 9 | 4 | 5
9.4.6 | Communication Protocol | IEC 61850-8-2, IEC 61850-8-1 |  | - | 9. | 4. | 6 | 9 | 4 | 6
9.4.7 | HMI Interface with Substation LAN redundancy | Bidder to state |  | - | 9. | 4. | 7 | 9 | 4 | 7
9.4.8 | Computer Platform/Type | Industrial Computer |  | - | 9. | 4. | 8 | 9 | 4 | 8
9.4.9 | Processor | Intel Core i7 or Equivalent |  | - | 9. | 4. | 9 | 9 | 4 | 9
9.4.10 | HMI Display | 27-inch LED dual display |  | - | 9. | 4. | 10 | 9 | 4 | 10
9.4.11 | Storage | 2TB SSD RAID-1 Storage |  | - | 9. | 4. | 11 | 9 | 4 | 11
9.4.12 | HMI Memory (capacity and redundancy) | Server 32GB / Client 16GB |  | - | 9. | 4. | 12 | 9 | 4 | 12
9.4.13 | HMI Additional Hardware | Bidder to state |  | - | 9. | 4. | 13 | 9 | 4 | 13
9.4.14 | HMI Mounting | Bidder to state |  | - | 9. | 4. | 14 | 9 | 4 | 14
9.4.15 | Server Operating System | Windows Server (Version with proven stability and compatibility with SAS Software) |  | - | 9. | 4. | 15 | 9 | 4 | 15
9.4.16 | HMI Operating System | Windows Professional (version with proven stability) |  | - | 9. | 4. | 16 | 9 | 4 | 16
9.4.17 | Antivirus Software | Proven Compatibility with SAS Applications |  | - | 9. | 4. | 17 | 9 | 4 | 17
9.4.18 | Backup Software Utility | Bidder to state |  | - | 9. | 4. | 18 | 9 | 4 | 18
[8 empty] | 9 | 4 | 19 | tom rad
9.5. | Gateway |  |  |  | 9. | 5. |  | 9 | 5 | 20 | R2
[8 empty] | 9 | 5 | 21 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 5 | 22 | R3
9.5.1 | Maker’s name | Bidder to state |  | - | 9. | 5. | 1 | 9 | 5 | 1
9.5.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 5. | 2 | 9 | 5 | 2
9.5.3 | Country of origin | Bidder to state |  | - | 9. | 5. | 3 | 9 | 5 | 3
9.5.4 | Description | SAS Gateway |  | - | 9. | 5. | 4 | 9 | 5 | 4
9.5.5 | Redundancy | 1+1 Hot standby |  | - | 9. | 5. | 5 | 9 | 5 | 5
9.5.6 | Communication Protocol | IEC 61850-8-2, IEC 61850-8-1, IEC 60870-5-104, Modbus Serial, Modbus TCP, IEC-103. |  | - | 9. | 5. | 6 | 9 | 5 | 6
9.5.7 | Substation LAN redundancy | Bidder to state |  | - | 9. | 5. | 7 | 9 | 5 | 7
9.5.8 | Computer Platform/Type | Industrial Computer |  | - | 9. | 5. | 8 | 9 | 5 | 8
9.5.9 | Processor | Intel Core i7 or Equivalent |  | - | 9. | 5. | 9 | 9 | 5 | 9
9.5.10 | Storage | 2TB SSD RAID-1 Storage |  | - | 9. | 5. | 10 | 9 | 5 | 10
9.5.11 | Memory (capacity and redundancy) | 16GB |  | - | 9. | 5. | 11 | 9 | 5 | 11
9.5.12 | Additional Hardware | Bidder to state |  | - | 9. | 5. | 12 | 9 | 5 | 12
9.5.13 | Mounting | Bidder to state |  | - | 9. | 5. | 13 | 9 | 5 | 13
9.5.14 | Operating System | Windows Professional (version with proven stability) |  | - | 9. | 5. | 14 | 9 | 5 | 14
9.5.15 | Antivirus Software | Proven Compatibility with SAS Applications |  | - | 9. | 5. | 15 | 9 | 5 | 15
9.5.16 | Backup Software Utility | Bidder to state |  | - | 9. | 5. | 16 | 9 | 5 | 16
[8 empty] | 9 | 5 | 17 | tom rad
9.6. | Remote Terminal Unit |  |  |  | 9. | 6. |  | 9 | 6 | 18 | R2
[8 empty] | 9 | 6 | 19 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 6 | 20 | R3
9.6.1 | Maker’s name | Bidder to state |  | - | 9. | 6. | 1 | 9 | 6 | 1
9.6.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 6. | 2 | 9 | 6 | 2
9.6.3 | Country of origin | Bidder to state |  | - | 9. | 6. | 3 | 9 | 6 | 3
9.6.4 | Description | RTU |  | - | 9. | 6. | 4 | 9 | 6 | 4
9.6.5 | Analogue inputs | Bidder to state |  | Nos. | 9. | 6. | 5 | 9 | 6 | 5
9.6.6 | Digital inputs | Bidder to state |  | Nos. | 9. | 6. | 6 | 9 | 6 | 6
9.6.7 | Digital outputs | Bidder to state |  | Nos. | 9. | 6. | 7 | 9 | 6 | 7
9.6.8 | Fibre ports | Bidder to state |  | Nos. | 9. | 6. | 8 | 9 | 6 | 8
9.6.9 | Upstream communication ports | ≥4 Ethernet ports |  | Nos. | 9. | 6. | 9 | 9 | 6 | 9
9.6.10 | UCP communication protocol support | IEC60870-5-104 |  | - | 9. | 6. | 10 | 9 | 6 | 10
9.6.11 | Downstream communication ports | ≥2 |  | Nos. | 9. | 6. | 11 | 9 | 6 | 11
9.6.12 | DCP communication protocol supported | IEC61850-8-2,61850-8-1 Modbus IEC60870-5-103,60870-5-104 |  | - | 9. | 6. | 12 | 9 | 6 | 12
[8 empty] | 9 | 6 | 13 | tom rad
9.7. | Engineering Workstation |  |  |  | 9. | 7. |  | 9 | 7 | 14 | R2
[8 empty] | 9 | 7 | 15 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 7 | 16 | R3
9.7.1 | Maker’s name | Bidder to state |  | - | 9. | 7. | 1 | 9 | 7 | 1
9.7.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 7. | 2 | 9 | 7 | 2
9.7.3 | Country of origin | Bidder to state |  | - | 9. | 7. | 3 | 9 | 7 | 3
9.7.4 | Description | EWS |  | - | 9. | 7. | 4 | 9 | 7 | 4
9.7.5 | Standards | IEC618-8-2, 618-8-1 |  | - | 9. | 7. | 5 | 9 | 7 | 5
9.7.6 | EWS Interface with Substation LAN redundancy | Bidder to state |  | - | 9. | 7. | 6 | 9 | 7 | 6
9.7.7 | Computer Platform/Type | Industrial Computer |  | - | 9. | 7. | 7 | 9 | 7 | 7
9.7.8 | Processor | Intel Core i7 or Equivalent |  | - | 9. | 7. | 8 | 9 | 7 | 8
9.7.9 | EWS Display | 27-inch LED dual display |  | - | 9. | 7. | 9 | 9 | 7 | 9
9.7.10 | Storage | 2TB SSD RAID-1 Storage |  | - | 9. | 7. | 10 | 9 | 7 | 10
9.7.11 | EWS Memory (capacity and redundancy) | 32GB |  | - | 9. | 7. | 11 | 9 | 7 | 11
9.7.12 | EWS Additional Hardware | Bidder to state |  | - | 9. | 7. | 12 | 9 | 7 | 12
9.7.13 | EWS Mounting | Bidder to state |  | - | 9. | 7. | 13 | 9 | 7 | 13
9.7.14 | EWS Operating System | Windows Professional (version with proven stability) |  | - | 9. | 7. | 14 | 9 | 7 | 14
9.7.15 | Antivirus Software | Proven Compatibility with SAS Applications |  | - | 9. | 7. | 15 | 9 | 7 | 15
9.7.16 | Backup Software Utility | Bidder to state |  | - | 9. | 7. | 16 | 9 | 7 | 16
[8 empty] | 9 | 7 | 17 | tom rad
9.8. | Station LAN |  |  |  | 9. | 8. |  | 9 | 8 | 18 | R2
[8 empty] | 9 | 8 | 19 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 8 | 20 | R3
9.8.1 | Maker’s name | Bidder to state |  | - | 9. | 8. | 1 | 9 | 8 | 1
9.8.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 8. | 2 | 9 | 8 | 2
9.8.3 | Country of origin | Bidder to state |  | - | 9. | 8. | 3 | 9 | 8 | 3
9.8.4 | Description | Station Bus Local Area Network |  | - | 9. | 8. | 4 | 9 | 8 | 4
9.8.5 | Standards and protocols | IEC61850-8-2, 61850-8-1, GOOSE, MMS, IEEE802.1q, 802.1d, NTP, PTP |  | - | 9. | 8. | 5 | 9 | 8 | 5
9.8.6 | GPS Time Server Manufacturer | Bidder to state |  | - | 9. | 8. | 6 | 9 | 8 | 6
9.8.7 | GPS Time Server Model Number | Bidder to state |  | - | 9. | 8. | 7 | 9 | 8 | 7
9.8.8 | GPS Time Server Country of Origin | Bidder to state |  | - | 9. | 8. | 8 | 9 | 8 | 8
9.8.9 | GPS Time Server Protocol | Bidder to state |  | - | 9. | 8. | 9 | 9 | 8 | 9
9.8.10 | GPS Time Server Protocol Accuracy | Bidder to state |  | - | 9. | 8. | 10 | 9 | 8 | 10
9.8.11 | Ethernet Switches Manufacturer | Bidder to state |  | - | 9. | 8. | 11 | 9 | 8 | 11
9.8.12 | Ethernet Switches Model Number | Bidder to state |  | - | 9. | 8. | 12 | 9 | 8 | 12
9.8.13 | Ethernet Switches Country or origin | Bidder to state |  | - | 9. | 8. | 13 | 9 | 8 | 13
9.8.14 | Ethernet Switches Number | Bidder to state |  | Nos. | 9. | 8. | 14 | 9 | 8 | 14
9.8.15 | Ethernet Switch Layer | 3 |  | - | 9. | 8. | 15 | 9 | 8 | 15
[8 empty] | 9 | 8 | 16 | tom rad
9.9. | All Bay Control Units |  |  |  | 9. | 9. |  | 9 | 9 | 17 | R2
[8 empty] | 9 | 9 | 18 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 9 | 19 | R3
9.9.1 | Maker’s name | Bidder to state |  | - | 9. | 9. | 1 | 9 | 9 | 1
9.9.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 9. | 2 | 9 | 9 | 2
9.9.3 | Country of origin | Bidder to state |  | - | 9. | 9. | 3 | 9 | 9 | 3
9.9.4 | Description | BCU requirements |  | - | 9. | 9. | 4 | 9 | 9 | 4
9.9.5 | Functional properties | Multi functional micro processor controlled integrated control and monitoring unit |  | - | 9. | 9. | 5 | 9 | 9 | 5
9.9.6 | Graphical Man-Machine Interface | Yes |  | - | 9. | 9. | 6 | 9 | 9 | 6
9.9.7 | Fuse Fail Supervision | Yes |  | - | 9. | 9. | 7 | 9 | 9 | 7
9.9.8 | Main Trip Circuit Supervision (Dual State) | Yes |  | - | 9. | 9. | 8 | 9 | 9 | 8
9.9.9 | Backup Trip Circuit Supervision (Dual State) | Yes |  | - | 9. | 9. | 9 | 9 | 9 | 9
9.9.10 | Circuit Breaker Fail Protection | Yes |  | - | 9. | 9. | 10 | 9 | 9 | 10
9.9.11 | Voltage and Current Measuring Functions | Yes |  | - | 9. | 9. | 11 | 9 | 9 | 11
9.9.12 | 3 Phase Power Measuring Functions | Yes |  | - | 9. | 9. | 12 | 9 | 9 | 12
9.9.13 | Circuit Breaker Wear Monitor | Yes |  | - | 9. | 9. | 13 | 9 | 9 | 13
9.9.14 | Synchro Check function | Yes |  | - | 9. | 9. | 14 | 9 | 9 | 14
9.9.15 | Electrically operated devices’ control | Yes - SCADA & Local selection via relay pushbuttons / switch |  | - | 9. | 9. | 15 | 9 | 9 | 15
9.9.16 | Local / Remote Control Selection | Yes - SCADA & Local selection via relay pushbuttons / switch |  | - | 9. | 9. | 16 | 9 | 9 | 16
9.9.17 | Binary opto-input Channels | >96 |  | Nos. | 9. | 9. | 17 | 9 | 9 | 17
9.9.18 | Binary Output Channels | >24 |  | Nos. | 9. | 9. | 18 | 9 | 9 | 18
9.9.19 | Internal hardware and Software Supervision | Internal Alarm variable programmable to a fail-safe Output Contact |  | - | 9. | 9. | 19 | 9 | 9 | 19
9.9.20 | Internal Relay Fail watchdog potential free contact | Yes |  | - | 9. | 9. | 20 | 9 | 9 | 20
9.9.21 | Data Communication on dual Ethernet port to Substation LAN | IEC61850-8-2, IEC61850-8-1, IEC61850-9-2 (including send /receive GOOSE) and legacy protocols such as MODBUS, IEC-103, etc |  | - | 9. | 9. | 21 | 9 | 9 | 21
9.9.22 | Large format Local HMI Display with integrated control functionality | Yes |  | - | 9. | 9. | 22 | 9 | 9 | 22
9.9.23 | Front-mounted LEDs for alarm or status annunciation | Yes |  | - | 9. | 9. | 23 | 9 | 9 | 23
9.9.24 | Full Local and Remote Control and Interlocking | Yes |  | - | 9. | 9. | 24 | 9 | 9 | 24
9.9.25 | Local Data Communication port | Yes (front) |  | - | 9. | 9. | 25 | 9 | 9 | 25
9.9.26 | Attach Data Sheet, Technical Specifications and Type Test certificates | Yes |  | - | 9. | 9. | 26 | 9 | 9 | 26
9.9.27 | Mechanically Latched | Yes |  | - | 9. | 9. | 27 | 9 | 9 | 27
9.9.28 | Flagged Indication | Yes |  | - | 9. | 9. | 28 | 9 | 9 | 28
9.9.29 | Reset | Electrical and Manual |  | - | 9. | 9. | 29 | 9 | 9 | 29
9.9.30 | Maximum Operation time | 25 |  | ms | 9. | 9. | 30 | 9 | 9 | 30
9.9.31 | Attach Data Sheet, Technical Specifications and Type Test certificates | Yes |  | - | 9. | 9. | 31 | 9 | 9 | 31
[8 empty] | 9 | 9 | 32 | tom rad
9.10. | Bay Control Unit OHL and Reactor |  |  |  | 9. | 10. |  | 9 | 10 | 33 | R2
[8 empty] | 9 | 10 | 34 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 10 | 35 | R3
9.10.1 | Maker’s name | Bidder to state |  | - | 9. | 10. | 1 | 9 | 10 | 1
9.10.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 10. | 2 | 9 | 10 | 2
9.10.3 | Country of origin | Bidder to state |  | - | 9. | 10. | 3 | 9 | 10 | 3
9.10.4 | Description | BCU |  | - | 9. | 10. | 4 | 9 | 10 | 4
9.10.5 | Functional properties | Multi functional micro processor controlled integrated control and monitoring unit |  | - | 9. | 10. | 5 | 9 | 10 | 5
9.10.6 | Model | Schneider Micom C264 or equivalent, Bidder to state tendered |  | - | 9. | 10. | 6 | 9 | 10 | 6
9.10.7 | Graphical Man-Machine Interface | Yes |  | - | 9. | 10. | 7 | 9 | 10 | 7
9.10.8 | Fuse Fail Supervision | Yes |  | - | 9. | 10. | 8 | 9 | 10 | 8
9.10.9 | Main Trip Circuit Supervision (Dual State) | Yes |  | - | 9. | 10. | 9 | 9 | 10 | 9
9.10.10 | Backup Trip Circuit Supervision (Dual State) | Yes |  | - | 9. | 10. | 10 | 9 | 10 | 10
9.10.11 | Circuit Breaker Fail Protection | Yes |  | - | 9. | 10. | 11 | 9 | 10 | 11
9.10.12 | Voltage and Current Measuring Functions | Yes |  | - | 9. | 10. | 12 | 9 | 10 | 12
9.10.13 | 3 Phase Power Measuring Functions | Yes |  | - | 9. | 10. | 13 | 9 | 10 | 13
9.10.14 | Circuit Breaker Wear Monitor | Yes |  | - | 9. | 10. | 14 | 9 | 10 | 14
9.10.15 | Synchro Check function | Yes |  | - | 9. | 10. | 15 | 9 | 10 | 15
9.10.16 | Electrically operated devices’ control | Yes - SCADA & Local selection via relay pushbuttons / switch |  | - | 9. | 10. | 16 | 9 | 10 | 16
9.10.17 | Local / Remote Control Selection | Yes - SCADA & Local selection via relay pushbuttons / switch |  | - | 9. | 10. | 17 | 9 | 10 | 17
9.10.18 | Binary opto-input Channels | >96 |  | - | 9. | 10. | 18 | 9 | 10 | 18
9.10.19 | Binary Output Channels | >24 |  | - | 9. | 10. | 19 | 9 | 10 | 19
9.10.20 | Binary Input Voltage Range | 60-220 |  | - | 9. | 10. | 20 | 9 | 10 | 20
9.10.21 | Rated Auxiliary Supply Voltage | 60-220 |  | - | 9. | 10. | 21 | 9 | 10 | 21
9.10.22 | Rated Auxiliary Supply Voltage Operation Range | 80 - 120 |  | - | 9. | 10. | 22 | 9 | 10 | 22
9.10.23 | Internal hardware and Software Supervision | Internal Alarm variable programmable to a fail-safe Output Contact |  | - | 9. | 10. | 23 | 9 | 10 | 23
9.10.24 | Internal Relay Fail watchdog potential free contact | Yes |  | - | 9. | 10. | 24 | 9 | 10 | 24
9.10.25 | Data Communication on dual Ethernet port to Substation LAN – IEC61850 (including send /receive GOOSE) and legacy protocols such as MODBUS, IEC-103, DNP.3, etc | Yes |  | - | 9. | 10. | 25 | 9 | 10 | 25
9.10.26 | Time Synchronization capable (SNTP/PTP) | Yes |  | - | 9. | 10. | 26 | 9 | 10 | 26
9.10.27 | Large format Local HMI Display with integrated control functionality | Yes |  | - | 9. | 10. | 27 | 9 | 10 | 27
9.10.28 | Front-mounted LEDs for alarm or status annunciation | Yes |  | - | 9. | 10. | 28 | 9 | 10 | 28
9.10.29 | Full Local and Remote Control and Interlocking | Yes |  | - | 9. | 10. | 29 | 9 | 10 | 29
9.10.30 | Local Data Communication port | Yes (front) |  | - | 9. | 10. | 30 | 9 | 10 | 30
9.10.31 | Communication requirements | In line with IEC 61850 |  | - | 9. | 10. | 31 | 9 | 10 | 31
9.10.32 | Type test | Authority, year, Doc.no |  | - | 9. | 10. | 32 | 9 | 10 | 32
9.10.33 | Standards | IEC |  | - | 9. | 10. | 33 | 9 | 10 | 33
[8 empty] | 9 | 10 | 34 | tom rad
9.11. | Busbar protection 330 and 132 kV - Main I |  |  |  | 9. | 11. |  | 9 | 11 | 35 | R2
[8 empty] | 9 | 11 | 36 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 11 | 37 | R3
9.11.1 | Maker’s name | Bidder to state |  | - | 9. | 11. | 1 | 9 | 11 | 1
9.11.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 11. | 2 | 9 | 11 | 2
9.11.3 | Country of origin | Bidder to state |  | - | 9. | 11. | 3 | 9 | 11 | 3
9.11.4 | Description | Zone protection relay |  | - | 9. | 11. | 4 | 9 | 11 | 4
9.11.5 | Functional properties | Multi functional micro processor controlled protection relay |  | - | 9. | 11. | 5 | 9 | 11 | 5
9.11.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 11. | 6 | 9 | 11 | 6
9.11.7 | Type test | Authority, year, Doc.no |  | - | 9. | 11. | 7 | 9 | 11 | 7
9.11.8 | Standards | IEC 61850 |  | - | 9. | 11. | 8 | 9 | 11 | 8
9.11.9 | Protection Functions supported | Low impedance differential with integral check zone and ≥ 6 unique protection zones |  | - | 9. | 11. | 9 | 9 | 11 | 9
9.11.10 | Minimum number of bays supported | 18 |  | Nos. | 9. | 11. | 10 | 9 | 11 | 10
9.11.11 | Communication medium supported | Fibre Optic |  | - | 9. | 11. | 11 | 9 | 11 | 11
9.11.12 | Number of user-definable sitting groups available | Bidder to State |  | Nos. | 9. | 11. | 12 | 9 | 11 | 12
9.11.13 | Internal sequence of event recording with an accuracy of 1ms | Yes |  | - | 9. | 11. | 13 | 9 | 11 | 13
9.11.14 | Relay operating time for an in-zone fault | <20 |  | ms | 9. | 11. | 14 | 9 | 11 | 14
9.11.15 | Operating voltages of digital inputs | < 80% of V nominal |  | V | 9. | 11. | 15 | 9 | 11 | 15
9.11.16 | Electrical environmental tests required | IV (severe) |  | - | 9. | 11. | 16 | 9 | 11 | 16
9.11.17 | Included protection functions: |  |  |  | 9. | 11. | 17 | 9 | 11 | 17
9.11.18 | 1. Differential Protection, 87B | Yes |  | - | 9. | 11. | 18 | 9 | 11 | 18
9.11.19 | Additional Functions: |  |  |  | 9. | 11. | 19 | 9 | 11 | 19
9.11.20 | - Event recording | Yes |  | - | 9. | 11. | 20 | 9 | 11 | 20
9.11.21 | - Disturbance recorder | Yes |  | - | 9. | 11. | 21 | 9 | 11 | 21
[8 empty] | 9 | 11 | 22 | tom rad
9.12. | Line Protection 330 and 132 kV - Main I Diff. Protection |  |  |  | 9. | 12. |  | 9 | 12 | 23 | R2
[8 empty] | 9 | 12 | 24 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 12 | 25 | R3
9.12.1 | Maker’s name | Bidder to state |  | - | 9. | 12. | 1 | 9 | 12 | 1
9.12.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 12. | 2 | 9 | 12 | 2
9.12.3 | Country of origin | Bidder to state |  | - | 9. | 12. | 3 | 9 | 12 | 3
9.12.4 | Description | Current differencial protection |  | - | 9. | 12. | 4 | 9 | 12 | 4
9.12.5 | Functional properties | Multi functional micro processor controlled protection relay |  | - | 9. | 12. | 5 | 9 | 12 | 5
9.12.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 12. | 6 | 9 | 12 | 6
9.12.7 | Type test | Authority, year, Doc.no |  | - | 9. | 12. | 7 | 9 | 12 | 7
9.12.8 | Standards | IEC61850 |  | - | 9. | 12. | 8 | 9 | 12 | 8
9.12.9 | Applicable Setting, Engineering, Disturbance Recording Software | Yes |  | - | 9. | 12. | 9 | 9 | 12 | 9
9.12.10 | Number of minimum user-definable setting groups available | 2 |  | Nos. | 9. | 12. | 10 | 9 | 12 | 10
9.12.11 | Integral sequence of event recording with an accuracy of 1ms | Yes |  | - | 9. | 12. | 11 | 9 | 12 | 11
9.12.12 | Integral Fault Recorder | Yes |  | - | 9. | 12. | 12 | 9 | 12 | 12
9.12.13 | Integral Fault Locator | Yes |  | - | 9. | 12. | 13 | 9 | 12 | 13
9.12.14 | Phase segregated protection | Yes |  | - | 9. | 12. | 14 | 9 | 12 | 14
9.12.15 | Adjustable biased differential protection characteristic | Yes |  | - | 9. | 12. | 15 | 9 | 12 | 15
9.12.16 | Trip Mode | 1 or 3 pole (selectable) |  | - | 9. | 12. | 16 | 9 | 12 | 16
9.12.17 | Relay operating time for an in- zone fault | <30 |  | ms | 9. | 12. | 17 | 9 | 12 | 17
9.12.18 | Operating voltages of digital inputs | < 80% of V nominal |  | % | 9. | 12. | 18 | 9 | 12 | 18
9.12.19 | Electrical environmental tests required | IV (severe) |  | - | 9. | 12. | 19 | 9 | 12 | 19
9.12.20 | Differential current pickup values | 0.1 to 2.0 x In; steps of 0.05 x In Timer: 0 to 20s Steps of 0.01s |  | - | 9. | 12. | 20 | 9 | 12 | 20
9.12.21 | Differential pickup/trip times | < 30 ms |  | - | 9. | 12. | 21 | 9 | 12 | 21
9.12.22 | Line Charge Compensation | Yes |  | - | 9. | 12. | 22 | 9 | 12 | 22
9.12.23 | Full scheme distance - all phase to phase and all phase to earth loop impedances shall be simultaneously computed and compared with each zone limit. | Yes |  | - | 9. | 12. | 23 | 9 | 12 | 23
9.12.24 | 4 forward zones ph-ph & ph-E | Yes |  | - | 9. | 12. | 24 | 9 | 12 | 24
9.12.25 | 1 reverse zone ph-ph & ph-E | Yes |  | - | 9. | 12. | 25 | 9 | 12 | 25
9.12.26 | Phase fault & Earth fault characteristic shapes (Mho, Quad) | Yes |  | - | 9. | 12. | 26 | 9 | 12 | 26
9.12.27 | Nominal Z1 Operating time | Yes |  | - | 9. | 12. | 27 | 9 | 12 | 27
9.12.28 | Impedance setting range, reactive reach, positive sequence reactance | Yes |  | - | 9. | 12. | 28 | 9 | 12 | 28
9.12.29 | Impedance setting range, reactive reach, zero sequence reactance | Yes |  | - | 9. | 12. | 29 | 9 | 12 | 29
9.12.30 | Impedance setting range, resistive reach, positive sequence resistance | Yes |  | - | 9. | 12. | 30 | 9 | 12 | 30
9.12.31 | Impedance setting range, resistive reach, zero sequence resistance | Yes |  | - | 9. | 12. | 31 | 9 | 12 | 31
9.12.32 | Phase selection logic | Yes |  | - | 9. | 12. | 32 | 9 | 12 | 32
9.12.33 | SOFT | Yes |  | - | 9. | 12. | 33 | 9 | 12 | 33
9.12.34 | Power Swing Blocking | Yes |  | - | 9. | 12. | 34 | 9 | 12 | 34
9.12.35 | Mutual zero sequence compensation | Yes |  | - | 9. | 12. | 35 | 9 | 12 | 35
9.12.36 | Voltage Transformer Supervision | Yes |  | - | 9. | 12. | 36 | 9 | 12 | 36
9.12.37 | Time delays for all Zones | Yes |  | - | 9. | 12. | 37 | 9 | 12 | 37
9.12.38 | Auto reclose 1 or 3 pole (selectable) | Yes |  | - | 9. | 12. | 38 | 9 | 12 | 38
9.12.39 | Check Synchronism | Yes |  | - | 9. | 12. | 39 | 9 | 12 | 39
9.12.40 | Breaker Fail Protection | Yes |  | - | 9. | 12. | 40 | 9 | 12 | 40
9.12.41 | Undervoltage protection | Yes |  | - | 9. | 12. | 41 | 9 | 12 | 41
9.12.42 | Overvoltage protection | Yes |  | - | 9. | 12. | 42 | 9 | 12 | 42
9.12.43 | Trip Circuit supervision | Yes |  | - | 9. | 12. | 43 | 9 | 12 | 43
9.12.44 | Broken conductor detection | Yes |  | - | 9. | 12. | 44 | 9 | 12 | 44
[8 empty] | 9 | 12 | 45 | tom rad
9.13. | Line Protection 330 and 132 kV - Main II Distance Protection |  |  |  | 9. | 13. |  | 9 | 13 | 46 | R2
[8 empty] | 9 | 13 | 47 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 13 | 48 | R3
9.13.1 | Maker’s name | Bidder to state |  | - | 9. | 13. | 1 | 9 | 13 | 1
9.13.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 13. | 2 | 9 | 13 | 2
9.13.3 | Country of origin | Bidder to state |  | - | 9. | 13. | 3 | 9 | 13 | 3
9.13.4 | Description | Distance protection relay |  | - | 9. | 13. | 4 | 9 | 13 | 4
9.13.5 | Functional properties | Multi functional micro processor controlled protection relay |  | - | 9. | 13. | 5 | 9 | 13 | 5
9.13.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 13. | 6 | 9 | 13 | 6
9.13.7 | Type test | Authority, year, Doc.no |  | - | 9. | 13. | 7 | 9 | 13 | 7
9.13.8 | Standards | IEC |  | - | 9. | 13. | 8 | 9 | 13 | 8
9.13.9 | Applicable Setting, Engineering, Disturbance Recording Software | Yes |  | - | 9. | 13. | 9 | 9 | 13 | 9
9.13.10 | Number of user-definable sitting groups available | 2 |  | Nos. | 9. | 13. | 10 | 9 | 13 | 10
9.13.11 | Internal sequence of event recording with an accuracy of 1ms | Yes |  | - | 9. | 13. | 11 | 9 | 13 | 11
9.13.12 | Binary inputs | ≥24 |  | Nos. | 9. | 13. | 12 | 9 | 13 | 12
9.13.13 | Analogue inputs | ≥4 CT and ≥4 VT |  | Nos. | 9. | 13. | 13 | 9 | 13 | 13
9.13.14 | Binary outputs for tripping | ≥4 |  | Nos. | 9. | 13. | 14 | 9 | 13 | 14
9.13.15 | Binary outputs for signal | ≥16 |  | Nos. | 9. | 13. | 15 | 9 | 13 | 15
9.13.16 | Operating voltages of digital inputs | < 80% of V nominal |  | V | 9. | 13. | 16 | 9 | 13 | 16
9.13.17 | Electrical environmental tests required | IV (severe) |  | - | 9. | 13. | 17 | 9 | 13 | 17
9.13.18 | Relay operating time for an in- zone fault | <30 |  | ms | 9. | 13. | 18 | 9 | 13 | 18
9.13.19 | Full scheme distance - all phase to phase and all phase to earth loop impedances shall be simultaneously computed and compared with each zone limit. | Yes |  | - | 9. | 13. | 19 | 9 | 13 | 19
9.13.20 | 4 forward zones ph-ph & ph-E | Yes |  | - | 9. | 13. | 20 | 9 | 13 | 20
9.13.21 | 1 reverse zone ph-ph & ph-E | Yes |  | - | 9. | 13. | 21 | 9 | 13 | 21
9.13.22 | Time delay for all zones | Yes |  | - | 9. | 13. | 22 | 9 | 13 | 22
9.13.23 | Zone enable/disable for all zones | Yes |  | - | 9. | 13. | 23 | 9 | 13 | 23
9.13.24 | Phase fault & Earth fault characteristic shapes (Mho, Quad) | Quad |  | - | 9. | 13. | 24 | 9 | 13 | 24
9.13.25 | Nominal Z1 Operating time | <30 |  | ms | 9. | 13. | 25 | 9 | 13 | 25
9.13.26 | Impedance setting range, reactive reach, positive sequence reactance | Bidder to state |  | - | 9. | 13. | 26 | 9 | 13 | 26
9.13.27 | Impedance setting range, reactive reach, zero sequence reactance | Bidder to state |  | - | 9. | 13. | 27 | 9 | 13 | 27
9.13.28 | Impedance setting range, resistive reach, positive sequence resistance | Bidder to state |  | - | 9. | 13. | 28 | 9 | 13 | 28
9.13.29 | Impedance setting range, resistive reach, zero sequence resistance | Bidder to state |  | - | 9. | 13. | 29 | 9 | 13 | 29
9.13.30 | Maximum system impedance ratio at which accuracy is maintained | Bidder to state |  | - | 9. | 13. | 30 | 9 | 13 | 30
9.13.31 | Distance Tele-protection schemes | DTT, PUTT, POTT, Blocking (selectable) |  | - | 9. | 13. | 31 | 9 | 13 | 31
9.13.32 | Week-end infeed trip | Yes |  | - | 9. | 13. | 32 | 9 | 13 | 32
9.13.33 | Current reversal logic | Yes |  | - | 9. | 13. | 33 | 9 | 13 | 33
9.13.34 | Phase selection logic | Yes |  | - | 9. | 13. | 34 | 9 | 13 | 34
9.13.35 | SOFT | Yes |  | - | 9. | 13. | 35 | 9 | 13 | 35
9.13.36 | Power Swing Blocking | Yes |  | - | 9. | 13. | 36 | 9 | 13 | 36
9.13.37 | Mutual zero sequence compensation | Yes |  | - | 9. | 13. | 37 | 9 | 13 | 37
9.13.38 | Voltage Transformer Supervision | Yes |  | - | 9. | 13. | 38 | 9 | 13 | 38
9.13.39 | CT Supervision | Yes |  | - | 9. | 13. | 39 | 9 | 13 | 39
9.13.40 | Directional Earth Fault (DEF) | Yes |  | - | 9. | 13. | 40 | 9 | 13 | 40
9.13.41 | DEF tele-protection scheme | None/ Permissive/ |  | - | 9. | 13. | 41 | 9 | 13 | 41
9.13.42 | Auto reclose | Blocking (selectable) 1 or 3 pole (selectable) |  | - | 9. | 13. | 42 | 9 | 13 | 42
9.13.43 | Check Synchronism | Yes |  | - | 9. | 13. | 43 | 9 | 13 | 43
9.13.44 | Breaker Fail Protection | Yes |  | - | 9. | 13. | 44 | 9 | 13 | 44
9.13.45 | Undervoltage protection | Yes |  | - | 9. | 13. | 45 | 9 | 13 | 45
9.13.46 | Trip Circuit supervision | Yes |  | - | 9. | 13. | 46 | 9 | 13 | 46
9.13.47 | Disturbance recorder | Yes |  | - | 9. | 13. | 47 | 9 | 13 | 47
[8 empty] | 9 | 13 | 48 | tom rad
9.14. | Line Protection 330 and 132 kV - Back-up |  |  |  | 9. | 14. |  | 9 | 14 | 49 | R2
[8 empty] | 9 | 14 | 50 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 14 | 51 | R3
9.14.1 | Maker’s name | Bidder to state |  | - | 9. | 14. | 1 | 9 | 14 | 1
9.14.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 14. | 2 | 9 | 14 | 2
9.14.3 | Country of origin | Bidder to state |  | - | 9. | 14. | 3 | 9 | 14 | 3
9.14.4 | Description | Feeder management relay |  | - | 9. | 14. | 4 | 9 | 14 | 4
9.14.5 | Functional properties | Multi functional micro processor controlled protection relay |  | - | 9. | 14. | 5 | 9 | 14 | 5
9.14.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 14. | 6 | 9 | 14 | 6
9.14.7 | Type test | Authority, year, Doc.no |  | - | 9. | 14. | 7 | 9 | 14 | 7
9.14.8 | Standards | IEC |  | - | 9. | 14. | 8 | 9 | 14 | 8
9.14.9 | Applicable Setting, Engineering, Disturbance Recording Software | Yes |  | - | 9. | 14. | 9 | 9 | 14 | 9
9.14.10 | Number of user-definable sitting groups available | 2 |  | Nos. | 9. | 14. | 10 | 9 | 14 | 10
9.14.11 | Internal sequence of event recording with an accuracy of 1ms | Yes |  | - | 9. | 14. | 11 | 9 | 14 | 11
9.14.12 | Binary inputs | ≥8 |  | Nos. | 9. | 14. | 12 | 9 | 14 | 12
9.14.13 | Analogue inputs | ≥5 CT and ≥3 VT |  | Nos. | 9. | 14. | 13 | 9 | 14 | 13
9.14.14 | Binary outputs for tripping | ≥7 |  | Nos. | 9. | 14. | 14 | 9 | 14 | 14
9.14.15 | Binary outputs for signal | ≥4 |  | Nos. | 9. | 14. | 15 | 9 | 14 | 15
9.14.16 | Operating voltages of digital inputs | < 80% of V nominal |  | V | 9. | 14. | 16 | 9 | 14 | 16
9.14.17 | Electrical environmental tests required | IV (severe) |  | - | 9. | 14. | 17 | 9 | 14 | 17
9.14.18 | Definite Time and IDMT Overcurrent | 0.08 to 4 x In; steps of 0.01 x In Timer: 0 to 100s steps of 0.01 s TMS 0.025 to 1.200 |  | - | 9. | 14. | 18 | 9 | 14 | 18
9.14.19 | Highset Overcurrent | 0.08 to 32 x In; steps of 0.01 x In Timer: 0.00 to 100s steps of 0.01 s |  | - | 9. | 14. | 19 | 9 | 14 | 19
9.14.20 | Definite Time and IDMT Earth Fault | 0.08 to 4 x In; steps of 0.01 x In Timer: 0 to 200s steps of 0.01 s TMS 0.025 to 1.200 |  | - | 9. | 14. | 20 | 9 | 14 | 20
9.14.21 | Highset Earth Fault | 0.08 to 32 x In; steps of 0.01 x In Timer: 0.00 to 200s steps of 0.01 s |  | - | 9. | 14. | 21 | 9 | 14 | 21
9.14.22 | 67/67N MTA: | -95° to +95° |  | - | 9. | 14. | 22 | 9 | 14 | 22
9.14.23 | Minimum operating range | 7 VP-P or VP-N |  | - | 9. | 14. | 23 | 9 | 14 | 23
9.14.24 | Breaker Fail | Yes |  | - | 9. | 14. | 24 | 9 | 14 | 24
9.14.25 | Over Voltage | Yes |  | - | 9. | 14. | 25 | 9 | 14 | 25
9.14.26 | Under Voltage | Yes |  | - | 9. | 14. | 26 | 9 | 14 | 26
9.14.27 | Under/Over Frequency | Yes |  | - | 9. | 14. | 27 | 9 | 14 | 27
9.14.28 | Direct Transfer Trip | Yes |  | - | 9. | 14. | 28 | 9 | 14 | 28
9.14.29 | CT Supervision | Yes |  | - | 9. | 14. | 29 | 9 | 14 | 29
9.14.30 | VT Supervision | Yes |  | - | 9. | 14. | 30 | 9 | 14 | 30
9.14.31 | SOTF | Yes |  | - | 9. | 14. | 31 | 9 | 14 | 31
9.14.32 | Additional Functions: |  |  |  | 9. | 14. | 32 | 9 | 14 | 32
9.14.33 | - Event recording | Yes |  | - | 9. | 14. | 33 | 9 | 14 | 33
9.14.34 | - Disturbance recorder | Yes |  | - | 9. | 14. | 34 | 9 | 14 | 34
[8 empty] | 9 | 14 | 35 | tom rad
9.15. | Transformer Automatic Voltage Control |  |  |  | 9. | 15. |  | 9 | 15 | 36 | R2
[8 empty] | 9 | 15 | 37 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 15 | 38 | R3
9.15.1 | Maker’s name | Bidder to state |  | - | 9. | 15. | 1 | 9 | 15 | 1
9.15.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 15. | 2 | 9 | 15 | 2
9.15.3 | Country of origin | Bidder to state |  | - | 9. | 15. | 3 | 9 | 15 | 3
9.15.4 | Description | TC control |  | - | 9. | 15. | 4 | 9 | 15 | 4
9.15.5 | Functional properties | Multi functional micro processor controlled relay |  | - | 9. | 15. | 5 | 9 | 15 | 5
9.15.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 15. | 6 | 9 | 15 | 6
9.15.7 | Type test | Authority, year, Doc.no |  | - | 9. | 15. | 7 | 9 | 15 | 7
9.15.8 | Standards | IEC |  | - | 9. | 15. | 8 | 9 | 15 | 8
9.15.9 | Paralleling control | Master Follower & Limiting of Circulating Current (selectable) |  | - | 9. | 15. | 9 | 9 | 15 | 9
9.15.10 | Local / Remote control selection | Yes - Local selection via relay pushbuttons / Switch |  | - | 9. | 15. | 10 | 9 | 15 | 10
9.15.11 | Manual / Auto control selection | Yes - SCADA & Local selection via relay pushbuttons |  | - | 9. | 15. | 11 | 9 | 15 | 11
9.15.12 | Manual Raise / Lower control | Yes - SCADA & Local selection via relay pushbuttons |  | - | 9. | 15. | 12 | 9 | 15 | 12
9.15.13 | Definite and Inverse time Voltage control characteristic | Yes |  | - | 9. | 15. | 13 | 9 | 15 | 13
9.15.14 | External Blocking Input | Yes |  | - | 9. | 15. | 14 | 9 | 15 | 14
9.15.15 | “Tap Position”-Interface to Transformer | BCD |  | - | 9. | 15. | 15 | 9 | 15 | 15
9.15.16 | Data Communication port to Substation LAN – IEC61850 (including send/receive GOOSE) | Yes |  | - | 9. | 15. | 16 | 9 | 15 | 16
9.15.17 | Local Data Communication Port | Yes |  | - | 9. | 15. | 17 | 9 | 15 | 17
[8 empty] | 9 | 15 | 18 | tom rad
9.16. | Transformer, Reactor Protection 330 and 132 kV - Main I |  |  |  | 9. | 16. |  | 9 | 16 | 19 | R2
[8 empty] | 9 | 16 | 20 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 16 | 21 | R3
9.16.1 | Maker’s name | To be stated by Bidder |  | - | 9. | 16. | 1 | 9 | 16 | 1
9.16.2 | Maker’s type and reference | To be stated by Bidder |  | - | 9. | 16. | 2 | 9 | 16 | 2
9.16.3 | Country of origin | To be stated by Bidder |  | - | 9. | 16. | 3 | 9 | 16 | 3
9.16.4 | Description | Biased Differential Protection Relay |  | - | 9. | 16. | 4 | 9 | 16 | 4
9.16.5 | Functional properties | Multi functional micro processor controlled protection relay |  | - | 9. | 16. | 5 | 9 | 16 | 5
9.16.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 16. | 6 | 9 | 16 | 6
9.16.7 | Type test | Authority, year, Doc.no |  | - | 9. | 16. | 7 | 9 | 16 | 7
9.16.8 | Standards | IEC |  | - | 9. | 16. | 8 | 9 | 16 | 8
9.16.9 | Applicable Setting, Engineering, Disturbance Recording Software | Yes |  | - | 9. | 16. | 9 | 9 | 16 | 9
9.16.10 | Number of minimum user-definable setting groups available | 2 |  | Nos. | 9. | 16. | 10 | 9 | 16 | 10
9.16.11 | Integral sequence of event recording with an accuracy of 1ms | Yes |  | - | 9. | 16. | 11 | 9 | 16 | 11
9.16.12 | Integral Fault Recorder | Yes |  | - | 9. | 16. | 12 | 9 | 16 | 12
9.16.13 | g) Relay operating time for an in- zone fault | <30 |  | ms | 9. | 16. | 13 | 9 | 16 | 13
9.16.14 | Binary inputs | ≥12 |  | Nos. | 9. | 16. | 14 | 9 | 16 | 14
9.16.15 | Analogue inputs CT / VT | ≥8 / 2 |  | Nos. | 9. | 16. | 15 | 9 | 16 | 15
9.16.16 | Binary outputs for tripping | ≥4 |  | Nos. | 9. | 16. | 16 | 9 | 16 | 16
9.16.17 | Binary outputs for signal | ≥8 |  | Nos. | 9. | 16. | 17 | 9 | 16 | 17
9.16.18 | Operating voltages of digital inputs | < 80% of V nominal |  | % | 9. | 16. | 18 | 9 | 16 | 18
9.16.19 | Electrical environmental tests required | IV (severe) |  | - | 9. | 16. | 19 | 9 | 16 | 19
9.16.20 | Differential current pickup values | 0.1 to 1.5 x In; steps of 0.05 x In Timer: 0 to 20s steps of 0.01s |  | - | 9. | 16. | 20 | 9 | 16 | 20
9.16.21 | Differential pickup/trip times | < 30 |  | ms | 9. | 16. | 21 | 9 | 16 | 21
9.16.22 | High Set Differential pickup / trip times | < 20 |  | ms | 9. | 16. | 22 | 9 | 16 | 22
9.16.23 | Differential Current IREF Values | 0.1 to 1.5 x In; steps of 0.05 x In Timer: 0 to 20s steps of 0.01s |  | - | 9. | 16. | 23 | 9 | 16 | 23
9.16.24 | IREF Differential pickup / trip times @ 2.5 x Setting | < 30 |  | ms | 9. | 16. | 24 | 9 | 16 | 24
9.16.25 | Definite Time Overcurrent | 1 to 20 x In; steps of 1 x In Timer: 0 to 20s steps of 0.01 s |  | - | 9. | 16. | 25 | 9 | 16 | 25
9.16.26 | IDMT Overcurrent | 0,5 to 5 x In; steps of 0.05 x In Time multiplier: 0.05 to 3s steps of 0.01s |  | - | 9. | 16. | 26 | 9 | 16 | 26
9.16.27 | Overexcitation protection (v/Hz) | Yes |  | - | 9. | 16. | 27 | 9 | 16 | 27
[8 empty] | 9 | 16 | 28 | tom rad
9.17. | Transformer, Reactor Protection 330 and 132 kV - Main II |  |  |  | 9. | 17. |  | 9 | 17 | 29 | R2
[8 empty] | 9 | 17 | 30 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 17 | 31 | R3
9.17.1 | Maker’s name | To be stated by Bidder |  | - | 9. | 17. | 1 | 9 | 17 | 1
9.17.2 | Maker’s type and reference | To be stated by Bidder |  | - | 9. | 17. | 2 | 9 | 17 | 2
9.17.3 | Country of origin | To be stated by Bidder |  | - | 9. | 17. | 3 | 9 | 17 | 3
9.17.4 | Description | Biased Differential Protection Relay |  | - | 9. | 17. | 4 | 9 | 17 | 4
9.17.5 | Functional properties | Multi functional micro processor controlled protection relay |  | - | 9. | 17. | 5 | 9 | 17 | 5
9.17.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 17. | 6 | 9 | 17 | 6
9.17.7 | Type test | Authority, year, Doc.no |  | - | 9. | 17. | 7 | 9 | 17 | 7
9.17.8 | Standards | IEC |  | - | 9. | 17. | 8 | 9 | 17 | 8
9.17.9 | Applicable Setting, Engineering, Disturbance Recording Software | Yes |  | - | 9. | 17. | 9 | 9 | 17 | 9
9.17.10 | Number of minimum user-definable setting groups available | 2 |  | Nos. | 9. | 17. | 10 | 9 | 17 | 10
9.17.11 | Integral sequence of event recording with an accuracy of 1ms | Yes |  | - | 9. | 17. | 11 | 9 | 17 | 11
9.17.12 | Integral Fault Recorder | Yes |  | - | 9. | 17. | 12 | 9 | 17 | 12
9.17.13 | Binary inputs | ≥12 |  | Nos. | 9. | 17. | 13 | 9 | 17 | 13
9.17.14 | Analogue inputs CT / VT | ≥8 / 2 |  | Nos. | 9. | 17. | 14 | 9 | 17 | 14
9.17.15 | Binary outputs for tripping | ≥4 |  | Nos. | 9. | 17. | 15 | 9 | 17 | 15
9.17.16 | Binary outputs for signal | ≥8 |  | Nos. | 9. | 17. | 16 | 9 | 17 | 16
9.17.17 | Operating voltages of digital inputs | < 80% of V nominal |  | % | 9. | 17. | 17 | 9 | 17 | 17
9.17.18 | Differential current pickup values | 0.1 to 1.5 x In; steps of 0.05 x In Timer: 0 to 20s steps of 0.01s |  | - | 9. | 17. | 18 | 9 | 17 | 18
9.17.19 | Differential pickup/trip times | < 30 |  | ms | 9. | 17. | 19 | 9 | 17 | 19
9.17.20 | High Set Differential pickup / trip times | < 20 |  | ms | 9. | 17. | 20 | 9 | 17 | 20
9.17.21 | Differential Current IREF Values | 0.1 to 1.5 x In; steps of 0.05 x In Timer: 0 to 20s steps of 0.01s |  | - | 9. | 17. | 21 | 9 | 17 | 21
9.17.22 | IREF Differential pickup / trip times @ 2.5 x Setting | < 30 |  | ms | 9. | 17. | 22 | 9 | 17 | 22
9.17.23 | Definite Time Overcurrent | 1 to 20 x In; steps of 1 x In Timer: 0 to 20s steps of 0.01 s |  | - | 9. | 17. | 23 | 9 | 17 | 23
9.17.24 | IDMT Overcurrent | 0,5 to 5 x In; steps of 0.05 x In Time multiplier: 0.05 to 3s steps of 0.01s |  | - | 9. | 17. | 24 | 9 | 17 | 24
9.17.25 | Overexcitation protection (v/Hz) | Yes |  | - | 9. | 17. | 25 | 9 | 17 | 25
[8 empty] | 9 | 17 | 26 | tom rad
9.18. | Transformer, Reactor and Neutral Reactor Protection 330 and 132 kV - Back-up |  |  |  | 9. | 18. |  | 9 | 18 | 27 | R2
[8 empty] | 9 | 18 | 28 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 18 | 29 | R3
9.18.1 | Maker’s name | To be stated by Bidder |  | - | 9. | 18. | 1 | 9 | 18 | 1
9.18.2 | Maker’s type and reference | To be stated by Bidder |  | - | 9. | 18. | 2 | 9 | 18 | 2
9.18.3 | Country of origin | To be stated by Bidder |  | - | 9. | 18. | 3 | 9 | 18 | 3
9.18.4 | Description | OC/EF relay |  | - | 9. | 18. | 4 | 9 | 18 | 4
9.18.5 | Functional properties | Multi functional micro processor controlled protection relay |  | - | 9. | 18. | 5 | 9 | 18 | 5
9.18.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 18. | 6 | 9 | 18 | 6
9.18.7 | Type test | Authority, year, Doc.no |  | - | 9. | 18. | 7 | 9 | 18 | 7
9.18.8 | Standards | IEC |  | - | 9. | 18. | 8 | 9 | 18 | 8
9.18.9 | Applicable Setting, Engineering, Disturbance Recording Software | Yes |  | - | 9. | 18. | 9 | 9 | 18 | 9
9.18.10 | Number of minimum user-definable setting groups available | 2 |  | Nos. | 9. | 18. | 10 | 9 | 18 | 10
9.18.11 | Integral sequence of event recording with an accuracy of 1ms | Yes |  | - | 9. | 18. | 11 | 9 | 18 | 11
9.18.12 | Integral Fault Recorder | Yes |  | - | 9. | 18. | 12 | 9 | 18 | 12
9.18.13 | Binary inputs | ≥8 |  | Nos. | 9. | 18. | 13 | 9 | 18 | 13
9.18.14 | Analogue inputs CT / VT | ≥5 / 3 |  | Nos. | 9. | 18. | 14 | 9 | 18 | 14
9.18.15 | Binary outputs for tripping | ≥4 |  | Nos. | 9. | 18. | 15 | 9 | 18 | 15
9.18.16 | Binary outputs for signal | ≥7 |  | Nos. | 9. | 18. | 16 | 9 | 18 | 16
9.18.17 | Operating voltages of digital inputs | < 80% of V nominal |  | % | 9. | 18. | 17 | 9 | 18 | 17
9.18.18 | Definite Time Overcurrent | 1 to 20 x In; steps of 1 x In Timer: 0 to 20s steps of 0.01 s |  | - | 9. | 18. | 18 | 9 | 18 | 18
9.18.19 | IDMT Overcurrent | 0,5 to 5 x In; steps of 0.05 x In Time multiplier: 0.05 to 3s steps of 0.01s |  | - | 9. | 18. | 19 | 9 | 18 | 19
[8 empty] | 9 | 18 | 20 | tom rad
9.19. | Transformer Protection 11/0.4 kV |  |  |  | 9. | 19. |  | 9 | 19 | 21 | R2
[8 empty] | 9 | 19 | 22 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 19 | 23 | R3
9.19.1 | Maker’s name | Bidder to state |  | - | 9. | 19. | 1 | 9 | 19 | 1
9.19.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 19. | 2 | 9 | 19 | 2
9.19.3 | Country of origin | Bidder to state |  | - | 9. | 19. | 3 | 9 | 19 | 3
9.19.4 | Description | OC/EF protection |  | - | 9. | 19. | 4 | 9 | 19 | 4
9.19.5 | Functional properties | Multi functional micro processor controlled protection relay |  | - | 9. | 19. | 5 | 9 | 19 | 5
9.19.6 | Communication requirements | In line with IEC 61850 |  | - | 9. | 19. | 6 | 9 | 19 | 6
9.19.7 | Type test | Authority, year, Doc.no |  | - | 9. | 19. | 7 | 9 | 19 | 7
9.19.8 | Standards | IEC |  | - | 9. | 19. | 8 | 9 | 19 | 8
9.19.9 | Overcurrent Protection, 50/51 | Yes |  | - | 9. | 19. | 9 | 9 | 19 | 9
9.19.10 | Earth Fault Protection, 50N/51N | Yes |  | - | 9. | 19. | 10 | 9 | 19 | 10
9.19.11 | Circuit Breaker Failure Protection, 50BF | Yes |  | - | 9. | 19. | 11 | 9 | 19 | 11
[8 empty] | 9 | 19 | 12 | tom rad
9.20. | Digital Meetering |  |  |  | 9. | 20. |  | 9 | 20 | 13 | R2
[8 empty] | 9 | 20 | 14 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 20 | 15 | R3
9.20.1 | Maker’s name | Bidder to state |  | - | 9. | 20. | 1 | 9 | 20 | 1
9.20.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 20. | 2 | 9 | 20 | 2
9.20.3 | Country of origin | Bidder to state |  | - | 9. | 20. | 3 | 9 | 20 | 3
9.20.4 | Description | Digital energy meter |  | - | 9. | 20. | 4 | 9 | 20 | 4
9.20.5 | Type test | Authority, year, Doc.no |  | - | 9. | 20. | 5 | 9 | 20 | 5
9.20.6 | Nominal system voltage | 110 |  | V | 9. | 20. | 6 | 9 | 20 | 6
9.20.7 | Capabilities | Time of use metering, Import and Export measuring, shall record the active energy (MWh), apparent energy (MVAh), reactive energy (MVArh) and the Maximum Demands (MVA, MW, MVAr) with date & time of occurrence for both import and export directions. The Maximum Demand shall be user programmable to MVA, MW or MVAr. ALL READINGS TO BE PRIMARY VALUES. Instrument Transformer CT and VT ratios shall be programmable on the meter.Programmable scaling of readings to Mega or Kilo and number of decimals. |  | - | 9. | 20. | 7 | 9 | 20 | 7
9.20.8 | Measuring voltage range | 80-120 |  | %Un | 9. | 20. | 8 | 9 | 20 | 8
9.20.9 | Tolerance | ±20 |  | % | 9. | 20. | 9 | 9 | 20 | 9
9.20.10 | Auxiliary supply voltage | Dual application, 40 – 250 AC/DC. DC auxiliary supply voltage use is first priority. |  | V | 9. | 20. | 10 | 9 | 20 | 10
9.20.11 | Current rating | 1/5 programable to any CT ratio |  | A | 9. | 20. | 11 | 9 | 20 | 11
9.20.12 | Starting current (0.002 In) | 2/10 |  | mA | 9. | 20. | 12 | 9 | 20 | 12
9.20.13 | Maximum power consumption | 15/3 |  | VA/W | 9. | 20. | 13 | 9 | 20 | 13
9.20.14 | Demand load profiling and Integration Period | Load profiling of active power, reactive power and apparent power demand. Average demand shall be selectable to be either by block demand or rolling demand. The integration period shall be user programmable (1 to 60 minutes), default 30 minutes. Window for rolling demand shall also be programmable. |  | - | 9. | 20. | 14 | 9 | 20 | 14
9.20.15 | System | 3 phase 3 wire, 3 Phase, 4 wire. The meter shall be programmable between the two systems. |  | - | 9. | 20. | 15 | 9 | 20 | 15
9.20.16 | Accuracy class line bay and reactor bay | 0.2 |  | - | 9. | 20. | 16 | 9 | 20 | 16
9.20.17 | Accuracy class transformer bay and gen-set | 0.25 |  | - | 9. | 20. | 17 | 9 | 20 | 17
9.20.18 | Short circuit rating | 20 In |  | A | 9. | 20. | 18 | 9 | 20 | 18
9.20.19 | Impulse withstand voltage | 3 |  | kV | 9. | 20. | 19 | 9 | 20 | 19
9.20.20 | Installation | At least two seals |  | - | 9. | 20. | 20 | 9 | 20 | 20
9.20.21 | Meter Display Information and measurements | 8 digit display |  | - | 9. | 20. | 21 | 9 | 20 | 21
9.20.22 | Communication Interface: Optical interface, Ethernet, Protocol: IEC 62056 | bi-directional and protocol to be of type Flag as per IEC 62056-21 for site communication, Functional Ethernet port for remote communication and remote reading. |  | - | 9. | 20. | 22 | 9 | 20 | 22
9.20.23 | Over-current protection with a short circuit current | 20 Imax |  | A | 9. | 20. | 23 | 9 | 20 | 23
9.20.24 | Meter shall have provision for the user to view a pre-configured cycle | Yes |  | - | 9. | 20. | 24 | 9 | 20 | 24
9.20.25 | Lightning protection according to | BS 1524 and IEC62053-21 |  | - | 9. | 20. | 25 | 9 | 20 | 25
9.20.26 | Anti-Tempering Features | Tamper protection Anti-tamper switch Tamper logging/indications AMR functionalities |  | - | 9. | 20. | 26 | 9 | 20 | 26
9.20.27 | Applicable electronic Meter software | Windows based software for programming and downloading. The meter should be fully user programmable and downloadable. Copies of CDs for the meter software with labelling showing software name, version, etc. |  | - | 9. | 20. | 27 | 9 | 20 | 27
9.20.28 | Time of Use Registers | 8 |  | Nos. | 9. | 20. | 28 | 9 | 20 | 28
9.20.29 | Maximum Demand Registers | 8 |  | Nos. | 9. | 20. | 29 | 9 | 20 | 29
9.20.30 | Volt Free Output Relays (Internal & normally open) | 4 |  | Nos. | 9. | 20. | 30 | 9 | 20 | 30
9.20.31 | Casing | House Service Pattern Case, extended Terminal Cover |  | - | 9. | 20. | 31 | 9 | 20 | 31
9.20.32 | Historical Data | Average demand Load Profiling (MW, MVAr, MVA) (450 days, 1 Channel, 30 minutes), at least twelve months historical active energy (MWh), reactive energy (MVArh), apparent energy (MVAh) and maximum demand billing data logging in meter memory. The average demand load profiling should be programmable between block demand and sliding demand. At least twelve months of sets of historical data |  | - | 9. | 20. | 32 | 9 | 20 | 32
9.20.33 | Quality Assurance Certificate | To be provided with the bid |  | - | 9. | 20. | 33 | 9 | 20 | 33
9.20.34 | Routine test results | To be provided on delivery of meters for each meter |  | - | 9. | 20. | 34 | 9 | 20 | 34
9.20.35 | Previous Type test results | To be provided with the bid |  | - | 9. | 20. | 35 | 9 | 20 | 35
9.20.36 | Drawings showing dimensions of meters | To be provided with the bid |  | - | 9. | 20. | 36 | 9 | 20 | 36
9.20.37 | Applicable standards | IEC 62052-11, 62053-21, 62053-22:, 62053-23, 62053-61; 62056 |  | - | 9. | 20. | 37 | 9 | 20 | 37
9.20.38 | Operators manual Hard copy | To be provided with meters, 5 copies |  | - | 9. | 20. | 38 | 9 | 20 | 38
9.20.39 | Technical manual Hard copy | To be provided with meters, 5 copies |  | - | 9. | 20. | 39 | 9 | 20 | 39
[8 empty] | 9 | 20 | 40 | tom rad
9.21. | Meters, indicating Instrument |  |  |  | 9. | 21. |  | 9 | 21 | 41 | R2
| To be filled in for each instrument type used | [6 empty] | 9 | 21 | 42 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 21 | 43 | R3
9.21.1 | Kind of meter | Bidder to state |  | - | 9. | 21. | 1 | 9 | 21 | 1
9.21.2 | Range | Bidder to state |  | - | 9. | 21. | 2 | 9 | 21 | 2
9.21.3 | Maker’s name | Bidder to state |  | - | 9. | 21. | 3 | 9 | 21 | 3
9.21.4 | Maker’s type and reference | Bidder to state |  | - | 9. | 21. | 4 | 9 | 21 | 4
9.21.5 | Country of origin | Bidder to state |  | - | 9. | 21. | 5 | 9 | 21 | 5
9.21.6 | Description | Bidder to state |  | - | 9. | 21. | 6 | 9 | 21 | 6
9.21.7 | Type test | Authority, year, Doc.no |  | - | 9. | 21. | 7 | 9 | 21 | 7
9.21.8 | Standards | IEC |  | - | 9. | 21. | 8 | 9 | 21 | 8
9.21.9 | Kind of meter | Bidder to state |  | - | 9. | 21. | 9 | 9 | 21 | 9
9.21.10 | Range | Bidder to state |  | - | 9. | 21. | 10 | 9 | 21 | 10
9.21.11 | Maker’s name | Bidder to state |  | - | 9. | 21. | 11 | 9 | 21 | 11
9.21.12 | Maker’s type and reference | Bidder to state |  | - | 9. | 21. | 12 | 9 | 21 | 12
9.21.13 | Country of origin | Bidder to state |  | - | 9. | 21. | 13 | 9 | 21 | 13
9.21.14 | Description | Bidder to state |  | - | 9. | 21. | 14 | 9 | 21 | 14
9.21.15 | Type test | Authority, year, Doc.no |  | - | 9. | 21. | 15 | 9 | 21 | 15
9.21.16 | Standards | IEC |  | - | 9. | 21. | 16 | 9 | 21 | 16
9.21.17 | Kind of meter | Bidder to state |  | - | 9. | 21. | 17 | 9 | 21 | 17
9.21.18 | Range | Bidder to state |  | - | 9. | 21. | 18 | 9 | 21 | 18
9.21.19 | Maker’s name | Bidder to state |  | - | 9. | 21. | 19 | 9 | 21 | 19
9.21.20 | Maker’s type and reference | Bidder to state |  | - | 9. | 21. | 20 | 9 | 21 | 20
9.21.21 | Country of origin | Bidder to state |  | - | 9. | 21. | 21 | 9 | 21 | 21
9.21.22 | Description | Bidder to state |  | - | 9. | 21. | 22 | 9 | 21 | 22
9.21.23 | Type test | Authority, year, Doc.no |  | - | 9. | 21. | 23 | 9 | 21 | 23
9.21.24 | Standards | IEC |  | - | 9. | 21. | 24 | 9 | 21 | 24
9.21.25 | Kind of meter | Bidder to state |  | - | 9. | 21. | 25 | 9 | 21 | 25
9.21.26 | Range | Bidder to state |  | - | 9. | 21. | 26 | 9 | 21 | 26
9.21.27 | Maker’s name | Bidder to state |  | - | 9. | 21. | 27 | 9 | 21 | 27
9.21.28 | Maker’s type and reference | Bidder to state |  | - | 9. | 21. | 28 | 9 | 21 | 28
9.21.29 | Country of origin | Bidder to state |  | - | 9. | 21. | 29 | 9 | 21 | 29
9.21.30 | Description | Bidder to state |  | - | 9. | 21. | 30 | 9 | 21 | 30
9.21.31 | Type test | Authority, year, Doc.no |  | - | 9. | 21. | 31 | 9 | 21 | 31
9.21.32 | Standards | IEC |  | - | 9. | 21. | 32 | 9 | 21 | 32
9.21.33 | Kind of meter | Bidder to state |  | - | 9. | 21. | 33 | 9 | 21 | 33
9.21.34 | Range | Bidder to state |  | - | 9. | 21. | 34 | 9 | 21 | 34
9.21.35 | Maker’s name | Bidder to state |  | - | 9. | 21. | 35 | 9 | 21 | 35
9.21.36 | Maker’s type and reference | Bidder to state |  | - | 9. | 21. | 36 | 9 | 21 | 36
9.21.37 | Country of origin | Bidder to state |  | - | 9. | 21. | 37 | 9 | 21 | 37
9.21.38 | Description | Bidder to state |  | - | 9. | 21. | 38 | 9 | 21 | 38
9.21.39 | Type test | Authority, year, Doc.no |  | - | 9. | 21. | 39 | 9 | 21 | 39
9.21.40 | Standards | IEC |  | - | 9. | 21. | 40 | 9 | 21 | 40
9.21.41 | Kind of meter | Bidder to state |  | - | 9. | 21. | 41 | 9 | 21 | 41
9.21.42 | Range | Bidder to state |  | - | 9. | 21. | 42 | 9 | 21 | 42
9.21.43 | Maker’s name | Bidder to state |  | - | 9. | 21. | 43 | 9 | 21 | 43
9.21.44 | Maker’s type and reference | Bidder to state |  | - | 9. | 21. | 44 | 9 | 21 | 44
9.21.45 | Country of origin | Bidder to state |  | - | 9. | 21. | 45 | 9 | 21 | 45
9.21.46 | Description | Bidder to state |  | - | 9. | 21. | 46 | 9 | 21 | 46
9.21.47 | Type test | Authority, year, Doc.no |  | - | 9. | 21. | 47 | 9 | 21 | 47
9.21.48 | Standards | IEC |  | - | 9. | 21. | 48 | 9 | 21 | 48
9.21.49 | Kind of meter | Bidder to state |  | - | 9. | 21. | 49 | 9 | 21 | 49
9.21.50 | Range | Bidder to state |  | - | 9. | 21. | 50 | 9 | 21 | 50
9.21.51 | Maker’s name | Bidder to state |  | - | 9. | 21. | 51 | 9 | 21 | 51
9.21.52 | Maker’s type and reference | Bidder to state |  | - | 9. | 21. | 52 | 9 | 21 | 52
9.21.53 | Country of origin | Bidder to state |  | - | 9. | 21. | 53 | 9 | 21 | 53
9.21.54 | Description | Bidder to state |  | - | 9. | 21. | 54 | 9 | 21 | 54
9.21.55 | Type test | Authority, year, Doc.no |  | - | 9. | 21. | 55 | 9 | 21 | 55
9.21.56 | Standards | IEC |  | - | 9. | 21. | 56 | 9 | 21 | 56
[8 empty] | 9 | 21 | 57 | tom rad
9.22. | OFC Approach Fibre Cable |  |  |  | 9. | 22. |  | 9 | 22 | 58 | R2
[8 empty] | 9 | 22 | 59 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 22 | 60 | R3
9.22.1 | Maker’s name | Bidder to state |  | - | 9. | 22. | 1 | 9 | 22 | 1
9.22.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 22. | 2 | 9 | 22 | 2
9.22.3 | Country of origin | Bidder to state |  | - | 9. | 22. | 3 | 9 | 22 | 3
9.22.4 | Description | Fibre optic cable |  | - | 9. | 22. | 4 | 9 | 22 | 4
9.22.5 | Type test | Authority, year, Doc.no |  | - | 9. | 22. | 5 | 9 | 22 | 5
9.22.6 | Standards | ITU-T G.655, ITU-T G.652, EIA/TIA 598, IEC 60794-1-1, 60794-1-2, 60974-4-10, 60793-2-50 |  | - | 9. | 22. | 6 | 9 | 22 | 6
9.22.7 | Number of fibres | 48 |  | - | 9. | 22. | 7 | 9 | 22 | 7
9.22.8 | Field mode wave length | 1310 |  | nm | 9. | 22. | 8 | 9 | 22 | 8
9.22.9 | Nominal cladding diameter | 125.0 |  | µm | 9. | 22. | 9 | 9 | 22 | 9
9.22.10 | Cable cut-off wavelength, maximum | 1260 |  | nm | 9. | 22. | 10 | 9 | 22 | 10
9.22.11 | Rodent proof | Yes |  | - | 9. | 22. | 11 | 9 | 22 | 11
9.22.12 | Tensile strength | 2000 |  | N | 9. | 22. | 12 | 9 | 22 | 12
9.22.13 | Crush strength per 100mm | 2000 |  | N | 9. | 22. | 13 | 9 | 22 | 13
9.22.14 | Attenuation coefficient maximum (1310-1625) | 0.4 |  | db/km | 9. | 22. | 14 | 9 | 22 | 14
9.22.15 | Minimum bending radius times of cable diameter Dynamic/Static | 20/10 |  | - | 9. | 22. | 15 | 9 | 22 | 15
9.22.16 | Cable-length/drum | Bidder to state |  | m | 9. | 22. | 16 | 9 | 22 | 16
9.22.17 | Weight/drum | Bidder to state |  | kg | 9. | 22. | 17 | 9 | 22 | 17
[8 empty] | 9 | 22 | 18 | tom rad
9.23. | Optical Distribution Frame (ODF) |  |  |  | 9. | 23. |  | 9 | 23 | 19 | R2
[8 empty] | 9 | 23 | 20 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 23 | 21 | R3
9.23.1 | Maker’s name | Bidder to state |  | - | 9. | 23. | 1 | 9 | 23 | 1
9.23.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 23. | 2 | 9 | 23 | 2
9.23.3 | Country of origin | Bidder to state |  | - | 9. | 23. | 3 | 9 | 23 | 3
9.23.4 | Description | Bidder to state |  | - | 9. | 23. | 4 | 9 | 23 | 4
9.23.5 | Type test | Authority, year, Doc.no |  | - | 9. | 23. | 5 | 9 | 23 | 5
9.23.6 | Standards | Contacts IEC 61754-4 |  | - | 9. | 23. | 6 | 9 | 23 | 6
9.23.7 | Insertion loss | <0.3 |  | dB | 9. | 23. | 7 | 9 | 23 | 7
9.23.8 | Attenuation variation at repeated connection/disconnection 500 times | 0.2 |  | dB | 9. | 23. | 8 | 9 | 23 | 8
9.23.9 | IP-class (Installed) | IP 54 |  | - | 9. | 23. | 9 | 9 | 23 | 9
9.23.10 | Life Time | >30 |  | years | 9. | 23. | 10 | 9 | 23 | 10
[8 empty] | 9 | 23 | 11 | tom rad
9.24. | Optical Transport Network (OTN) |  |  |  | 9. | 24. |  | 9 | 24 | 12 | R2
[8 empty] | 9 | 24 | 13 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 24 | 14 | R3
9.24.1 | Maker’s type and reference | To be stated by Bidder |  |  | 9. | 24. | 1 | 9 | 24 | 1
9.24.2 | Manufacturer | To be stated by Bidder |  |  | 9. | 24. | 2 | 9 | 24 | 2
9.24.3 | Country of origin | To be stated by Bidder |  |  | 9. | 24. | 3 | 9 | 24 | 3
9.24.4 | OTN Characteristics |  |  |  | 9. | 24. | 4 | 9 | 24 | 4
9.24.5 | Equipment Type | OTN |  |  | 9. | 24. | 5 | 9 | 24 | 5
9.24.6 | Auxiliary power supply, voltage range | -48 to -54 |  | V DC | 9. | 24. | 6 | 9 | 24 | 6
9.24.7 | Transmission Capacity | 4000G or better |  |  | 9. | 24. | 7 | 9 | 24 | 7
9.24.8 | Local/Remote Management | Open for integration, managing and monitoring on the already operational ZTE Network Management System (NMS) |  |  | 9. | 24. | 8 | 9 | 24 | 8
9.24.9 | Transmission Distance without Signal Degradation | 200 |  | km | 9. | 24. | 9 | 9 | 24 | 9
9.24.10 | Support 40 x 100/200G Lambda System | Yes |  |  | 9. | 24. | 10 | 9 | 24 | 10
9.24.11 | Supported Switching Granularity | ODU0/1/2/2e/3/4/Flex/ Packet/VC |  |  | 9. | 24. | 11 | 9 | 24 | 11
9.24.12 | Unified management | Yes |  |  | 9. | 24. | 12 | 9 | 24 | 12
9.24.13 | Reliability design (Supports 1+1 protection of main control, clock and power) | Yes |  |  | 9. | 24. | 13 | 9 | 24 | 13
9.24.14 | Intelligent Optical Network | Yes |  |  | 9. | 24. | 14 | 9 | 24 | 14
9.24.15 | Intelligent ROADM | Yes |  |  | 9. | 24. | 15 | 9 | 24 | 15
9.24.16 | Smooth Expansion and Upgrade | Yes |  |  | 9. | 24. | 16 | 9 | 24 | 16
9.24.17 | ODUK Protection | ODUK1 + 1 |  |  | 9. | 24. | 17 | 9 | 24 | 17
9.24.18 | Provided Service | Not less than 4 x 100G Capacity per direction in Line Side |  |  | 9. | 24. | 18 | 9 | 24 | 18
9.24.19 | Provided Service | Not less than 10 x 10G and 10 x GE as Access |  |  | 9. | 24. | 19 | 9 | 24 | 19
9.24.20 | OTDR |  |  |  | 9. | 24. | 20 | 9 | 24 | 20
9.24.21 | Built-in OTDR Function | Yes |  |  | 9. | 24. | 21 | 9 | 24 | 21
9.24.22 | Measure Optical Fiber Attenuation | Yes |  |  | 9. | 24. | 22 | 9 | 24 | 22
9.24.23 | Measure Connector Loss | Yes |  |  | 9. | 24. | 23 | 9 | 24 | 23
9.24.24 | Locate Optical Fiber Faults | Yes |  |  | 9. | 24. | 24 | 9 | 24 | 24
9.24.25 | Learn about Optical Fiber Loss along the Length | Yes |  |  | 9. | 24. | 25 | 9 | 24 | 25
[8 empty] | 9 | 24 | 26 | tom rad
9.25. | Optical Transport Network Equipment |  |  |  | 9. | 25. |  | 9 | 25 | 27 | R2
[8 empty] | 9 | 25 | 28 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 25 | 29 | R3
9.25.1 | Type | DWDM |  |  | 9. | 25. | 1 | 9 | 25 | 1
9.25.2 | Manufacturer | Bidder to state |  |  | 9. | 25. | 2 | 9 | 25 | 2
9.25.3 | Country of origin | Bidder to state |  |  | 9. | 25. | 3 | 9 | 25 | 3
9.25.4 | Manufacturer's type designation | Bidder to state |  |  | 9. | 25. | 4 | 9 | 25 | 4
9.25.5 | Catalogue number | Bidder to state |  |  | 9. | 25. | 5 | 9 | 25 | 5
9.25.6 | Firmaware version | Bidder to state |  |  | 9. | 25. | 6 | 9 | 25 | 6
9.25.7 | Functions supported |  |  |  | 9. | 25. | 7 | 9 | 25 | 7
9.25.8 | FOADM (Fixed Optical Add/Drop Multiplexer) and ROADM (Reconfigurable Optical Add/Drop Multiplexer)based on the support for ROADM optical layer wavelength service grooming | Yes |  |  | 9. | 25. | 8 | 9 | 25 | 8
9.25.9 | ODUk electrical switching, Packet switching and TDM switching | Yes |  |  | 9. | 25. | 9 | 9 | 25 | 9
9.25.10 | 80x10G/40G/100G and 53 400G large capacity transmission | Yes |  |  | 9. | 25. | 10 | 9 | 25 | 10
9.25.11 | 100Gbit/s System |  |  |  | 9. | 25. | 11 | 9 | 25 | 11
9.25.12 | 80/96/120 wavelengths | Yes |  |  | 9. | 25. | 12 | 9 | 25 | 12
9.25.13 | 80/96/120 100GE transmission | Yes |  |  | 9. | 25. | 13 | 9 | 25 | 13
9.25.14 | PM-QPSK Coherent Rx modulation for ULH transmission | Yes |  |  | 9. | 25. | 14 | 9 | 25 | 14
9.25.15 | Forward Error Correction (FEC), Advanced Forward Error Correction (AFEC), Soft Decision FEC (SD-FEC), Electrical Return-to-Zero (ERZ) and adaptive receiver etc. | Yes |  |  | 9. | 25. | 15 | 9 | 25 | 15
9.25.16 | Flexible add/drop of 1 to 80 wave-length with 50GHz channel spacing, and adjustable channel spacing (Gridless, n × 12.5GHz) | Yes |  |  | 9. | 25. | 16 | 9 | 25 | 16
9.25.17 | 4 types of electrical switching sub-racks(S1, S2, S3 and S6), which can implement ODU0/1/2/2e/3/4/flex/packet/VC based centralized non-blocking cell switching and realize flexible service scheduling in electrical layer | Yes |  |  | 9. | 25. | 17 | 9 | 25 | 17
[8 empty] | 9 | 25 | 18 | tom rad
9.26. | Packet Transport Network Equipment |  |  |  | 9. | 26. |  | 9 | 26 | 19 | R2
[8 empty] | 9 | 26 | 20 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 26 | 21 | R3
9.26.1 | Type | Bidder to state |  |  | 9. | 26. | 1 | 9 | 26 | 1
9.26.2 | Manufacturer | Bidder to state |  |  | 9. | 26. | 2 | 9 | 26 | 2
9.26.3 | Country of origin | Bidder to state |  |  | 9. | 26. | 3 | 9 | 26 | 3
9.26.4 | Manufacturer's type designation | Bidder to state |  |  | 9. | 26. | 4 | 9 | 26 | 4
9.26.5 | Catalogue number | Bidder to state |  |  | 9. | 26. | 5 | 9 | 26 | 5
9.26.6 | Firmaware version | Bidder to state |  |  | 9. | 26. | 6 | 9 | 26 | 6
9.26.7 | Functions supported |  |  |  | 9. | 26. | 7 | 9 | 26 | 7
9.26.8 | L2 switching (Ethernet/MPLS) | Yes |  |  | 9. | 26. | 8 | 9 | 26 | 8
9.26.9 | L1 switching (OTN/SDH) | Yes |  |  | 9. | 26. | 9 | 9 | 26 | 9
9.26.10 | Static MS-PW mode | Yes |  |  | 9. | 26. | 10 | 9 | 26 | 10
9.26.11 | TDM services via TDM E1 interface and Ch STM-N interface | Yes |  |  | 9. | 26. | 11 | 9 | 26 | 11
9.26.12 | OTN circuit service, as well as ODU0, ODU1, and ODU2/2E crossing granularity | Yes |  |  | 9. | 26. | 12 | 9 | 26 | 12
9.26.13 | Multiple virtual Ethernet connections such as E-LINE, E-LAN and E-TREE with traffic monitoring, QoS, OAM and protection function corresponding based on specification | Yes |  |  | 9. | 26. | 13 | 9 | 26 | 13
9.26.14 | ingress and egress port mirroring | Yes |  |  | 9. | 26. | 14 | 9 | 26 | 14
9.26.15 | port rate, duplex mode and forced/self-negotiation query | Yes |  |  | 9. | 26. | 15 | 9 | 26 | 15
9.26.16 | storm suppression of broadcast/multicast/unknown unicast packets | Yes |  |  | 9. | 26. | 16 | 9 | 26 | 16
9.26.17 | powerful VLAN function to divide virtual working groups(such as VLAN, QinQ) | Yes |  |  | 9. | 26. | 17 | 9 | 26 | 17
9.26.18 | Link aggregation | Yes |  |  | 9. | 26. | 18 | 9 | 26 | 18
9.26.19 | L2VPN multi-cast | Yes |  |  | 9. | 26. | 19 | 9 | 26 | 19
9.26.20 | VPLS/VPWS/H-VPLS | Yes |  |  | 9. | 26. | 20 | 9 | 26 | 20
9.26.21 | MAC address floating prohibition | Yes |  |  | 9. | 26. | 21 | 9 | 26 | 21
9.26.22 | Standard-based DiffServ, including traffic classification, policing, shaping, congestion control, queue scheduling | Yes |  |  | 9. | 26. | 22 | 9 | 26 | 22
9.26.23 | Multiple OAM mechanism such as MPLS-TP OAM, and Ethernet OAM, link OAM | Yes |  |  | 9. | 26. | 23 | 9 | 26 | 23
9.26.24 | network-level clock synchronization Multi-Service Bearer platform | Yes |  |  | 9. | 26. | 24 | 9 | 26 | 24
9.26.25 | PWE3 circuit emulation of E1, STM-N, and ETHERNET port | Yes |  |  | 9. | 26. | 25 | 9 | 26 | 25
9.26.26 | MPLS-TP tunnel | Yes |  |  | 9. | 26. | 26 | 9 | 26 | 26
[8 empty] | 9 | 26 | 27 | tom rad
9.27. | Synchronous Digital Hierarchy (SDH)Equipment STM-64 |  |  |  | 9. | 27. |  | 9 | 27 | 28 | R2
[8 empty] | 9 | 27 | 29 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 27 | 30 | R3
9.27.1 | Type | Bidder to state |  |  | 9. | 27. | 1 | 9 | 27 | 1
9.27.2 | Manufacturer | Bidder to state |  |  | 9. | 27. | 2 | 9 | 27 | 2
9.27.3 | Country of origin | Bidder to state |  |  | 9. | 27. | 3 | 9 | 27 | 3
9.27.4 | Manufacturer's type designation | Bidder to state |  |  | 9. | 27. | 4 | 9 | 27 | 4
9.27.5 | Catalogue number | Bidder to state |  |  | 9. | 27. | 5 | 9 | 27 | 5
9.27.6 | Firmaware version | Bidder to state |  |  | 9. | 27. | 6 | 9 | 27 | 6
9.27.7 | Functions supported |  |  |  | 9. | 27. | 7 | 9 | 27 | 7
9.27.8 | L2 switching (Ethernet/MPLS) | Yes |  |  | 9. | 27. | 8 | 9 | 27 | 8
9.27.9 | L1 switching (SDH VCs) | Yes |  |  | 9. | 27. | 9 | 9 | 27 | 9
9.27.10 | Static MS-PW mode | Yes |  |  | 9. | 27. | 10 | 9 | 27 | 10
9.27.11 | TDM services via TDM E1 interface and Ch STM-N interface | Yes |  |  | 9. | 27. | 11 | 9 | 27 | 11
9.27.12 | SDH circuit service, as well as VC12, VC3,and VC4 crossing granularity | Yes |  |  | 9. | 27. | 12 | 9 | 27 | 12
9.27.13 | Multiple virtual Ethernet connections such as E-LINE, E-LAN and E-TREE with traffic monitoring, QoS, OAM and protection function corresponding based on specification | Yes |  |  | 9. | 27. | 13 | 9 | 27 | 13
9.27.14 | ingress and egress port mirroring | Yes |  |  | 9. | 27. | 14 | 9 | 27 | 14
9.27.15 | port rate, duplex mode and forced/self-negotiation query | Yes |  |  | 9. | 27. | 15 | 9 | 27 | 15
9.27.16 | storm suppression of broadcast/multicast/unknown unicast packets | Yes |  |  | 9. | 27. | 16 | 9 | 27 | 16
9.27.17 | powerful VLAN function to divide virtual working groups(such as VLAN, QinQ) | Yes |  |  | 9. | 27. | 17 | 9 | 27 | 17
9.27.18 | Link aggregation | Yes |  |  | 9. | 27. | 18 | 9 | 27 | 18
9.27.19 | L2VPN multi-cast | Yes |  |  | 9. | 27. | 19 | 9 | 27 | 19
9.27.20 | VPLS/VPWS/H-VPLS | Yes |  |  | 9. | 27. | 20 | 9 | 27 | 20
9.27.21 | MAC address floating prohibition | Yes |  |  | 9. | 27. | 21 | 9 | 27 | 21
9.27.22 | Standard-based DiffServ, including traffic classification, policing, shaping, congestion control, queue scheduling | Yes |  |  | 9. | 27. | 22 | 9 | 27 | 22
9.27.23 | Multiple OAM mechanism such as MPLS-TP OAM, and Ethernet OAM, link OAM | Yes |  |  | 9. | 27. | 23 | 9 | 27 | 23
9.27.24 | network-level clock synchronization Multi-Service Bearer platform | Yes |  |  | 9. | 27. | 24 | 9 | 27 | 24
9.27.25 | PWE3 circuit emulation of E1, STM-N, and ETHERNET port | Yes |  |  | 9. | 27. | 25 | 9 | 27 | 25
9.27.26 | MPLS-TP tunnel | Yes |  |  | 9. | 27. | 26 | 9 | 27 | 26
[8 empty] | 9 | 27 | 27 | tom rad
9.28. | FOX 615 Equipment STM-16 |  |  |  | 9. | 28. |  | 9 | 28 | 28 | R2
[8 empty] | 9 | 28 | 29 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 28 | 30 | R3
9.28.1 | Type | Bidder to state |  |  | 9. | 28. | 1 | 9 | 28 | 1
9.28.2 | Manufacturer | Bidder to state |  |  | 9. | 28. | 2 | 9 | 28 | 2
9.28.3 | Country of origin | Bidder to state |  |  | 9. | 28. | 3 | 9 | 28 | 3
9.28.4 | Manufacturer's type designation | Bidder to state |  |  | 9. | 28. | 4 | 9 | 28 | 4
9.28.5 | Catalogue number | Bidder to state |  |  | 9. | 28. | 5 | 9 | 28 | 5
9.28.6 | Firmaware version | Bidder to state |  |  | 9. | 28. | 6 | 9 | 28 | 6
9.28.7 | Functions supported |  |  |  | 9. | 28. | 7 | 9 | 28 | 7
9.28.8 | L2 switching (Ethernet/MPLS) | Yes |  |  | 9. | 28. | 8 | 9 | 28 | 8
9.28.9 | L1 switching (SDH (KLMs)) | Yes |  |  | 9. | 28. | 9 | 9 | 28 | 9
9.28.10 | Static MS-PW mode | Yes |  |  | 9. | 28. | 10 | 9 | 28 | 10
9.28.11 | TDM services via TDM E1 interface and Ch STM-N interface | Yes |  |  | 9. | 28. | 11 | 9 | 28 | 11
9.28.12 | SDH circuit service, as well as (KLMs) or VC12, VC3,and VC4 crossing granularit | Yes |  |  | 9. | 28. | 12 | 9 | 28 | 12
9.28.13 | Multiple virtual Ethernet connections such as E-LINE, E-LAN and E-TREE with traffic monitoring, QoS, OAM and protection function corresponding based on specification | Yes |  |  | 9. | 28. | 13 | 9 | 28 | 13
9.28.14 | ingress and egress port mirroring | Yes |  |  | 9. | 28. | 14 | 9 | 28 | 14
9.28.15 | port rate, duplex mode and forced/self-negotiation query | Yes |  |  | 9. | 28. | 15 | 9 | 28 | 15
9.28.16 | storm suppression of broadcast/multicast/unknown unicast packets | Yes |  |  | 9. | 28. | 16 | 9 | 28 | 16
9.28.17 | powerful VLAN function to divide virtual working groups(such as VLAN, QinQ) | Yes |  |  | 9. | 28. | 17 | 9 | 28 | 17
9.28.18 | Link aggregation | Yes |  |  | 9. | 28. | 18 | 9 | 28 | 18
9.28.19 | L2VPN multi-cast | Yes |  |  | 9. | 28. | 19 | 9 | 28 | 19
9.28.20 | VPLS/VPWS/H-VPLS | Yes |  |  | 9. | 28. | 20 | 9 | 28 | 20
9.28.21 | MAC address floating prohibition | Yes |  |  | 9. | 28. | 21 | 9 | 28 | 21
9.28.22 | Standard-based DiffServ, including traffic classification, policing, shaping, congestion control, queue scheduling | Yes |  |  | 9. | 28. | 22 | 9 | 28 | 22
9.28.23 | Multiple OAM mechanism such as MPLS-TP OAM, and Ethernet OAM, link OAM | Yes |  |  | 9. | 28. | 23 | 9 | 28 | 23
9.28.24 | network-level clock synchronization Multi-Service Bearer platform | Yes |  |  | 9. | 28. | 24 | 9 | 28 | 24
9.28.25 | PWE3 circuit emulation of E1, STM-N, and ETHERNET port | Yes |  |  | 9. | 28. | 25 | 9 | 28 | 25
9.28.26 | OPIC (differential protection) | Yes |  |  | 9. | 28. | 26 | 9 | 28 | 26
9.28.27 | TEPI (Distance protection) | Yes |  |  | 9. | 28. | 27 | 9 | 28 | 27
[8 empty] | 9 | 28 | 28 | tom rad
9.29. | PABX Equipment |  |  |  | 9. | 29. |  | 9 | 29 | 29 | R2
[8 empty] | 9 | 29 | 30 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 29 | 31 | R3
9.29.1 | Type | Bidder to state |  |  | 9. | 29. | 1 | 9 | 29 | 1
9.29.2 | Manufacturer | Bidder to state |  |  | 9. | 29. | 2 | 9 | 29 | 2
9.29.3 | Country of origin | Bidder to state |  |  | 9. | 29. | 3 | 9 | 29 | 3
9.29.4 | Manufacturer's type designation | Bidder to state |  |  | 9. | 29. | 4 | 9 | 29 | 4
9.29.5 | Catalogue number | Bidder to state |  |  | 9. | 29. | 5 | 9 | 29 | 5
9.29.6 | Firmaware version | Bidder to state |  |  | 9. | 29. | 6 | 9 | 29 | 6
9.29.7 | Functions supported |  |  |  | 9. | 29. | 7 | 9 | 29 | 7
9.29.8 | L2 switching (Ethernet/MPLS) | Yes |  |  | 9. | 29. | 8 | 9 | 29 | 8
9.29.9 | Console cable supported | Yes |  |  | 9. | 29. | 9 | 9 | 29 | 9
9.29.10 | Corporate wide network Licensing | Yes |  |  | 9. | 29. | 10 | 9 | 29 | 10
9.29.11 | IP telephone Availability | Yes |  |  | 9. | 29. | 11 | 9 | 29 | 11
9.29.12 | SIP telephone Licensing | Yes |  |  | 9. | 29. | 12 | 9 | 29 | 12
9.29.13 | Digital telephone intergration | Yes |  |  | 9. | 29. | 13 | 9 | 29 | 13
9.29.14 | Analogue telephone intergration | Yes |  |  | 9. | 29. | 14 | 9 | 29 | 14
9.29.15 | ABC-F Intergration | Yes |  |  | 9. | 29. | 15 | 9 | 29 | 15
[8 empty] | 9 | 29 | 16 | tom rad
9.30. | Laptop Computer |  |  |  | 9. | 30. |  | 9 | 30 | 17 | R2
[8 empty] | 9 | 30 | 18 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 9 | 30 | 19 | R3
9.30.1 | Maker’s name | Bidder to state |  | - | 9. | 30. | 1 | 9 | 30 | 1
9.30.2 | Maker’s type and reference | Bidder to state |  | - | 9. | 30. | 2 | 9 | 30 | 2
9.30.3 | Country of origin | Bidder to state |  | - | 9. | 30. | 3 | 9 | 30 | 3
9.30.4 | Processor | intel Core i7 10th generation |  | - | 9. | 30. | 4 | 9 | 30 | 4
9.30.5 | Integrated camera | HD 720p with IR with microphone |  | - | 9. | 30. | 5 | 9 | 30 | 5
9.30.6 | Display | 14'' diagonal FHD IPS eDP+PSR anti-glare with ambient light sensor (1920x1080) 400 nits |  | - | 9. | 30. | 6 | 9 | 30 | 6
9.30.7 | Graphics | Integrated Intel UHD Graphics 620 Discrete AMD Radeon Pro WX 3200 (4GB GDDR5 dedicated) |  | - | 9. | 30. | 7 | 9 | 30 | 7
9.30.8 | System memory | 8 |  | GB | 9. | 30. | 8 | 9 | 30 | 8
9.30.9 | Internal storage SSD | 1 |  | TB | 9. | 30. | 9 | 9 | 30 | 9
9.30.10 | Communication WLAN and Bluetooth | Intel 8265 ac 2x2 + Bluetooth 4.2 WW with 2 antennas |  | - | 9. | 30. | 10 | 9 | 30 | 10
9.30.11 | Wireless WAN | No WWAN |  | - | 9. | 30. | 11 | 9 | 30 | 11
9.30.12 | Fingerprint sensor | Yes |  | - | 9. | 30. | 12 | 9 | 30 | 12
9.30.13 | Smart card reader | 1 |  | No. | 9. | 30. | 13 | 9 | 30 | 13
9.30.14 | Battery | Min. 50 |  | Wh | 9. | 30. | 14 | 9 | 30 | 14
9.30.15 | AC adapter | 65 W Fast charge |  | - | 9. | 30. | 15 | 9 | 30 | 15
9.30.16 | Warranty | 1 |  | Year | 9. | 30. | 16 | 9 | 30 | 16
9.30.17 | Country/Hardware kit | Country localisation AFRC-E |  | - | 9. | 30. | 17 | 9 | 30 | 17
9.30.18 | Keyboard | Dual point Backlit spill-resistant Collaboration AFRC-E |  | - | 9. | 30. | 18 | 9 | 30 | 18
9.30.19 | Chassi type | All metal |  | - | 9. | 30. | 19 | 9 | 30 | 19
9.30.20 | Back pack | Executive |  | - | 9. | 30. | 20 | 9 | 30 | 20
[8 empty] | 9 | 30 | 21 | tom rad
10. | Wide Area Monitoring Protection and Control |  |  |  | 10. |  |  | 10 | 30 | 22 | R1
10.1. | WAMPACS |  |  |  | 10. | 1. |  | 10 | 1 | 23 | R2
[8 empty] | 10 | 1 | 24 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 10 | 1 | 25 | R3
10.1.1 | Stability Control Sub-System | The following shall be the system performance requirements; |  | - | 10. | 1. | 1 | 10 | 1 | 1
10.1.2 |  | i. Control Function Not rely on GPS |  | - | 10. | 1. | 2 | 10 | 1 | 2
|  | ii. Data refresh rate ≥ 6 times per cycle |  | -
|  | iii. Trip generation/load in 278 ms or less following fault inception |  | -
|  | iv. Distributed decision-making |  | -
|  | v. Full-IED Embedded hardware |  | -
|  | vi. Be hardware independent |  | -
|  | vii. Be upgradeable with standard industry products |  | -
|  | viii. Real-time Operation System, Non-windows, non-Linux |  | -
10.1.2 | Stability Data Management System | The following shall be the software requirements; |  | - | 10. | 1. | 2 | 10 | 1 | 2
|  | i. Standard C++, C, or java shall be used |  | -
|  | ii. Data Base used by the system must be ORACLE |  | -
|  | iii. Support expansion of processing capacity |  | -
|  | iv. Operation System is windows or Linux |  | -
10.1.3 | Monitoring | 1. Non volatile memory for; |  | -
10.1.3 |  | i. Event recording |  | - | 10. | 1. | 3 | 10 | 1 | 3
|  | ii. Disturbance recording |  | -
|  | iii. Remote viewing report |  | -
|  | iv. Acquire the oscillography files in COMTRADE format |  | -
|  | 2. Inbuilt; |  | -
|  | i. Voltage Transformer Supervision |  | -
|  | ii. Current Transformer Supervision |  | -
|  | iii. Trip circuit Supervision |  | -
10.1.4 | Communication | The following shall be the communication requirements; |  | - | 10. | 1. | 4 | 10 | 1 | 4
|  | i. Front port for direct PC – IED administration PC-IED debugging. |  | -
|  | ii. All relay interrogation hardware and software |  | -
10.1.5 | AC current inputs | 1. The following shall be the CT requirements; |  | - | 10. | 1. | 5 | 10 | 1 | 5
|  | i. 1A or 5A |  | -
|  | ii. Continuous withstand – 4 times the nominal value |  | -
|  | iii. 10 second withstand – 30 times the nominal value |  | -
|  | iv. 1 second withstand – 100 times the nominal value |  | -
10.1.6 | AC voltage inputs | The following shall be the VT requirements; |  | - | 10. | 1. | 6 | 10 | 1 | 6
|  | i. 110V AC nominal phase to phase input |  | -
|  | ii. Operating voltage of 1 to 170V AC |  | -
|  | iii. A continuous withstand of 2 times the nominal voltage |  | -
|  | iv. A short time (1 second) withstand of at least 3 times the nominal voltage |  | -
10.1.7 | DC power supply | The following shall be the DC power supply requirements; |  | - | 10. | 1. | 7 | 10 | 1 | 7
|  | i. Normal operation at 80%~120% rated voltage |  | -
|  | ii. Static power consumption ≤ 50W |  | -
10.1.8 | Frequency | The following shall be the frequency requirements; |  | - | 10. | 1. | 8 | 10 | 1 | 8
|  | i. 50Hz will be used |  | -
10.1.9 | Binary inputs | The binary inputs shall; |  | - | 10. | 1. | 9 | 10 | 1 | 9
|  | i. Optically be coupled |  | -
|  | ii. Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  | -
|  | iii. Be programmable to internal logic functions |  | -
10.1.10 | Binary outputs | The following specifications shall apply for relay binary output; |  | - | 10. | 1. | 10 | 10 | 1 | 10
|  | i. Trip action time ≤ 8ms |  | -
|  | ii. Trip return time ≤ 5ms |  | -
|  | iii. Signal action time ≤10ms |  | -
|  | iv. Signal return time ≤ 10ms |  | -
10.1.11 | Product version | The IEDs shall be the top of range commercially produced and market proven reliability of service. |  | - | 10. | 1. | 11 | 10 | 1 | 11
10.1.12 | environment condition | The following specifications shall be the environment condition requirements; |  | - | 10. | 1. | 12 | 10 | 1 | 12
|  | i. Operating temperature： -10°C~+55°C |  | -
|  | ii. Storage temperature： -25°C~+55°C |  | -
|  | iii. Transport temperature： -1°C~+70°C |  | -
|  | iv. Relative humidity：5%~95% |  | -
10.1.13 | measurement accuracy | The following specifications shall be the measurement accuracy requirements; |  | - | 10. | 1. | 13 | 10 | 1 | 13
|  | i. AC voltage effective value measuring relative error ≤±1% |  | -
|  | ii. AC current effective value measuring relative error ≤±1% |  | -
|  | iii. Active power measuring relative error ≤±2% |  | -
10.1.14 | Print interface | Configure with print interface |  | - | 10. | 1. | 14 | 10 | 1 | 14
10.1.15 | Synchronous clock interface | Configure with synchronous clock interface |  | - | 10. | 1. | 15 | 10 | 1 | 15
10.1.16 | User Interface | The following specifications shall be the UI requirements; |  | - | 10. | 1. | 16 | 10 | 1 | 16
|  | i. Monitoring, and management |  | -
|  | ii. Display, reporting, and data modifications |  | -
|  | iii. Installation of new analytics and modifications of UI configurations |  | -
10.1.17 | Reference | Shall have installed the same system in three different countries. The system shall have been put in operation at least 2 years. |  | - | 10. | 1. | 17 | 10 | 1 | 17
[8 empty] | 10 | 1 | 18 | tom rad
11. | Distribution |  |  |  | 11. |  |  | 11 | 1 | 19 | R1
11.1. | Wooden poles 12m |  |  |  | 11. | 1. |  | 11 | 1 | 20 | R2
[8 empty] | 11 | 1 | 21 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 11 | 1 | 22 | R3
11.1.1 | Name of manufacturer | Bidder to state |  | - | 11. | 1. | 1 | 11 | 1 | 1
11.1.2 | Country of manufacture | Bidder to state |  | - | 11. | 1. | 2 | 11 | 1 | 2
11.1.3 | Timber species | Bidder to state |  | - | 11. | 1. | 3 | 11 | 1 | 3
11.1.4 | Standard | SANS 754 |  | - | 11. | 1. | 4 | 11 | 1 | 4
11.1.5 | Class | Bidder to state |  | - | 11. | 1. | 5 | 11 | 1 | 5
11.1.6 | Minimum fibre stress | 55 |  | Mpa | 11. | 1. | 6 | 11 | 1 | 6
11.1.7 | Preservative |  |  |  | 11. | 1. | 7 | 11 | 1 | 7
11.1.8 | - kind | CCA |  | - | 11. | 1. | 8 | 11 | 1 | 8
11.1.9 | - according to standard | BS 1990: Part 1, BS 144 |  | - | 11. | 1. | 9 | 11 | 1 | 9
11.1.10 | Length | 12 |  | m | 11. | 1. | 10 | 11 | 1 | 10
11.1.11 | Circumference at 1.8 m from the butt |  |  | cm | 11. | 1. | 11 | 11 | 1 | 11
11.1.12 | Circumference at 1.8 m from the top |  |  | cm | 11. | 1. | 12 | 11 | 1 | 12
11.1.13 | Rated load (at 30 cm from top, planting depth H1) |  |  | kN | 11. | 1. | 13 | 11 | 1 | 13
[8 empty] | 11 | 1 | 14 | tom rad
11.2. | ABC 3x120+70 |  |  |  | 11. | 2. |  | 11 | 2 | 15 | R2
[8 empty] | 11 | 2 | 16 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 11 | 2 | 17 | R3
11.2.1 | Name of Manufacturer | Bidder to state |  | - | 11. | 2. | 1 | 11 | 2 | 1
11.2.2 | Country of origin | Bidder to state |  | - | 11. | 2. | 2 | 11 | 2 | 2
11.2.3 | Standard | Bidder to state |  | - | 11. | 2. | 3 | 11 | 2 | 3
11.2.4 | Type | Bidder to state |  | - | 11. | 2. | 4 | 11 | 2 | 4
11.2.5 | Rated voltage | 1 |  | kV | 11. | 2. | 5 | 11 | 2 | 5
11.2.6 | Manufacturer's type designation | Bidder to state |  | - | 11. | 2. | 6 | 11 | 2 | 6
11.2.7 | Cross-sectional area of phase conductor | 120 |  | mm² | 11. | 2. | 7 | 11 | 2 | 7
11.2.8 | Cross-sectional area of supporting core | 70 |  | mm² | 11. | 2. | 8 | 11 | 2 | 8
11.2.9 | Overall diameter | Bidder to state |  | mm | 11. | 2. | 9 | 11 | 2 | 9
11.2.10 | Insulation material | XLPE |  | - | 11. | 2. | 10 | 11 | 2 | 10
11.2.11 | Insulation thickness | Bidder to state |  | mm | 11. | 2. | 11 | 11 | 2 | 11
11.2.12 | Weight | Bidder to state |  | kg/km | 11. | 2. | 12 | 11 | 2 | 12
11.2.13 | Calculated breaking load | 8 |  | kN | 11. | 2. | 13 | 11 | 2 | 13
11.2.14 | Calculated Current-carrying capacity +800 at +400 | 283 |  | A | 11. | 2. | 14 | 11 | 2 | 14
11.2.15 | Short-circuit capacity (1 sec.) | 11 |  | kA | 11. | 2. | 15 | 11 | 2 | 15
11.2.16 | Rated DC resistance at 200 C | Bidder to state |  | Ω/km | 11. | 2. | 16 | 11 | 2 | 16
[8 empty] | 11 | 2 | 17 | tom rad
11.3. | 33 kV Single-phase Load Break Fuse |  |  |  | 11. | 3. |  | 11 | 3 | 18 | R2
[8 empty] | 11 | 3 | 19 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 11 | 3 | 20 | R3
11.3.1 | Make | Bidder to state |  | - | 11. | 3. | 1 | 11 | 3 | 1
11.3.2 | Manufacturer's type designation | Bidder to state |  | - | 11. | 3. | 2 | 11 | 3 | 2
11.3.3 | Description | Bidder to state |  | - | 11. | 3. | 3 | 11 | 3 | 3
11.3.4 | Type | Bidder to state |  | - | 11. | 3. | 4 | 11 | 3 | 4
11.3.5 | Standard | Bidder to state |  | - | 11. | 3. | 5 | 11 | 3 | 5
11.3.6 | Rated current | min. 100 |  | A | 11. | 3. | 6 | 11 | 3 | 6
11.3.7 | Rated voltage | 36 |  | kV | 11. | 3. | 7 | 11 | 3 | 7
11.3.8 | Rated short-time (1 sec.) witstand current, Ith | 25 |  | kAr.m.s | 11. | 3. | 8 | 11 | 3 | 8
11.3.9 | Creepage distance | 1324 |  | mm | 11. | 3. | 9 | 11 | 3 | 9
[8 empty] | 11 | 3 | 10 | tom rad
11.4. | 33/0.4 kV Housing Distribution Transformer |  |  |  | 11. | 4. |  | 11 | 4 | 11 | R2
[8 empty] | 11 | 4 | 12 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 11 | 4 | 13 | R3
11.4.1 | Type | 3-phase oil immersed |  | - | 11. | 4. | 1 | 11 | 4 | 1
11.4.2 | Manufacturer | Bidder to state |  | - | 11. | 4. | 2 | 11 | 4 | 2
11.4.3 | Country of origin | Bidder to state |  | - | 11. | 4. | 3 | 11 | 4 | 3
11.4.4 | Manufacturer's type designation | Bidder to state |  | - | 11. | 4. | 4 | 11 | 4 | 4
11.4.5 | Standard | IEC 60076, EN HD 428, EN 50216 |  | - | 11. | 4. | 5 | 11 | 4 | 5
11.4.6 | Type test report | Authority, year, Doc.no |  | - | 11. | 4. | 6 | 11 | 4 | 6
11.4.7 | Installation | Outdoor |  |  | 11. | 4. | 7 | 11 | 4 | 7
11.4.8 | Rated power | 100 |  | kVA | 11. | 4. | 8 | 11 | 4 | 8
11.4.9 | Rated voltage | 33/0.4 |  | kV | 11. | 4. | 9 | 11 | 4 | 9
11.4.10 | Off-circuit tap changer | ± 2 x 2,5 % |  | - | 11. | 4. | 10 | 11 | 4 | 10
11.4.11 | Impedance | 4 |  | % | 11. | 4. | 11 | 11 | 4 | 11
11.4.12 | Connection | Dyn11 |  | - | 11. | 4. | 12 | 11 | 4 | 12
11.4.13 | Short-circuit voltage | Bidder to state |  | % | 11. | 4. | 13 | 11 | 4 | 13
11.4.14 | Zero-sequence impedance | Bidder to state |  | ohm | 11. | 4. | 14 | 11 | 4 | 14
11.4.15 | No-load losses | Bidder to state |  | W | 11. | 4. | 15 | 11 | 4 | 15
11.4.16 | Load losses | Bidder to state |  | W | 11. | 4. | 16 | 11 | 4 | 16
11.4.17 | Temperature rise, oil | 50 |  | K | 11. | 4. | 17 | 11 | 4 | 17
11.4.18 | Temperature rise, winding | 55 |  | K | 11. | 4. | 18 | 11 | 4 | 18
11.4.19 | Type of cooling | ONAN |  | - | 11. | 4. | 19 | 11 | 4 | 19
11.4.20 | Sound level | Bidder to state |  | dB(A) | 11. | 4. | 20 | 11 | 4 | 20
11.4.21 | Type of tank | Sealed, bolted lid |  | - | 11. | 4. | 21 | 11 | 4 | 21
11.4.22 | Total weight | Bidder to state |  | kg | 11. | 4. | 22 | 11 | 4 | 22
11.4.20 | Dimensions (length x width x height) | Bidder to state |  | mm | 11. | 4. | 20 | 11 | 4 | 20
[8 empty] | 11 | 4 | 21 | tom rad
12. | Civil |  |  |  | 12. |  |  | 12 | 4 | 22 | R1
12.1. | Gabions (for substation perimeter; Refer to drawing PP-ZTIP-P04-ODSS-C109_Nakonde SS GA_R00_30062026 Note 4) |  |  |  | 12. | 1. |  | 12 | 1 | 23 | R2
[8 empty] | 12 | 1 | 24 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 12 | 1 | 25 | R3
12.1.1 | Manufacturer | Bidder to state |  | - | 12. | 1. | 1 | 12 | 1 | 1
12.1.2 | Country of origin | Bidder to state |  | - | 12. | 1. | 2 | 12 | 1 | 2
12.1.3 | Description | Welded gabions |  | - | 12. | 1. | 3 | 12 | 1 | 3
12.1.4 | Wire, Hard Drawn Steel, Electrically Welded | 4 |  | mm | 12. | 1. | 4 | 12 | 1 | 4
12.1.5 | Weld mesh aperture | 75x75 |  | mm | 12. | 1. | 5 | 12 | 1 | 5
12.1.6 | Size | 1x1x2 |  | m | 12. | 1. | 6 | 12 | 1 | 6
12.1.20 | Life Time | >50 |  | years | 12. | 1. | 20 | 12 | 1 | 20
[8 empty] | 12 | 1 | 21 | tom rad
13. | Tools |  |  |  | 13. |  |  | 13 | 1 | 22 | R1
13.1. | Splicing Machine |  |  |  | 13. | 1. |  | 13 | 1 | 23 | R2
[8 empty] | 13 | 1 | 24 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 1 | 25 | R3
13.1.1 | Fibre alignment method | Active core alignment |  |  | 13. | 1. | 1 | 13 | 1 | 1
13.1.2 | Applicable fibre |  |  |  | 13. | 1. | 2 | 13 | 1 | 2
13.1.3 | -Fibre Type | Single Mode |  |  | 13. | 1. | 3 | 13 | 1 | 3
Multi-Mode
13.1.4 | -Cladding diameter | Bidder to state |  |  | 13. | 1. | 4 | 13 | 1 | 4
13.1.5 | Applicable coating |  |  |  | 13. | 1. | 5 | 13 | 1 | 5
13.1.6 | -Sheath clamp | Coating diameter: max. 3 000 μm |  |  | 13. | 1. | 6 | 13 | 1 | 6
cleave length: 5 mm - 16 mm
13.1.7 | Fibre splice performance |  |  |  | 13. | 1. | 7 | 13 | 1 | 7
13.1.8 | -Splice loss | ITU-T G.652: avg. 0.02 dB |  |  | 13. | 1. | 8 | 13 | 1 | 8
ITU-T G.651: avg. 0.01 dB
ITU-T G.653: avg. 0.04 dB
ITU-T G.655: avg. 0.04 dB
ITU-T G.657: avg. 0.02 dB
13.1.9 | -Splice time | SM FAST mode: avg. 7 sec - 9 se |  |  | 13. | 1. | 9 | 13 | 1 | 9
AUTO mode: 14 sec - 16 sec
13.1.10 | Applicable protection sleeve |  |  |  | 13. | 1. | 10 | 13 | 1 | 10
13.1.11 | -Sleeve type | Heat shrinkable sleeve |  |  | 13. | 1. | 11 | 13 | 1 | 11
13.1.12 | -Sleeve length | Max. 66 mm |  |  | 13. | 1. | 12 | 13 | 1 | 12
13.1.13 | -Sleeve diameter | Max. 6.0 mm before shrinking |  |  | 13. | 1. | 13 | 13 | 1 | 13
13.1.14 | Sleeve heat performance |  |  |  | 13. | 1. | 14 | 13 | 1 | 14
13.1.15 | -Heat time | 60 mm slim mode: avg. 9 sec - 10 sec |  |  | 13. | 1. | 15 | 13 | 1 | 15
60 mm mode: avg. 13 sec - 15 sec
13.1.16 | Fibre tensile test force | Approx. 2.0 N |  |  | 13. | 1. | 16 | 13 | 1 | 16
13.1.17 | Electrode life | 5000+ |  |  | 13. | 1. | 17 | 13 | 1 | 17
13.1.18 | Dimensions (W × D × H) | Within 170×173×150 mm |  |  | 13. | 1. | 18 | 13 | 1 | 18
13.1.19 | Weight | 2.8 kg (with battery) |  |  | 13. | 1. | 19 | 13 | 1 | 19
13.1.20 | Environmental condition |  |  |  | 13. | 1. | 20 | 13 | 1 | 20
13.1.21 | -Temperature | Operate: -10 - +50 |  | °C | 13. | 1. | 21 | 13 | 1 | 21
|  | Storage: -40 - +80 |  | °C
13.1.22 | -Humidity | Operate: 0 - 95 non-condensing |  | % RH | 13. | 1. | 22 | 13 | 1 | 22
|  | Storage: 0 - 95 non-condensing |  | % RH
13.1.23 | -Altitude | 1600 |  | masl | 13. | 1. | 23 | 13 | 1 | 23
13.1.24 | AC adaptor Input | AC 100 to 240 V, 50/60 Hz, max. 1.5 A |  |  | 13. | 1. | 24 | 13 | 1 | 24
13.1.25 | Battery pack |  |  |  | 13. | 1. | 25 | 13 | 1 | 25
13.1.26 | -Type | Rechargeable lithium-ion |  |  | 13. | 1. | 26 | 13 | 1 | 26
13.1.27 | -Output | Approx. DC 14.4 V / 6,380 mAh |  |  | 13. | 1. | 27 | 13 | 1 | 27
13.1.28 | -Capacity | Approx. 300 splice and heat cycles |  |  | 13. | 1. | 28 | 13 | 1 | 28
13.1.29 | -Temperature | Recharge: 0°C - 40°C |  |  | 13. | 1. | 29 | 13 | 1 | 29
13.1.30 |  | Storage: -20°C - +30°C |  |  | 13. | 1. | 30 | 13 | 1 | 30
13.1.31 | -Battery life | Approx. 500 recharge cycles |  |  | 13. | 1. | 31 | 13 | 1 | 31
13.1.32 | Display |  |  |  | 13. | 1. | 32 | 13 | 1 | 32
13.1.33 | LCD monitor | TFT 5 inches with touch screen |  |  | 13. | 1. | 33 | 13 | 1 | 33
13.1.34 | Magnification | 200 to 300x |  |  | 13. | 1. | 34 | 13 | 1 | 34
13.1.35 | Illumination V-grooves | LED lamp |  |  | 13. | 1. | 35 | 13 | 1 | 35
13.1.36 | Interface |  |  |  | 13. | 1. | 36 | 13 | 1 | 36
13.1.37 | -PC | USB2.0 Mini B type |  |  | 13. | 1. | 37 | 13 | 1 | 37
13.1.38 | -External LED lamp | USB2.0 A type |  |  | 13. | 1. | 38 | 13 | 1 | 38
approx. DC 5 V, 500 mA
13.1.39 | -Ribbon stripper | Mini DIN 6 pin |  |  | 13. | 1. | 39 | 13 | 1 | 39
DC 12 V, max. 1 A
13.1.40 | -Wireless | Bluetooth 4.1 LE |  |  | 13. | 1. | 40 | 13 | 1 | 40
13.1.41 | Data storage |  |  |  | 13. | 1. | 41 | 13 | 1 | 41
13.1.42 | -Splice mode | 100 splice modes |  |  | 13. | 1. | 42 | 13 | 1 | 42
13.1.43 | -Heat mode | 30 heat modes |  |  | 13. | 1. | 43 | 13 | 1 | 43
13.1.44 | -Splice result | 20 000 splices |  |  | 13. | 1. | 44 | 13 | 1 | 44
13.1.45 | -Splice image | 100 images |  |  | 13. | 1. | 45 | 13 | 1 | 45
13.1.46 | Screw hole for tripod | 1/4-20UNC |  |  | 13. | 1. | 46 | 13 | 1 | 46
13.1.47 | Other features |  |  |  | 13. | 1. | 47 | 13 | 1 | 47
13.1.48 | -Automatic functions | Splice mode select by fibre type analysis |  |  | 13. | 1. | 48 | 13 | 1 | 48
Discharge power calibration
Wind protector: open/close
Sheath clamp: open
Heater lid: open/close
Heater clamp: open/close
13.1.49 | -Reference guide | Video and PDF file stored in splicer |  |  | 13. | 1. | 49 | 13 | 1 | 49
13.1.50 | -Sheath clamp | Easy sleeve positioning clamp |  |  | 13. | 1. | 50 | 13 | 1 | 50
13.1.51 | -Electrode | Replaceable without tool |  |  | 13. | 1. | 51 | 13 | 1 | 51
13.1.52 | Cleaver/Stripper/Alcohol Dispenser | Set/Lot |  |  | 13. | 1. | 52 | 13 | 1 | 52
[8 empty] | 13 | 1 | 53 | tom rad
13.2. | Circuit Breaker Analyser |  |  |  | 13. | 2. |  | 13 | 2 | 54 | R2
[8 empty] | 13 | 2 | 55 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 2 | 56 | R3
13.2.1 | Make | Megger TM1800 Expert |  |  | 13. | 2. | 1 | 13 | 2 | 1
13.2.2 | Dual Ground Timing Circuit Breaker Analyze | Yes |  |  | 13. | 2. | 2 | 13 | 2 | 2
13.2.3 | CABA Software | Yes |  |  | 13. | 2. | 3 | 13 | 2 | 3
13.2.4 | USB communication interface | Yes |  |  | 13. | 2. | 4 | 13 | 2 | 4
13.2.5 | Transducers for motion, vibration, timing, contact, resistance and DRM, including all accessories | Yes |  |  | 13. | 2. | 5 | 13 | 2 | 5
13.2.6 | Mains input (nominal) | 240 |  | VAC | 13. | 2. | 6 | 13 | 2 | 6
13.2.7 | Frequency | 50 |  | Hz | 13. | 2. | 7 | 13 | 2 | 7
13.2.8 | Power consumption | <250 |  | VA | 13. | 2. | 8 | 13 | 2 | 8
13.2.9 | Dimensions | Bidder to state |  |  | 13. | 2. | 9 | 13 | 2 | 9
13.2.10 | Weight | Bidder to state |  |  | 13. | 2. | 10 | 13 | 2 | 10
13.2.11 | External input - TRIG IN |  |  |  | 13. | 2. | 11 | 13 | 2 | 11
13.2.12 | -Voltage mode |  |  |  | 13. | 2. | 12 | 13 | 2 | 12
13.2.13 | -Input range | 0 – 250 AC, 0 – ± 300 DC |  | V | 13. | 2. | 13 | 13 | 2 | 13
13.2.14 | -Threshold level | User configurable in software in steps of 1 |  | V | 13. | 2. | 14 | 13 | 2 | 14
13.2.15 | -Contact mode |  |  |  | 13. | 2. | 15 | 13 | 2 | 15
13.2.16 | -Open circuit voltage | 35 ±20% |  | VDC | 13. | 2. | 16 | 13 | 2 | 16
13.2.17 | -Short circuit current | 10-40 |  | mA | 13. | 2. | 17 | 13 | 2 | 17
13.2.18 | -Threshold level | 1-2k |  | Ω | 13. | 2. | 18 | 13 | 2 | 18
13.2.19 | External outputs -TRIG OUT |  |  |  | 13. | 2. | 19 | 13 | 2 | 19
13.2.20 | -Pulse duration | 1 – 999, user configurable in steps of 1 |  | ms | 13. | 2. | 20 | 13 | 2 | 20
13.2.21 | -Voltage mode |  |  |  | 13. | 2. | 21 | 13 | 2 | 21
13.2.22 | -Open circuit voltage | 12 ±5% |  | VDC | 13. | 2. | 22 | 13 | 2 | 22
13.2.23 | -Voltage at 0.5 A | 9 ±10% |  | VDC | 13. | 2. | 23 | 13 | 2 | 23
13.2.24 | -Max. short circuit current | 1.5 |  | A | 13. | 2. | 24 | 13 | 2 | 24
13.2.25 | -Contact mode |  |  |  | 13. | 2. | 25 | 13 | 2 | 25
13.2.26 | -Max. switching current | 0.5-1 at 12V and resistive load |  | A | 13. | 2. | 26 | 13 | 2 | 26
13.2.27 | -Voltage drop at 0.5 A | 4.5 ±10% |  | VDC | 13. | 2. | 27 | 13 | 2 | 27
13.2.28 | -Short circuit protection | Fuse 1 fast acting type (F1H250V) |  | ADC | 13. | 2. | 28 | 13 | 2 | 28
13.2.29 | Communication interfaces |  |  |  | 13. | 2. | 29 | 13 | 2 | 29
13.2.30 | USB | Universal Serial Bus ver. 2.0 |  |  | 13. | 2. | 30 | 13 | 2 | 30
13.2.31 | Ethernet | 100 base-Tx Fast Ethernet |  |  | 13. | 2. | 31 | 13 | 2 | 31
13.2.32 | External screen | SVGA, up to 800 x 600 at 24 bit color, 32 MB SDRAM |  |  | 13. | 2. | 32 | 13 | 2 | 32
13.2.33 | CABA Local | Circuit breaker analyzing software |  |  | 13. | 2. | 33 | 13 | 2 | 33
13.2.34 | Available languages | English, French, German, Spanish, Swedish. Translation kit available |  |  | 13. | 2. | 34 | 13 | 2 | 34
13.2.35 | Display | Super-Bright for good visibility in direct Sunlight |  |  | 13. | 2. | 35 | 13 | 2 | 35
13.2.36 | Diagonal size | 21 cm (8”) |  |  | 13. | 2. | 36 | 13 | 2 | 36
13.2.37 | Keyboard | Built-in |  |  | 13. | 2. | 37 | 13 | 2 | 37
13.2.38 | Modules |  |  |  | 13. | 2. | 38 | 13 | 2 | 38
13.2.39 | Control module | Yes |  |  | 13. | 2. | 39 | 13 | 2 | 39
13.2.40 | -Number of channels | 3 |  | Nos. | 13. | 2. | 40 | 13 | 2 | 40
13.2.41 | -Time base inaccuracy | ±0.01 of reading ±1 sample interval |  | % | 13. | 2. | 41 | 13 | 2 | 41
13.2.42 | -Max. sample rate | 10 k |  | Hz | 13. | 2. | 42 | 13 | 2 | 42
13.2.43 | -Measurement time | 45 at 10 kHz sample rate, |  | s | 13. | 2. | 43 | 13 | 2 | 43
|  | 90 at 5 kHz sample rate, |  | s
|  | 200 at 10 kHz sample rate using datacompression |  | s
13.2.44 | Timing M/R module | Yes |  |  | 13. | 2. | 44 | 13 | 2 | 44
13.2.45 | -No. of channels | 6 |  | Nos. | 13. | 2. | 45 | 13 | 2 | 45
13.2.46 | -Time base inaccuracy | ±0.01 of reading ±1 sample interval |  | % | 13. | 2. | 46 | 13 | 2 | 46
13.2.47 | -Min. resolution | 0.05 |  | ms | 13. | 2. | 47 | 13 | 2 | 47
13.2.48 | -Max. sample rate | 40k |  | Hz | 13. | 2. | 48 | 13 | 2 | 48
13.2.49 | -Measurement time | 8 at 40 kHz sample rate, |  | s | 13. | 2. | 49 | 13 | 2 | 49
|  | 32 at 10 kHz sample rate, |  | s
|  | 200 at 10 kHz sample rate using data compression |  | s
Data compression available at samplerates up to 20 kHz
13.2.50 | DCM module | Yes |  |  | 13. | 2. | 50 | 13 | 2 | 50
13.2.51 | -No. of channels | 6 |  | Nos. | 13. | 2. | 51 | 13 | 2 | 51
13.2.52 | -Voltage | 0 - 5 rms AC |  | VACrms | 13. | 2. | 52 | 13 | 2 | 52
13.2.53 | -Current | 0 - 70 rms AC |  | mA ACrms | 13. | 2. | 53 | 13 | 2 | 53
13.2.54 | DCM module – Dual Ground testing | Yes |  |  | 13. | 2. | 54 | 13 | 2 | 54
13.2.55 | -No. of channels | 6 |  | Nos. | 13. | 2. | 55 | 13 | 2 | 55
13.2.56 | -Voltage | V |  | VACrms | 13. | 2. | 56 | 13 | 2 | 56
13.2.57 | -Current | mA |  | mA ACrms | 13. | 2. | 57 | 13 | 2 | 57
13.2.58 | Analog module | Yes |  |  | 13. | 2. | 58 | 13 | 2 | 58
13.2.59 | -No. of channels | 3 |  | Nos. | 13. | 2. | 59 | 13 | 2 | 59
13.2.60 | -Time base inaccuracy | ±0.01 of reading ±1 sample interval |  | % | 13. | 2. | 60 | 13 | 2 | 60
13.2.61 | -Max. sample rate | 40 |  | Hz | 13. | 2. | 61 | 13 | 2 | 61
13.2.62 | -Measurement time | 35 at 40 kHz sample rate, |  | s | 13. | 2. | 62 | 13 | 2 | 62
|  | 70 at 20 kHz sample rate, |  | s
|  | 200 at 10 kHz sample rate using data compression |  | s
13.2.63 | -Transducer resistance | 500 – 10k at 10 V output |  | Ω | 13. | 2. | 63 | 13 | 2 | 63
13.2.64 | Digital module | Yes |  |  | 13. | 2. | 64 | 13 | 2 | 64
13.2.65 | -No. of channels | 6 |  | Nos. | 13. | 2. | 65 | 13 | 2 | 65
13.2.66 | -Supported types | Incremental transducers, RS422 |  |  | 13. | 2. | 66 | 13 | 2 | 66
13.2.67 | -Time base inaccuracy | ±0.01 of reading ±1 sample interval |  | % | 13. | 2. | 67 | 13 | 2 | 67
13.2.68 | -Max. sample rate | 20k |  | Hz | 13. | 2. | 68 | 13 | 2 | 68
13.2.69 | -Measurement time | 35 at 20 kHz sample rate, |  | s | 13. | 2. | 69 | 13 | 2 | 69
|  | 70 at 10 kHz sample rate, |  | s
|  | 200 at 10 kHz sample rate using data compression |  | s
13.2.70 | Timing Aux module | Yes |  |  | 13. | 2. | 70 | 13 | 2 | 70
13.2.71 | -No. of channels | 6 |  | Nos. | 13. | 2. | 71 | 13 | 2 | 71
13.2.72 | -Time base inaccuracy | ±0.01 of reading ±1 sample interval |  | % | 13. | 2. | 72 | 13 | 2 | 72
13.2.73 | -Max. sample rate | 20 |  | kHz | 13. | 2. | 73 | 13 | 2 | 73
13.2.74 | -Measurement time | 35 at 20 kHz sample rate, |  | s | 13. | 2. | 74 | 13 | 2 | 74
|  | 70 at 10 kHz sample rate, |  | s
|  | 200 at 10 kHz sample rate using data compression |  | s
13.2.75 | Transducers with mounting kits | Yes |  |  | 13. | 2. | 75 | 13 | 2 | 75
13.2.76 | All Cables for testing | Yes |  |  | 13. | 2. | 76 | 13 | 2 | 76
13.2.77 | Accessories to be included | Yes |  |  | 13. | 2. | 77 | 13 | 2 | 77
13.2.78 | HDD module | Yes |  |  | 13. | 2. | 78 | 13 | 2 | 78
13.2.79 | Environment |  |  |  | 13. | 2. | 79 | 13 | 2 | 79
13.2.80 | Application field | For use in high-voltage substations and industrial environment |  |  | 13. | 2. | 80 | 13 | 2 | 80
13.2.81 | Operating Temperature | -1 to +50 |  | °C | 13. | 2. | 81 | 13 | 2 | 81
13.2.82 | Storage & transport | -55 to +70 |  | °C | 13. | 2. | 82 | 13 | 2 | 82
13.2.83 | Humidity | 85 |  | % | 13. | 2. | 83 | 13 | 2 | 83
13.2.84 | Altitude | 1400 |  | m | 13. | 2. | 84 | 13 | 2 | 84
13.2.85 | Manufacturers Authorization to be provided with bid | Yes |  |  | 13. | 2. | 85 | 13 | 2 | 85
13.2.86 | Calibration certificate to be provided on delivery | Yes |  |  | 13. | 2. | 86 | 13 | 2 | 86
13.2.87 | Brochure to be provided with bid | Yes |  |  | 13. | 2. | 87 | 13 | 2 | 87
13.2.88 | User Manual to be provided on delivery | Yes |  |  | 13. | 2. | 88 | 13 | 2 | 88
13.2.89 | IEC standards | Yes |  |  | 13. | 2. | 89 | 13 | 2 | 89
[8 empty] | 13 | 2 | 90 | tom rad
13.3. | Omicron CT Analyser |  |  |  | 13. | 3. |  | 13 | 3 | 91 | R2
[8 empty] | 13 | 3 | 92 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 3 | 93 | R3
13.3.1 | Omicron CT Analyzer |  |  |  | 13. | 3. | 1 | 13 | 3 | 1
13.3.2 | Measure CT ratio, composite error, excitation and knee point, winding resistance. |  |  |  | 13. | 3. | 2 | 13 | 3 | 2
13.3.3 | Measure and assesseCTs with accuracy classes ≥ 0.3 according to IEC and IEEE standards |  |  |  | 13. | 3. | 3 | 13 | 3 | 3
13.3.4 | standard package to accuracy classes ≥ 0.1 and additional assessment standards |  |  |  | 13. | 3. | 4 | 13 | 3 | 4
13.3.5 | Measures protection CTs according to IEEE C57.13 (does not support metering CTs) |  |  |  | 13. | 3. | 5 | 13 | 3 | 5
13.3.6 | Firmware Features |  |  |  | 13. | 3. | 6 | 13 | 3 | 6
13.3.7 | CT secondary wiring phase and polarity measurements |  |  |  | 13. | 3. | 7 | 13 | 3 | 7
13.3.8 | Composite error measurements for nominal current |  |  |  | 13. | 3. | 8 | 13 | 3 | 8
13.3.9 | Ratio error and phase displacement measurement for no load and rated load |  |  |  | 13. | 3. | 9 | 13 | 3 | 9
13.3.10 | Measurement of excitation characteristics (voltage/current) |  |  |  | 13. | 3. | 10 | 13 | 3 | 10
13.3.11 | Knee point voltage from 1 V up to 4 kV |  |  |  | 13. | 3. | 11 | 13 | 3 | 11
13.3.12 | Knee point voltage from 0.1 V up to 40 kV |  |  |  | 13. | 3. | 12 | 13 | 3 | 12
13.3.13 | Automated calculation of knee points according to IEC and IEEE |  |  |  | 13. | 3. | 13 | 13 | 3 | 13
13.3.14 | Comparison of excitation curve to a reference curve |  |  |  | 13. | 3. | 14 | 13 | 3 | 14
13.3.15 | CT winding resistance measurement (primary and secondary) |  |  |  | 13. | 3. | 15 | 13 | 3 | 15
13.3.16 | CT accuracy measurements (ratio 1...25000) (ratio error and phase displacement depending on burden and current |  |  |  | 13. | 3. | 16 | 13 | 3 | 16
13.3.17 | IEC 61869 / 60044, or IEEE C57.13 classes ≥ 0.3 |  |  |  | 13. | 3. | 17 | 13 | 3 | 17
13.3.18 | IEC 61869 / 60044, or IEEE C57.13 classes ≥ 0.1 |  |  |  | 13. | 3. | 18 | 13 | 3 | 18
13.3.19 | Customized standards or local / national standards |  |  |  | 13. | 3. | 19 | 13 | 3 | 19
13.3.20 | Automatic assessment of CT performance according to the selected standard |  |  |  | 13. | 3. | 20 | 13 | 3 | 20
13.3.21 | Customization of assessment rules (for example implementation of national standards) |  |  |  | 13. | 3. | 21 | 13 | 3 | 21
13.3.22 | Composite error measurement for overcurrent conditions (ALF/ALFi, FS/FSi for IEC and Vb for IEEE |  |  |  | 13. | 3. | 22 | 13 | 3 | 22
13.3.23 | Determination of ALF and FS for IEC or Vb for IEEE |  |  |  | 13. | 3. | 23 | 13 | 3 | 23
13.3.24 | Secondary burden measurement |  |  |  | 13. | 3. | 24 | 13 | 3 | 24
13.3.25 | Nameplate guesser “function for CTs with unknown data |  |  |  | 13. | 3. | 25 | 13 | 3 | 25
13.3.26 | Simulation of measured data |  |  |  | 13. | 3. | 26 | 13 | 3 | 26
13.3.27 | Measurement of transient behavior of TPS, TPX, TPY and TPZ type CTs |  |  |  | 13. | 3. | 27 | 13 | 3 | 27
13.3.28 | Determination of the transient dimensioning factor (Ktd) |  |  |  | 13. | 3. | 28 | 13 | 3 | 28
13.3.29 | Considering Duty Cycles C-O / C-O-C-O, for example auto-reclosure system |  |  |  | 13. | 3. | 29 | 13 | 3 | 29
13.3.30 | Automatic demagnetization of the CT after the test |  |  |  | 13. | 3. | 30 | 13 | 3 | 30
13.3.31 | Remote control with CT Analyzer Suite software |  |  |  | 13. | 3. | 31 | 13 | 3 | 31
13.3.32 | Flexible manual current and voltage source (QuickTest) |  |  |  | 13. | 3. | 32 | 13 | 3 | 32
13.3.33 | Testing of CTs for line frequencies of 50 Hz |  |  |  | 13. | 3. | 33 | 13 | 3 | 33
13.3.34 | CT SB2 (switch box) for measurements of CTs with up to 6 taps, including accessories |  |  |  | 13. | 3. | 34 | 13 | 3 | 34
13.3.35 | CPOL3 for verifying the correct polarity of the secondary wiring along all connection points |  |  |  | 13. | 3. | 35 | 13 | 3 | 35
13.3.36 | RemAlyzer software for measuring the residual magnetism in CTs |  |  |  | 13. | 3. | 36 | 13 | 3 | 36
13.3.37 | Firmware Upgrades |  |  |  | 13. | 3. | 37 | 13 | 3 | 37
13.3.38 | Basic -> Standard Upgrades Basic to Standard Package P0006569 |  |  |  | 13. | 3. | 38 | 13 | 3 | 38
13.3.39 | Basic -> Advanced Upgrades Basic to Advanced Package P0006570 |  |  |  | 13. | 3. | 39 | 13 | 3 | 39
13.3.40 | Standard -> Advanced Upgrades Standard to Advanced Package P0006566 |  |  |  | 13. | 3. | 40 | 13 | 3 | 40
13.3.41 | IEEE Protection -> Advanced Upgrades IEEE Protection to Advanced Package P0006567 |  |  |  | 13. | 3. | 41 | 13 | 3 | 41
13.3.42 | Additional features |  |  |  | 13. | 3. | 42 | 13 | 3 | 42
13.3.43 | Simulate different burdens and currents |  |  |  | 13. | 3. | 43 | 13 | 3 | 43
13.3.44 | Analyze the effect of CT saturation |  |  |  | 13. | 3. | 44 | 13 | 3 | 44
13.3.45 | Measure VT ratio |  |  |  | 13. | 3. | 45 | 13 | 3 | 45
13.3.46 | Multimeter |  |  |  | 13. | 3. | 46 | 13 | 3 | 46
[8 empty] | 13 | 3 | 47 | tom rad
13.4. | OTDR |  |  |  | 13. | 4. |  | 13 | 4 | 48 | R2
[8 empty] | 13 | 4 | 49 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 4 | 50 | R3
13.4.1 | Dimensions | 270 (W) × 165 (H) × 61 (D) mm |  |  | 13. | 4. | 1 | 13 | 4 | 1
13.4.2 | Mass (without protection) | Without battery 1.6 kg, 1.9 kg including battery |  |  | 13. | 4. | 2 | 13 | 4 | 2
13.4.3 | Mass (with protection) | 2.6 kg including battery |  |  | 13. | 4. | 3 | 13 | 4 | 3
13.4.4 | Display | 8-inch touch screen TFT-Colour LCD |  |  | 13. | 4. | 4 | 13 | 4 | 4
13.4.5 | Interface | USB 1.1, Type A × 1 (memory), Type B × 1 (USB mass storage) |  |  | 13. | 4. | 5 | 13 | 4 | 5
13.4.6 | Data Storage | Internal memory: Not less than1 |  |  | 13. | 4. | 6 | 13 | 4 | 6
GB (50,000 traces),
External memory (USB): up to 32 GB
13.4.7 | Power Supply | 12 V(dc), 100 V(ac) to 240 V(ac), Allowable input voltage range: 90 V to 264 V, 50 Hz/60 Hz |  |  | 13. | 4. | 7 | 13 | 4 | 7
13.4.8 | Battery | Type: Lithium-ion |  |  | 13. | 4. | 8 | 13 | 4 | 8
Operating Time: 12 hours, Telcordia GR-196-CORE
Recharge Time: <5 hours (power off)
13.4.9 | Power Saving Functions | Backlight off: Disable/1 to 99 minutes |  |  | 13. | 4. | 9 | 13 | 4 | 9
Auto shutdown: Disable/1 to 99 minutes
13.4.10 | Power Consumption | 20W max (recharging), 4W standard (low backlight, sweep stopped) |  |  | 13. | 4. | 10 | 13 | 4 | 10
13.4.11 | Vertical Scale | 0.13, 0.33, 0.65, 1.3, 3.25, 6.5, 13 dB/div |  |  | 13. | 4. | 11 | 13 | 4 | 11
13.4.12 | IOR Setting | 1.300000 to 1.699999 (0.000001 steps) |  |  | 13. | 4. | 12 | 13 | 4 | 12
13.4.13 | Units | km, m, kft, ft, mi |  |  | 13. | 4. | 13 | 13 | 4 | 13
13.4.14 | Languages | User selectable (English a must) |  |  | 13. | 4. | 14 | 13 | 4 | 14
13.4.15 | Sampling Points∗2 | Normal: 5001, |  |  | 13. | 4. | 15 | 13 | 4 | 15
High density: 20001 or 25001, Very high density: 100,001 or 150,001
13.4.16 | Sampling Resolution | 0.05m to 60m |  |  | 13. | 4. | 16 | 13 | 4 | 16
13.4.17 | Reflectance Accuracy | Single mode: ±2 dB, multimode: ±4 dB |  |  | 13. | 4. | 17 | 13 | 4 | 17
13.4.18 | Distance Accuracy | 14- 15- ±1 m ±3 × measurement distance × 10–5 ± marker resolution (excluding IOR uncertainty) |  |  | 13. | 4. | 18 | 13 | 4 | 18
13.4.19 | Distance Range | Single mode: 0.5 to 300 km Multimode: 0.5 to 100 km |  |  | 13. | 4. | 19 | 13 | 4 | 19
13.4.20 | Testing Modes | 1-Fibre Visualizer: Provides end/break location, end to end loss, fibre length, easy graphical summary, PDF report, PDF viewer |  |  | 13. | 4. | 20 | 13 | 4 | 20
2-Standard OTDR: User selectable automatic or manual set-up
3-Construction OTDR: Automated, multi-wavelength testing
4-Light source: Stabilized Light source (CW, 270 Hz, 1 kHz, 2 kHz output)
5-Loss test set: Power meter and Light source
6- Connector Video Inspection Probe
7-Visual fault locator (optional): Visible red light for fibre identification and troubleshooting
13.4.21 | Fibre Event Analysis | A- Auto or manual operation, displayed in table format |  |  | 13. | 4. | 21 | 13 | 4 | 21
B- User defined PASS/FAIL thresholds:
- Reflective and non-reflective events: 0.01 to 9.99 dB (0.01 dB steps)
- Reflectance: –70.0 to –20.0 dB (0.1 dB steps)
- Fibre end/break: 1 to 99 dB (1 dB steps)
C- Number of detected events: up to 99
D -Macro bend detection
13.4.22 | OTDR Trace Format | Telcordia universal. SOR, issue 2 (SR-4731) |  |  | 13. | 4. | 22 | 13 | 4 | 22
13.4.23 | Other Functions |  |  |  | 13. | 4. | 23 | 13 | 4 | 23
13.4.24 | -Real time sweep∗3 | 0.15 sec |  |  | 13. | 4. | 24 | 13 | 4 | 24
13.4.25 | -Loss modes | 2-point loss, dB/km, 2-point LSA, splice loss, ORL |  |  | 13. | 4. | 25 | 13 | 4 | 25
13.4.26 | -Averaging modes | Timed (1 to 3600 sec.) |  |  | 13. | 4. | 26 | 13 | 4 | 26
13.4.27 | -Live fibre detect | Verifies presence of communication light in optical Fibre |  |  | 13. | 4. | 27 | 13 | 4 | 27
13.4.28 | -Connection check | Automatic check of OTDR to FUT connection quality |  |  | 13. | 4. | 28 | 13 | 4 | 28
13.4.29 | -Connectivity | Bluetooth, Wi-Fi and Ethernet |  |  | 13. | 4. | 29 | 13 | 4 | 29
13.4.30 | Environmental Conditions |  |  |  | 13. | 4. | 30 | 13 | 4 | 30
13.4.31 | -Operating temperature and humidity | –10° to +50°C, <80% (non-condensing) |  |  | 13. | 4. | 31 | 13 | 4 | 31
13.4.32 | -Storage temperature and humidity | –20° to +60°C, <80% (non-condensing) |  |  | 13. | 4. | 32 | 13 | 4 | 32
13.4.33 | -Vibration | Conforming to MIL-T-28800E Class 3 |  |  | 13. | 4. | 33 | 13 | 4 | 33
13.4.34 | -Dust proof | MIL-T-28800E (Dust Exposure) Class 2 |  |  | 13. | 4. | 34 | 13 | 4 | 34
13.4.35 | -Drip proof | IP51 (IEC 60529), JIS C 0920 TYPE I |  |  | 13. | 4. | 35 | 13 | 4 | 35
13.4.36 | -CE | EMC: EN61326-1, |  |  | 13. | 4. | 36 | 13 | 4 | 36
|  | EN61000-3-2 |  |  | 13. | 4. | 37 | 13 | 4 | 37
|  | LVD: EN61010-1 |  |  | 13. | 4. | 38 | 13 | 4 | 38
|  | RoHS: EN50581 |  |  | 13. | 4. | 39 | 13 | 4 | 39
[8 empty] | 13 | 4 | 40 | tom rad
13.5. | Earth Resistance Tester |  |  |  | 13. | 5. |  | 13 | 5 | 41 | R2
[8 empty] | 13 | 5 | 42 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 5 | 43 | R3
13.5.1 | Description | Megger DET2/3 Earth Resistance Tester suitable for testing of earth electrodes and measuring earth resistivity. |  |  | 13. | 5. | 1 | 13 | 5 | 1
13.5.2 | Earth Resistance Test Ranges | 0.01 to 19.99 |  | Ω | 13. | 5. | 2 | 13 | 5 | 2
|  | 0.1 to 199.9 |  | Ω
|  | 0.001k to 1.999k |  | Ω
|  | 0.01k to 19.99 k |  | Ω
13.5.3 | Accuracy (at 23°C) | ±7.5% ±3 digits (±10% at >0.5 ohms and ±0.05 ohm at <0.5 ohms for KEMA K85B requirements. |  | % | 13. | 5. | 3 | 13 | 5 | 3
13.5.4 | Maximum service error | ±7.5% ±3 digits (±10% at >0.5 ohms and ±0.05 ohm at <0.5 ohms for KEMA K85B requirements. |  | % | 13. | 5. | 4 | 13 | 5 | 4
13.5.5 | Display Type | 31⁄2 digit L.C.D. with Ω, kΩ and low battery voltage indicators. LEDs for high noise, high voltage probe resistance and high current loop resistance. |  |  | 13. | 5. | 5 | 13 | 5 | 5
13.5.6 | Test Frequency | Variable including 128 ±0,5 |  | Hz | 13. | 5. | 6 | 13 | 5 | 6
13.5.7 | Test voltage | Maximum 50 V peak |  | V | 13. | 5. | 7 | 13 | 5 | 7
| Test Current | 10 @ 20 Ω |  | mA ACrms
|  | 1 @ 200 Ω |  | mA ACrms
|  | 100 @ 2k Ω and 20kΩ |  | μA ACrms
13.5.8 | IP rating | IP54 |  |  | 13. | 5. | 8 | 13 | 5 | 8
13.5.9 | Battery type | 6 x 1.5 V (AA) IEC LR6 cells giving 600 typical 15 s tests at 20°C |  |  | 13. | 5. | 9 | 13 | 5 | 9
13.5.10 | Voltage Withstand | 250 between any two terminals |  | VAC | 13. | 5. | 10 | 13 | 5 | 10
13.5.11 | Flash Test | Tested to 2.3 |  | kVrms | 13. | 5. | 11 | 13 | 5 | 11
13.5.12 | Potential Circuit Interference | Voltages of 40 V pk to pk at 50 Hz, 60 Hz, 200 Hz or 162⁄3 Hz in the potential circuit must have a maximum effect of typically 1% on the reading in the 20 Ω to 2 kΩ ranges. If the ‘NOISE’ LED is not showing, the maximum error due to noise on these ranges shall not exceed 2%. In the 20 kΩ range this is reduced to 32V pk to pk. |  | V | 13. | 5. | 12 | 13 | 5 | 12
13.5.13 | Current Loop Interference | Voltages of 60 V pk to pk, 50 Hz, 60 Hz, 200 Hz or 162⁄3 Hz in the current loop must have a maximum effect of 1% on the reading with minimal current loop resistance. |  | mA | 13. | 5. | 13 | 13 | 5 | 13
13.5.14 | Dimensions | 243 x 161 x 70 |  | mm | 13. | 5. | 14 | 13 | 5 | 14
13.5.15 | Weight | 0.82 to 1.27 |  | kg | 13. | 5. | 15 | 13 | 5 | 15
13.5.16 | Maximum Current Loop Resistance | An additional error of typically 1% may be introduced for current loop resistances of: |  |  | 13. | 5. | 16 | 13 | 5 | 16
|  | 20 Ω |  | Ω
|  | 200 Ω |  | Ω
|  | 2k Ω and 20kΩ |  | Ω
13.5.17 | Environmental Conditions |  |  |  | 13. | 5. | 17 | 13 | 5 | 17
13.5.18 | Altitude above sea level | 1400 |  | m | 13. | 5. | 18 | 13 | 5 | 18
13.5.19 | Humidity | 90% relative humidity max. at 45°C |  | % | 13. | 5. | 19 | 13 | 5 | 19
13.5.20 | Operating Temperature | -20 to +45 |  | °C | 13. | 5. | 20 | 13 | 5 | 20
13.5.21 | Storage temperature range | -40 to +70 |  | °C | 13. | 5. | 21 | 13 | 5 | 21
13.5.22 | Temperature Coefficient | ±0,1% per °C over the temperature range -15 to +45 |  | %/°C | 13. | 5. | 22 | 13 | 5 | 22
13.5.23 | Other Requirements |  |  |  | 13. | 5. | 23 | 13 | 5 | 23
13.5.24 | Brochures in colour to be provided with the Bid | Yes |  |  | 13. | 5. | 24 | 13 | 5 | 24
13.5.25 | Display Backlight | Yes |  |  | 13. | 5. | 25 | 13 | 5 | 25
13.5.26 | Previous test report to the relevant standards to be provided with the bid | Yes |  |  | 13. | 5. | 26 | 13 | 5 | 26
13.5.27 | Quality assurance certificate to be provided with the Bid | Yes |  |  | 13. | 5. | 27 | 13 | 5 | 27
[8 empty] | 13 | 5 | 28 | tom rad
13.6. | Micro-Ohmmeter |  |  |  | 13. | 6. |  | 13 | 6 | 29 | R2
[8 empty] | 13 | 6 | 30 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 6 | 31 | R3
13.6.1 | Micro-Ohmmeter | Megger Micro-Ohmmeter or its equivalent |  |  | 13. | 6. | 1 | 13 | 6 | 1
13.6.2 | Measurement range | 0.1 μ – 1.999 |  | Ω | 13. | 6. | 2 | 13 | 6 | 2
13.6.3 | Resolution | 0.1 μ |  | Ω | 13. | 6. | 3 | 13 | 6 | 3
13.6.4 | Noise rejection | Differential 100 @ 50-60 Hz on test leads |  | mV | 13. | 6. | 4 | 13 | 6 | 4
13.6.5 | DC output | Smooth DC |  |  | 13. | 6. | 5 | 13 | 6 | 5
13.6.6 | IP rating | IP54 Lid open / IP65 Lid closed |  |  | 13. | 6. | 6 | 13 | 6 | 6
13.6.7 | Operating temperature range | -20 up to 50 |  | °C | 13. | 6. | 7 | 13 | 6 | 7
13.6.8 | Storage temperature range | -30 up to 70 |  | °C | 13. | 6. | 8 | 13 | 6 | 8
13.6.9 | Humidity | <85 R.H. non-condensing |  | % | 13. | 6. | 9 | 13 | 6 | 9
13.6.10 | Battery life | 200 single 100 A tests or up to 2x 10 minutes continuous 100 A output |  |  | 13. | 6. | 10 | 13 | 6 | 10
13.6.11 | Battery type | User replaceable Li-ion battery pack |  |  | 13. | 6. | 11 | 13 | 6 | 11
13.6.12 | Battery charge time | Full charge in 2.5 Hrs from flat |  | Hrs | 13. | 6. | 12 | 13 | 6 | 12
13.6.13 | Maximum output voltage | 2V (battery), 3V(AC) |  | V | 13. | 6. | 13 | 13 | 6 | 13
13.6.14 | EMC | IEC61326-1 |  |  | 13. | 6. | 14 | 13 | 6 | 14
13.6.15 | Safety | IEC61010 |  |  | 13. | 6. | 15 | 13 | 6 | 15
CAT IV 600 VAC / 500 VDC up to 2000 m
CAT IV 300 V up to 4000 m
13.6.16 | Accuracy at |  |  |  | 13. | 6. | 16 | 13 | 6 | 16
13.6.17 | 50 – 110 A / 0-100.00 m | Typical ± (0.2% + 0.2 μΩ) |  |  | 13. | 6. | 17 | 13 | 6 | 17
Max. ± (0.2% + 0.8 μΩ)
13.6.18 | 11 – 49 A / 10 μ – 100.00 m | Typical ± (0.2% + 0.5 μΩ) |  |  | 13. | 6. | 18 | 13 | 6 | 18
Max. ± (0.2% + 2.0 μΩ)
13.6.19 | 10:00:00 / 10 μ – 1000.0 m | Typical ± (0.2% + 1.0 μΩ) |  |  | 13. | 6. | 19 | 13 | 6 | 19
Max. ± (0.2% + 2.5 μΩ)
13.6.20 | Standard test leads, with separate Current & Potential leads | 5m Current Lead, 5m potential lead - CAT IV 600 |  |  | 13. | 6. | 20 | 13 | 6 | 20
13.6.21 | Test Modes | Auto, Continuous mode and Manual |  |  | 13. | 6. | 21 | 13 | 6 | 21
13.6.22 | Internal memory | Yes |  |  | 13. | 6. | 22 | 13 | 6 | 22
13.6.23 | -Storage with USB |  |  |  | 13. | 6. | 23 | 13 | 6 | 23
13.6.24 | -Download capability |  |  |  | 13. | 6. | 24 | 13 | 6 | 24
13.6.25 | Dual Ground TM capability with the DC clamp | Yes |  |  | 13. | 6. | 25 | 13 | 6 | 25
13.6.26 | Display clearly showing large digits for test results and visible in all light conditions | Yes |  |  | 13. | 6. | 26 | 13 | 6 | 26
13.6.27 | Back light display | Yes |  |  | 13. | 6. | 27 | 13 | 6 | 27
13.6.28 | Manufacturers Authorisation to be provided with bid | Yes |  |  | 13. | 6. | 28 | 13 | 6 | 28
13.6.29 | Calibration certificate to be provided on delivery | Yes |  |  | 13. | 6. | 29 | 13 | 6 | 29
13.6.30 | Brochure to be provided with bid | Yes |  |  | 13. | 6. | 30 | 13 | 6 | 30
13.6.31 | All accessories to be included | Yes |  |  | 13. | 6. | 31 | 13 | 6 | 31
13.6.32 | User Manual to be provided on delivery | Yes |  |  | 13. | 6. | 32 | 13 | 6 | 32
[8 empty] | 13 | 6 | 33 | tom rad
13.7. | Dielectric Oil Tester |  |  |  | 13. | 7. |  | 13 | 7 | 34 | R2
[8 empty] | 13 | 7 | 35 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 7 | 36 | R3
13.7.1 | Make | Megger OTS 100AF |  |  | 13. | 7. | 1 | 13 | 7 | 1
13.7.2 | Power Supply | 220 (50 Hz) |  | VAC | 13. | 7. | 2 | 13 | 7 | 2
13.7.3 | Power Consumption | max. 75 VA |  | VA | 13. | 7. | 3 | 13 | 7 | 3
13.7.4 | Output Voltage | 0…..100 |  | kVeff Symetric | 13. | 7. | 4 | 13 | 7 | 4
13.7.5 | For insulating liquids with tan delta values | < 4.5 or specific resistance ρ > 30MΩm |  |  | 13. | 7. | 5 | 13 | 7 | 5
13.7.6 | Voltage slew rate | 0.5 ….. 10 |  | kV/s | 13. | 7. | 6 | 13 | 7 | 6
13.7.7 | Switch off time | < 10 |  | µs | 13. | 7. | 7 | 13 | 7 | 7
13.7.8 | Voltage control | Real breakdown Monitoring |  |  | 13. | 7. | 8 | 13 | 7 | 8
13.7.9 | Internal measurement of the oil sample temperature | 0….99 |  | ͦC | 13. | 7. | 9 | 13 | 7 | 9
13.7.10 | Temperature resolution | 1 |  | ͦC | 13. | 7. | 10 | 13 | 7 | 10
13.7.11 | Display | LCD colour display |  |  | 13. | 7. | 11 | 13 | 7 | 11
13.7.12 | Voltage measurement Accuracy | 0 ….. 100 ± 1 |  | kV | 13. | 7. | 12 | 13 | 7 | 12
13.7.13 | Resolution | 0.1 |  | kV | 13. | 7. | 13 | 13 | 7 | 13
13.7.14 | Languages | English |  |  | 13. | 7. | 14 | 13 | 7 | 14
13.7.15 | Pre- programmed standards | ASTM D 1816-04 1mm, ASTM D 1816-04 2mm, ASTM D 877 / 87 PA, ASTM D 877 / 87 PB, BS EN 60156, CEI EN 60156, CSSR RVHP / 85, IEC 60156 / 1995 – 05, IRAM 2341 / 72, JIS C2101 / 78, PN 77 / E -04408, PA SEV EN 60156, UNE EN 60156, NF EN 60156, SABS EN 60156, VDE 0370 PART 5 / 96, AS1767.2.1, Individual measurement |  |  | 13. | 7. | 15 | 13 | 7 | 15
13.7.16 | Customer – specific programs | 10 |  |  | 13. | 7. | 16 | 13 | 7 | 16
13.7.17 | Interface | USB 2.0 |  |  | 13. | 7. | 17 | 13 | 7 | 17
13.7.18 | Printer | 2” Thermal paper printer (minimal) |  |  | 13. | 7. | 18 | 13 | 7 | 18
13.7.19 | Ambient temperature | -10 ……. 55 |  | ͦ C | 13. | 7. | 19 | 13 | 7 | 19
13.7.20 | Storage temperature | -20 ……+60 |  | ͦ C | 13. | 7. | 20 | 13 | 7 | 20
13.7.21 | Relative humidity | Non-condensing |  |  | 13. | 7. | 21 | 13 | 7 | 21
13.7.22 | Dimensions (w x H x D) | < 545 x 460 x 380 |  | mm | 13. | 7. | 22 | 13 | 7 | 22
13.7.23 | Weight | 40 |  | kg | 13. | 7. | 23 | 13 | 7 | 23
13.7.24 | Degree of protection | IP 32 |  |  | 13. | 7. | 24 | 13 | 7 | 24
13.7.25 | Designed and manufactured in acc. With the following Equipment standards | IEC 61010 – 1, EN 61010-1, VDE 0411 part 1 |  |  | 13. | 7. | 25 | 13 | 7 | 25
13.7.26 | Brochure | To be provided with bid |  |  | 13. | 7. | 26 | 13 | 7 | 26
13.7.27 | Delivery to Include |  |  |  | 13. | 7. | 27 | 13 | 7 | 27
13.7.28 | -Oil Tester | Yes |  |  | 13. | 7. | 28 | 13 | 7 | 28
13.7.29 | -Integrated printer | Yes |  |  | 13. | 7. | 29 | 13 | 7 | 29
13.7.30 | -Magnetic Oil Stirrer | Yes |  |  | 13. | 7. | 30 | 13 | 7 | 30
13.7.31 | -Lifting stick for magnetic stirrer | Yes |  |  | 13. | 7. | 31 | 13 | 7 | 31
13.7.32 | -Setting gauges | Yes |  |  | 13. | 7. | 32 | 13 | 7 | 32
13.7.33 | -Test vessel | Yes |  |  | 13. | 7. | 33 | 13 | 7 | 33
13.7.34 | -Mains connection cable | Yes |  |  | 13. | 7. | 34 | 13 | 7 | 34
13.7.35 | -User manual | Yes |  |  | 13. | 7. | 35 | 13 | 7 | 35
13.7.36 | -Rugged Transport case | Yes |  |  | 13. | 7. | 36 | 13 | 7 | 36
13.7.37 | -Paper roll for printer | Yes |  |  | 13. | 7. | 37 | 13 | 7 | 37
13.7.38 | -Ring nut wrench for disassembling the test vessel | Yes |  |  | 13. | 7. | 38 | 13 | 7 | 38
[8 empty] | 13 | 7 | 39 | tom rad
13.8. | SF6 Gas Leak Detector |  |  |  | 13. | 8. |  | 13 | 8 | 40 | R2
[8 empty] | 13 | 8 | 41 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 8 | 42 | R3
13.8.1 | Measuring Principle | Ion - Vacuum - Principle |  |  | 13. | 8. | 1 | 13 | 8 | 1
13.8.2 | Power Supply | 3V DC, two “C” cell Alkaline batteries |  |  | 13. | 8. | 2 | 13 | 8 | 2
13.8.3 | Ultimate Sensitivity | 14 |  | gm/year | 13. | 8. | 3 | 13 | 8 | 3
13.8.4 | Operating Temperature | 0 - 52 |  | °C | 13. | 8. | 4 | 13 | 8 | 4
13.8.5 | Battery Life Approximately | 30 |  | Hour | 13. | 8. | 5 | 13 | 8 | 5
13.8.6 | Duty Cycle | Continuous, no limitation |  |  | 13. | 8. | 6 | 13 | 8 | 6
13.8.7 | Response Time | Instantaneously |  |  | 13. | 8. | 7 | 13 | 8 | 7
13.8.8 | Reset Time | 1 |  | s | 13. | 8. | 8 | 13 | 8 | 8
13.8.9 | Warm-Up Time Approximately | 2 |  | s | 13. | 8. | 9 | 13 | 8 | 9
[8 empty] | 13 | 8 | 10 | tom rad
13.9. | SF6 Gas Filling kits |  |  |  | 13. | 9. |  | 13 | 9 | 11 | R2
[8 empty] | 13 | 9 | 12 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 9 | 13 | R3
13.9.1 | High-Quality Hoses: They should have proper fittings on each end to create leak-proof connections with the gas cylinder and the circuit breaker. | Yes |  |  | 13. | 9. | 1 | 13 | 9 | 1
13.9.2 | Pressure Gauges: These are instruments with dials or displays that show the pressure of the gas inside the hoses or circuit breakers. | Yes |  |  | 13. | 9. | 2 | 13 | 9 | 2
13.9.3 | Valves: These are controllable openings that regulate the flow of gas within the filling system. | Yes |  |  | 13. | 9. | 3 | 13 | 9 | 3
13.9.4 | Safety Devices: |  |  |  | 13. | 9. | 4 | 13 | 9 | 4
13.9.5 | o Pressure Relief Valves: These are automatic safety mechanisms that release excess pressure if it builds up beyond a safe limit. This prevents damage to equipment and potential injury. | Yes |  |  | 13. | 9. | 5 | 13 | 9 | 5
13.9.6 | o Emergency Shut-Off Mechanisms: These are manual or automatic systems that can quickly stop the flow of gas in case of an emergency. This can be a button on the control panel or a valve that can be closed manually. | Yes |  |  | 13. | 9. | 6 | 13 | 9 | 6
13.9.7 | Clear Labeling and Instructions: The kit should have clear labels on all components, indicating their function and proper usage. Additionally, the kit should come with detailed instructions that outline the safe setup and operation of the entire filling system. | Yes |  |  | 13. | 9. | 7 | 13 | 9 | 7
[8 empty] | 13 | 9 | 8 | tom rad
13.10. | Secondary Injection Test Set |  |  |  | 13. | 10. |  | 13 | 10 | 9 | R2
[8 empty] | 13 | 10 | 10 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 10 | 11 | R3
13.10.1 | Make | CMC500 (356) |  |  | 13. | 10. | 1 | 13 | 10 | 1
13.10.2 | Environmental conditions |  |  |  | 13. | 10. | 2 | 13 | 10 | 2
13.10.3 | Temperature |  |  |  | 13. | 10. | 3 | 13 | 10 | 3
13.10.4 | Operating temperature | –25 … +50 |  | °C | 13. | 10. | 4 | 13 | 10 | 4
13.10.5 | Storage temperature | –40 … +70 |  | °C | 13. | 10. | 5 | 13 | 10 | 5
13.10.6 | Operating altitude, max | 2000 |  | m | 13. | 10. | 6 | 13 | 10 | 6
13.10.7 | Storage altitude, max | 15000 |  | m | 13. | 10. | 7 | 13 | 10 | 7
13.10.8 | Humidity | 5 … 95 |  | %RH | 13. | 10. | 8 | 13 | 10 | 8
13.10.9 | Shock | 15 g @ 11 ms |  |  | 13. | 10. | 9 | 13 | 10 | 9
30 g @ 6 ms
13.10.10 | Vibration (not in operation) | 10 … 500 Hz, 1 g |  |  | 13. | 10. | 10 | 13 | 10 | 10
20 sweep cycles
13.10.11 | Vibration (in operation) | 10 … 500 Hz, 0.5 g, |  |  | 13. | 10. | 11 | 13 | 10 | 11
13.10.12 |  | 1 sweep cycle |  |  | 13. | 10. | 12 | 13 | 10 | 12
13.10.13 | Drop | 10 |  | cm | 13. | 10. | 13 | 13 | 10 | 13
13.10.14 | Standards |  |  |  | 13. | 10. | 14 | 13 | 10 | 14
13.10.15 | -Europe | EN 60068-2-1, EN 60068-2-2, EN 60068-2-6, EN 60068-2-14, EN 60068-2-27, EN 60068-2-30, EN 60068-2-31, EN 60068-2-78 |  |  | 13. | 10. | 15 | 13 | 10 | 15
13.10.16 | -International | IEC 60068-2-1, IEC 60068-2-2, IEC 60068-2-6, IEC 60068-2-14, IEC 60068-2-27, IEC 60068-2-30, IEC 60068-2-31, IEC 60068-2-7 |  |  | 13. | 10. | 16 | 13 | 10 | 16
13.10.17 | Mechanical data |  |  |  | 13. | 10. | 17 | 13 | 10 | 17
13.10.18 | Weight | 15.6 |  | kg | 13. | 10. | 18 | 13 | 10 | 18
13.10.19 | Dimensions without handles (W × H × D) | 364 × 263 × 225 |  | mm | 13. | 10. | 19 | 13 | 10 | 19
13.10.20 | Protection class | IP20 |  |  | 13. | 10. | 20 | 13 | 10 | 20
13.10.21 | Standards |  |  |  | 13. | 10. | 21 | 13 | 10 | 21
13.10.22 | -International | IEC 60068-2-6, 10 Hz–500 Hz, 1 g/20 sweeps not operating, 10 Hz–500 Hz, 0.5 g/20 sweeps operating IEC 60068-2-27, 15g/11 ms, 30 g/6 ms, IEC 60068-2-31, 0.1 m, IEC 60721-3-7 (7M2) |  |  | 13. | 10. | 22 | 13 | 10 | 22
13.10.23 | Electromagnetic compatibility (EMC |  |  |  | 13. | 10. | 23 | 13 | 10 | 23
13.10.24 | Emission |  |  |  | 13. | 10. | 24 | 13 | 10 | 24
13.10.25 | -International | IEC 61326-1, IEC 55032 (Class A), IEC 61000-3-2/3 |  |  | 13. | 10. | 25 | 13 | 10 | 25
13.10.26 | Immunity |  |  |  | 13. | 10. | 26 | 13 | 10 | 26
13.10.27 | -International | IEC 61326-1, IEC 61000-4-2/3/4/5/6/8/11, IEC 61000-6-5, installation category II, IEC 61326-3-1 |  |  | 13. | 10. | 27 | 13 | 10 | 27
13.10.28 | Safety standards |  |  |  | 13. | 10. | 28 | 13 | 10 | 28
13.10.29 | Certified standards |  |  |  | 13. | 10. | 29 | 13 | 10 | 29
13.10.30 | -International | IEC 61010-1, IEC 61010-2-030, ISO 13849-1 |  |  | 13. | 10. | 30 | 13 | 10 | 30
13.10.31 | Electrical insulation |  |  |  | 13. | 10. | 31 | 13 | 10 | 31
13.10.32 | Protection | class I |  |  | 13. | 10. | 32 | 13 | 10 | 32
13.10.33 | Power supply |  |  |  | 13. | 10. | 33 | 13 | 10 | 33
13.10.34 | Connection | C14 connector according to EN IEC/IEC 60320-1 |  |  | 13. | 10. | 34 | 13 | 10 | 34
13.10.35 | Voltage (single phase) |  |  |  | 13. | 10. | 35 | 13 | 10 | 35
13.10.36 | -Nominal voltage | 100 … 240 V (± 10 %) |  | V | 13. | 10. | 36 | 13 | 10 | 36
13.10.37 | -Operational range | 85 … 264 V |  | V | 13. | 10. | 37 | 13 | 10 | 37
13.10.38 | Nominal current | 10 ... 15 A (configurable, see Power supply plug types) |  |  | 13. | 10. | 38 | 13 | 10 | 38
13.10.39 | Frequence | 50/60 Hz |  |  | 13. | 10. | 39 | 13 | 10 | 39
13.10.40 |  | 47 … 63 Hz |  |  | 13. | 10. | 40 | 13 | 10 | 40
13.10.41 | Overvoltage category | III |  |  | 13. | 10. | 41 | 13 | 10 | 41
[8 empty] | 13 | 10 | 42 | tom rad
13.11. | Tool Box |  |  |  | 13. | 11. |  | 13 | 11 | 43 | R2
[8 empty] | 13 | 11 | 44 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 11 | 45 | R3
13.11.1 | ½” Socket 8mm |  |  |  | 13. | 11. | 1 | 13 | 11 | 1
13.11.2 | ½” Socket 9mm |  |  |  | 13. | 11. | 2 | 13 | 11 | 2
13.11.3 | ½” Socket 10mm |  |  |  | 13. | 11. | 3 | 13 | 11 | 3
13.11.4 | ½” Socket 11mm |  |  |  | 13. | 11. | 4 | 13 | 11 | 4
13.11.5 | ½” Socket 12mm |  |  |  | 13. | 11. | 5 | 13 | 11 | 5
13.11.6 | ½” Socket 13mm |  |  |  | 13. | 11. | 6 | 13 | 11 | 6
13.11.7 | ½” Socket 14mm |  |  |  | 13. | 11. | 7 | 13 | 11 | 7
13.11.8 | ½” Socket 15mm |  |  |  | 13. | 11. | 8 | 13 | 11 | 8
13.11.9 | ½” Socket 16mm |  |  |  | 13. | 11. | 9 | 13 | 11 | 9
13.11.10 | ½” Socket 17mm |  |  |  | 13. | 11. | 10 | 13 | 11 | 10
13.11.11 | ½” Socket 18mm |  |  |  | 13. | 11. | 11 | 13 | 11 | 11
13.11.12 | ½” Socket 19mm |  |  |  | 13. | 11. | 12 | 13 | 11 | 12
13.11.13 | ½” Socket 20mm |  |  |  | 13. | 11. | 13 | 13 | 11 | 13
13.11.14 | ½” Socket 21mm |  |  |  | 13. | 11. | 14 | 13 | 11 | 14
13.11.15 | ½” Socket 22mm |  |  |  | 13. | 11. | 15 | 13 | 11 | 15
13.11.16 | ½” Socket 24mm |  |  |  | 13. | 11. | 16 | 13 | 11 | 16
13.11.17 | ½” Rachet |  |  |  | 13. | 11. | 17 | 13 | 11 | 17
13.11.18 | ½” Extension 125mm |  |  |  | 13. | 11. | 18 | 13 | 11 | 18
13.11.19 | Club Hammer |  |  |  | 13. | 11. | 19 | 13 | 11 | 19
13.11.20 | Hammer |  |  |  | 13. | 11. | 20 | 13 | 11 | 20
13.11.21 | Pliers 180mm |  |  |  | 13. | 11. | 21 | 13 | 11 | 21
13.11.22 | Tape Measure 5mtrs |  |  |  | 13. | 11. | 22 | 13 | 11 | 22
13.11.23 | Hacksaw |  |  |  | 13. | 11. | 23 | 13 | 11 | 23
13.11.24 | Cold Chisels (Set) |  |  |  | 13. | 11. | 24 | 13 | 11 | 24
13.11.25 | Water Pump Pliers |  |  |  | 13. | 11. | 25 | 13 | 11 | 25
13.11.26 | Shifting Spanners Heavy 150mm |  |  |  | 13. | 11. | 26 | 13 | 11 | 26
13.11.27 | Utility Knife |  |  |  | 13. | 11. | 27 | 13 | 11 | 27
13.11.28 | Combination Spanner 6mm |  |  |  | 13. | 11. | 28 | 13 | 11 | 28
13.11.29 | Combination Spanner 8mm |  |  |  | 13. | 11. | 29 | 13 | 11 | 29
13.11.30 | Combination Spanner 9mm |  |  |  | 13. | 11. | 30 | 13 | 11 | 30
13.11.31 | Combination Spanner 10m |  |  |  | 13. | 11. | 31 | 13 | 11 | 31
13.11.32 | Combination Spanner 11mm |  |  |  | 13. | 11. | 32 | 13 | 11 | 32
13.11.33 | Combination Spanner 12mm |  |  |  | 13. | 11. | 33 | 13 | 11 | 33
13.11.34 | Combination Spanner 13mm |  |  |  | 13. | 11. | 34 | 13 | 11 | 34
13.11.35 | Combination Spanner 14mm |  |  |  | 13. | 11. | 35 | 13 | 11 | 35
13.11.36 | Combination Spanner 15mm |  |  |  | 13. | 11. | 36 | 13 | 11 | 36
13.11.37 | Combination Spanner 16mm |  |  |  | 13. | 11. | 37 | 13 | 11 | 37
13.11.38 | Combination Spanner 17mm |  |  |  | 13. | 11. | 38 | 13 | 11 | 38
13.11.39 | Combination Spanner 18mm |  |  |  | 13. | 11. | 39 | 13 | 11 | 39
13.11.40 | Combination Spanner 19mm |  |  |  | 13. | 11. | 40 | 13 | 11 | 40
13.11.41 | Combination Spanner 20mm |  |  |  | 13. | 11. | 41 | 13 | 11 | 41
13.11.42 | Combination Spanner 21mm |  |  |  | 13. | 11. | 42 | 13 | 11 | 42
13.11.43 | Combination Spanner 22mm |  |  |  | 13. | 11. | 43 | 13 | 11 | 43
13.11.44 | Combination Spanner 23mm |  |  |  | 13. | 11. | 44 | 13 | 11 | 44
13.11.45 | Combination Spanner 24mm |  |  |  | 13. | 11. | 45 | 13 | 11 | 45
13.11.46 | Long Nose Pliers 160mm |  |  |  | 13. | 11. | 46 | 13 | 11 | 46
13.11.47 | Hex Key – Set |  |  |  | 13. | 11. | 47 | 13 | 11 | 47
13.11.48 | Diagonal Cutter |  |  |  | 13. | 11. | 48 | 13 | 11 | 48
13.11.49 | Drive Pin Punch (Set) |  |  |  | 13. | 11. | 49 | 13 | 11 | 49
13.11.50 | Screw Driver (Set) |  |  |  | 13. | 11. | 50 | 13 | 11 | 50
[8 empty] | 13 | 11 | 51 | tom rad
13.12. | Disturbance fault recorder |  |  |  | 13. | 12. |  | 13 | 12 | 52 | R2
[8 empty] | 13 | 12 | 53 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 12 | 54 | R3
13.12.1 | Maker’s name | Bidder to state |  |  | 13. | 12. | 1 | 13 | 12 | 1
13.12.2 | Maker’s type and reference | Bidder to state |  |  | 13. | 12. | 2 | 13 | 12 | 2
13.12.3 | Country of origin | Bidder to state |  |  | 13. | 12. | 3 | 13 | 12 | 3
13.12.4 | Description | Fault Recorder |  |  | 13. | 12. | 4 | 13 | 12 | 4
13.12.5 | Type test | Authority, year, Doc.no |  |  | 13. | 12. | 5 | 13 | 12 | 5
13.12.6 | Standards | IEC 60794-1-1, 60794-1-2, 60974-4-10, 60793-2-50 |  |  | 13. | 12. | 6 | 13 | 12 | 6
13.12.7 | GENERAL - ELECTRICAL |  |  |  | 13. | 12. | 7 | 13 | 12 | 7
13.12.8 | Channel capacity | 64 analog inputs (voltage, current, DC transducers) |  |  | 13. | 12. | 8 | 13 | 12 | 8
12 high-speed analog inputs for Traveling Wave Fault Location
256 opto-isolated digital inputs; Up to 8 fiber-optic links to connect to remote acquisition modules
13.12.9 | Acquisition system | 16-bit opto-isolated analog-to-digital converters, independent for each channel (50 Hz channels) |  |  | 13. | 12. | 9 | 13 | 12 | 9
256 points-per-cycle sampling rates (50 Hz channels)
Frequency response of DC to 3.0 kHz
13.12.10 | GOOSE messaging | 320 binary inputs in 61850-8-1 GOOSE messages |  |  | 13. | 12. | 10 | 13 | 12 | 10
13.12.11 | Sampled Values | Reading and recording up to 8 streams of Sampled Values IEC 61850-9-2LE simultaneously with up to 64 analog conventional channels |  |  | 13. | 12. | 11 | 13 | 12 | 11
Monitoring and recording DC measurement from IEC 61850-9-2LE Sampled Values
13.12.12 | Hard Drive | 60 GB SSD (solid-state drive) capacity. 33,5 GB reserved for recordings; |  |  | 13. | 12. | 12 | 13 | 12 | 12
13.12.13 | Trigger Waveform | Trigger waveform recorder at 256, 128, or 64 samples/cycle; |  |  | 13. | 12. | 13 | 13 | 12 | 13
13.12.14 | Waveform recording | Continuous waveform recorder at 16 samples/cycle; |  |  | 13. | 12. | 14 | 13 | 12 | 14
13.12.15 | Disturbance recorder | Continuous disturbance recorder and triggered disturbance recorder at 1 sample/cycle |  |  | 13. | 12. | 15 | 13 | 12 | 15
13.12.16 | Time synchronization | IRIGB-004 and SNTP/NTP (version 2, 3 or 4) time synchronization |  |  | 13. | 12. | 16 | 13 | 12 | 16
13.12.17 | Travelling waves | Automatic Traveling Wave Fault Location functionality with voltage from VT |  |  | 13. | 12. | 17 | 13 | 12 | 17
13.12.18 |  | MODBUS and DNP3 interface for SCADA integration |  |  | 13. | 12. | 18 | 13 | 12 | 18
13.12.19 | Synchrophasor measurement | Synchrophasor measurement and transmission as per IEEE C37.118.1a-2014 and IEEE C37.118.2-2011 |  |  | 13. | 12. | 19 | 13 | 12 | 19
13.12.20 | Trnsmission of synchrophasors | Capable of transmitting synchrophasors (IEEE C37.118.1a-2014 and IEEE C37.118.2-2011) from Sampled Values IEC 61850-9-2LE and conventional analog channels measurements simultaneously; |  |  | 13. | 12. | 20 | 13 | 12 | 20
13.12.21 | Historical Values | Historical average at aggregation intervals of 1 or 10 minutes. |  |  | 13. | 12. | 21 | 13 | 12 | 21
13.12.22 | Harmonic measurement | Measurement and recording of harmonics up to the 50th order as per IEC 61000-4-7 |  |  | 13. | 12. | 22 | 13 | 12 | 22
13.12.23 | Cross trigger | Cross-trigger using standard network connection |  |  | 13. | 12. | 23 | 13 | 12 | 23
13.12.24 | MECHANICAL SPECIFICATIONS |  |  |  | 13. | 12. | 24 | 13 | 12 | 24
13.12.25 | Design | The device shall have a modular design i.e. where the entire DFR scheme has one common set of processing and control cards/units and where analog and binary data input cards/units (acquisition units) can be added as separate modules to expand the number of analog and binary inputs that can be monitored |  |  | 13. | 12. | 25 | 13 | 12 | 25
The processing unit shall be presented in a 3U case height format (133,55 mm), and the acquisition units shall be presented in a 5U case height format (222,0 mm).
The processing unit shall be housed in a 19’’ case width (482,6 mm), and the acquisition units shall be housed in a ½ 19’’ (222,0 mm).
The solution design shall be fan-less and have no rotating parts
13.12.26 | Processing Unit | The degree of protection offered shall be as per IEC 60529: 2002: |  |  | 13. | 12. | 26 | 13 | 12 | 26
• IP 40 Protection for the front panel;
• IP 20 Protection for the sides and rear of the case;
• The device shall be housed in a metallic case wrapper;
13.12.27 | Acquisition system | • IP 54 Protection for the front panel; |  |  | 13. | 12. | 27 | 13 | 12 | 27
• IP 20 Protection for the sides and rear of the case;
• IP 10 Protection for the sides of the case;
• The device shall be housed in a metallic case wrapper
13.12.28 | General input/ Output | CT terminals shall be ring-lug screw type for security and robustness |  |  | 13. | 12. | 28 | 13 | 12 | 28
13.12.29 | Communication and alarming | • Two 10/100BaseT electrical Ethernet interfaces for communication, configuration, download and GOOSE reading |  |  | 13. | 12. | 29 | 13 | 12 | 29
• Two embedded electrical-to-optical Ethernet converters with ST connectors
• RS232 serial port for modem connection;
• One RJ45 Ethernet interface for Process Bus (IEC 61850-9-2LE Sampled Values) connection.
• Local HMI interface on the front panel for monitoring
• 4 dry-contact relays for remote signaling of alarms;
• Fax and e-mail message after detection of a trigger. The fax can be sent to two different destinations and the e-mail to four different destinations.
13.12.30 | Power Supply Specification | • Nominal range: 100-250 V dc, 110-240 V ac |  |  | 13. | 12. | 30 | 13 | 12 | 30
• Maximum voltage range: 80-300 V dc, 88-264 V ac
• Frequency: 50 Hz, ± 3 Hz
13.12.31 | Enviromental Conditions - Ambient Temperature Range | Operating temperature range: -40°C to +55°C (or -40°F to +131°F) |  |  | 13. | 12. | 31 | 13 | 12 | 31
Tested as per IEC 60068-2-1: -40°C operation (16 hours)
Tested as per IEC 60068-2-2: +85°C operation (16 hours)
13.12.32 | Standards Compliance / Type Tests | EMC Compliance; As a minimum, the equipment shall use the IEC 60255-26 standard to establish EMC conformity |  |  | 13. | 12. | 32 | 13 | 12 | 32
13.12.33 | Product Safety | As minimum, the equipment shall use the IEC 61010-1 standard to ensure product safety. The device shall meet the IEC 60255-5, ensuring insulation resistance greater than 100MΩ when applying 500 Vdc. |  |  | 13. | 12. | 33 | 13 | 12 | 33
13.12.34 | Mechanical Robustness | The device shall comply with vibration, shock and seismic tests as described in IEC 60255-21 standard. |  |  | 13. | 12. | 34 | 13 | 12 | 34
13.12.35 | Vibration Test | As per IEC 60255-21-1 Class 2 |  |  | 13. | 12. | 35 | 13 | 12 | 35
13.12.36 | Shock | As per IEC 60255-21-2 Class 1 |  |  | 13. | 12. | 36 | 13 | 12 | 36
13.12.37 | Sesmic tests | As per IEC 60255-21-3 Class 2 |  |  | 13. | 12. | 37 | 13 | 12 | 37
[8 empty] | 13 | 12 | 38 | tom rad
13.13. | Vacuum Pump for Transformer Drying |  |  |  | 13. | 13. |  | 13 | 13 | 39 | R2
[8 empty] | 13 | 13 | 40 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 13 | 41 | R3
13.13.1 | Nominal suction capacity | 3500 |  | m3/hr | 13. | 13. | 1 | 13 | 13 | 1
13.13.2 | Ultimate vacuum pressure | 10 |  | mbar | 13. | 13. | 2 | 13 | 13 | 2
13.13.3 | Input power | 23 |  | kW | 13. | 13. | 3 | 13 | 13 | 3
13.13.4 | Cooling system | Air Natural |  |  | 13. | 13. | 4 | 13 | 13 | 4
13.13.5 | Operating temperature | 90 |  | oC | 13. | 13. | 5 | 13 | 13 | 5
13.13.6 | Connections | Intake: 2” |  | Inch | 13. | 13. | 6 | 13 | 13 | 6
|  | Outlet: 1.5” |  | Inch | 13. | 13. | 7 | 13 | 13 | 7
13.13.8 | Noise | 72 |  | dB (A) | 13. | 13. | 8 | 13 | 13 | 8
13.13.9 | Accessories | Vacuum Hoses to be provided with Vacuum Plant (2 x 20m) |  |  | 13. | 13. | 9 | 13 | 13 | 9
Gauges to be provided
13.13.10 | Outline dimensions (LxWxH) and Drawing | Bidder to indicate |  |  | 13. | 13. | 10 | 13 | 13 | 10
13.13.11 | Electrical supply | 3 Ph.,400V, AC, 50Hz |  |  | 13. | 13. | 11 | 13 | 13 | 11
[8 empty] | 13 | 13 | 12 | tom rad
13.14. | Insulation Resistance Tester 15000V |  |  |  | 13. | 14. |  | 13 | 14 | 13 | R2
[8 empty] | 13 | 14 | 14 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 14 | 15 | R3
13.14.1 | Description | Megger MIT 1025 Insulation Resistance Tester able to perform insulation resistance tests up to 15 kV |  |  | 13. | 14. | 1 | 13 | 14 | 1
13.14.2 | Maximum output voltage | 15000 |  | V | 13. | 14. | 2 | 13 | 14 | 2
13.14.3 | Max. resistance | 20 |  | TΩ | 13. | 14. | 3 | 13 | 14 | 3
13.14.4 | Accuracy from 1 MΩ to ≤ 2 TΩ | ±5 |  | % | 13. | 14. | 4 | 13 | 14 | 4
13.14.5 | Accuracy from 1 MΩ to to 20 TΩ | ±20 |  | % | 13. | 14. | 5 | 13 | 14 | 5
13.14.6 | Test voltages | 500, 1000, 2500, 5000, 10000 |  | V | 13. | 14. | 6 | 13 | 14 | 6
13.14.7 | Industry standard tests | Auto IR, PI, DAR, SV, and DD |  |  | 13. | 14. | 7 | 13 | 14 | 7
13.14.8 | AC voltage range | 90 - 264 |  | V | 13. | 14. | 8 | 13 | 14 | 8
13.14.9 | Frequency range | 47 - 63 |  | Hz | 13. | 14. | 9 | 13 | 14 | 9
13.14.10 | Short circuit/charge current | 3 |  | mA | 13. | 14. | 10 | 13 | 14 | 10
13.14.11 | Maximum noise rejection | 3 |  | mA | 13. | 14. | 11 | 13 | 14 | 11
13.14.12 | IP rating Lid open | IP40 |  |  | 13. | 14. | 12 | 13 | 14 | 12
13.14.13 | IP rating Lid closed | IP65 |  |  | 13. | 14. | 13 | 13 | 14 | 13
13.14.14 | Storage temperature range | -25 up to 65 |  | °C | 13. | 14. | 14 | 13 | 14 | 14
13.14.15 | Battery life single charge | 4.5 hours (typical) continuous testing at 10 kV with a 100 MΩ load |  |  | 13. | 14. | 15 | 13 | 14 | 15
13.14.16 | Battery type | Rechargeable Li-ion battery |  |  | 13. | 14. | 16 | 13 | 14 | 16
13.14.17 | Battery charge time | Full charge in 2.5 Hours from dead |  |  | 13. | 14. | 17 | 13 | 14 | 17
13.14.18 | Display type | Large character digital display |  |  | 13. | 14. | 18 | 13 | 14 | 18
13.14.19 | Memory storage | Provides memory storage for test results up to 200 records retrievable |  |  | 13. | 14. | 19 | 13 | 14 | 19
13.14.20 | Discharge | Automatic discharge after test |  |  | 13. | 14. | 20 | 13 | 14 | 20
13.14.21 | Detection of External Voltage | Visual or audible warning if external voltage is present |  |  | 13. | 14. | 21 | 13 | 14 | 21
13.14.22 | Data transfer via USB interface | Required |  |  | 13. | 14. | 22 | 13 | 14 | 22
13.14.23 | Display Backlight | Required |  |  | 13. | 14. | 23 | 13 | 14 | 23
13.14.24 | Easy rotary switch operation | Required |  |  | 13. | 14. | 24 | 13 | 14 | 24
13.14.25 | Voltage output measurement | Required |  |  | 13. | 14. | 25 | 13 | 14 | 25
13.14.26 | Anti-skid/vibration absorbing | Required |  |  | 13. | 14. | 26 | 13 | 14 | 26
13.14.27 | Interference rejection | 2 mA rms at 200 V and above |  |  | 13. | 14. | 27 | 13 | 14 | 27
13.14.28 | Guard Terminal | 2 % error guarding 500kΩ leakage with 100MΩ load |  |  | 13. | 14. | 28 | 13 | 14 | 28
13.14.29 | Environmental Conditions |  |  |  | 13. | 14. | 29 | 13 | 14 | 29
13.14.30 | Altitude above sea level | 1400 |  | m | 13. | 14. | 30 | 13 | 14 | 30
13.14.31 | Humidity | 85 |  | % | 13. | 14. | 31 | 13 | 14 | 31
13.14.32 | Operating Temperature | -1 to 45 |  | °C | 13. | 14. | 32 | 13 | 14 | 32
13.14.33 | Other Requirements |  |  |  | 13. | 14. | 33 | 13 | 14 | 33
13.14.34 | Brochures in colour to be provided with the bid | Required |  |  | 13. | 14. | 34 | 13 | 14 | 34
13.14.35 | Previous test report to the relevant standards to be provided with the bid | Required |  |  | 13. | 14. | 35 | 13 | 14 | 35
13.14.36 | CAT IV 600V certification to be provided with the bid | Required |  |  | 13. | 14. | 36 | 13 | 14 | 36
13.14.37 | Quality assurance certificate to be provided with the bid | Required |  |  | 13. | 14. | 37 | 13 | 14 | 37
13.14.38 | Calibration certificate to be provided on delivery | Required |  |  | 13. | 14. | 38 | 13 | 14 | 38
13.14.39 | Routine test results to be provided on delivery | Required |  |  | 13. | 14. | 39 | 13 | 14 | 39
13.14.37 | Applicable standard (s) | IEC 61326-1, IEC 61010 |  |  | 13. | 14. | 37 | 13 | 14 | 37
[8 empty] | 13 | 14 | 38 | tom rad
13.15. | OMICRON CPC100 |  |  |  | 13. | 15. |  | 13 | 15 | 39 | R2
[8 empty] | 13 | 15 | 40 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 13 | 15 | 41 | R3
13.15.1 | CURRENT TRANSFORMER TESTING |  |  |  | 13. | 15. | 1 | 13 | 15 | 1
13.15.2 | CT ratio (with burden) up to 800 A or 2 000 A with CP CB2, 5 kVA output power |  |  |  | 13. | 15. | 2 | 13 | 15 | 2
13.15.3 | CT burden up to 6 AAC ¦ secondary |  |  |  | 13. | 15. | 3 | 13 | 15 | 3
13.15.4 | CT excitation curve (knee point) up to 2 kVAC |  |  |  | 13. | 15. | 4 | 13 | 15 | 4
13.15.5 | Polarity check with CPOL3 up to 800 A or up to 2 000 A with CP CB2 |  |  |  | 13. | 15. | 5 | 13 | 15 | 5
13.15.6 | Accuracy limiting factor (ALF) test |  |  |  | 13. | 15. | 6 | 13 | 15 | 6
13.15.7 | CT ratio with voltage up to 130 VAC ¦ bushing CTs |  |  |  | 13. | 15. | 7 | 13 | 15 | 7
13.15.8 | CT winding resistance up to 6 ADC |  |  |  | 13. | 15. | 8 | 13 | 15 | 8
13.15.9 | CT demagnetization and remanence |  |  |  | 13. | 15. | 9 | 13 | 15 | 9
13.15.10 | CT voltage withstand test up to 2 kVAC |  |  |  | 13. | 15. | 10 | 13 | 15 | 10
13.15.11 | CT ratio Rogowski and CT ratio low power up to 800 A or up to 2 000 A with CP CB2, 5 kVA output power |  |  |  | 13. | 15. | 11 | 13 | 15 | 11
13.15.12 | Power/dissipation factor test up to 12kV/15 kV, 300 mA ¦ with CP TD12/15 |  |  |  | 13. | 15. | 12 | 13 | 15 | 12
13.15.13 | IEC 61850 Sampled Values testing |  |  |  | 13. | 15. | 13 | 13 | 15 | 13
13.15.14 |  |  |  |  | 13. | 15. | 14 | 13 | 15 | 14
13.15.15 | VOLTAGE TRANSFORMER TESTING |  |  |  | 13. | 15. | 15 | 13 | 15 | 15
13.15.16 | VT ratio up to 2 kVAC ¦ polarity and burden |  |  |  | 13. | 15. | 16 | 13 | 15 | 16
13.15.17 | VT burden up to 130 VAC ¦ secondary |  |  |  | 13. | 15. | 17 | 13 | 15 | 17
13.15.18 | VT secondary voltage withstand test up to 2 Kvac |  |  |  | 13. | 15. | 18 | 13 | 15 | 18
13.15.19 | Polarity check with CPOL3 up to 2 kVAC |  |  |  | 13. | 15. | 19 | 13 | 15 | 19
13.15.20 | VT electronics up to 2 kVAC |  |  |  | 13. | 15. | 20 | 13 | 15 | 20
13.15.21 | VT voltage withstand test up to 2 kVAC |  |  |  | 13. | 15. | 21 | 13 | 15 | 21
13.15.22 | IEC 61850 Sampled Values testing |  |  |  | 13. | 15. | 22 | 13 | 15 | 22
13.15.23 | Power/dissipation factor test up to 12 kV/15kV, 300 mA ¦ with CP TD12/15 |  |  |  | 13. | 15. | 23 | 13 | 15 | 23
13.15.24 |  |  |  |  | 13. | 15. | 24 | 13 | 15 | 24
13.15.25 | POWER AND DISTRIBUTION TRANSFORMER TESTING |  |  |  | 13. | 15. | 25 | 13 | 15 | 25
13.15.26 | DC winding resistance up to 100 ADC |  |  |  | 13. | 15. | 26 | 13 | 15 | 26
13.15.27 | Transformer demagnetization with CP SB1 |  |  |  | 13. | 15. | 27 | 13 | 15 | 27
13.15.28 | Dynamic load tap changer diagnostics (on load tap changer test) up to 100 ADC ¦ optionally with CP SB1 |  |  |  | 13. | 15. | 28 | 13 | 15 | 28
13.15.29 | Transformer turns ratio (TTR) per tap up to 2 kVAC ¦ including polarity and excitation current ¦IEC 61387-1 support for transformer with unconventional vector groups |  |  |  | 13. | 15. | 29 | 13 | 15 | 29
13.15.30 | Automatically determination of the transformer’s vector group with CP SB1 Leakage reactance / short circuit impedance up to 6 AAC Transformer, bushing: power/dissipation factor + insulation capacitance up to 12 kV/15kV, 300 mA ¦ frequency from 15 Hz to 400 Hz ¦ with CP TD12/15 Insulating fluids: power/dissipation factor up to 12 kV/15kV, 300 mA ¦ with CP TD12/15 and CP TC12 |  |  |  | 13. | 15. | 30 | 13 | 15 | 30
13.15.31 | Excitation current per tap up to 12 kV/15kV, 300 mA ¦ with CP TD12/15 |  |  |  | 13. | 15. | 31 | 13 | 15 | 31
13.15.32 | Frequency response of stray losses (FRSL) Surge arrestors: leakage current and watt losses up to 12 kV/15kV, 300 mA ¦ with CP TD12/15 |  |  |  | 13. | 15. | 32 | 13 | 15 | 32
13.15.33 | HV source for voltage withstand test up to 15 kVA ¦ with 3 CPCs + TRC1 |  |  |  | 13. | 15. | 33 | 13 | 15 | 33
13.15.34 | HV source for PD measurements up to 15 kVA ¦ with 3 CPCs + TRC1 |  |  |  | 13. | 15. | 34 | 13 | 15 | 34
13.15.35 | LINE IMPENDANDANCE MEASUREMENT - CABLE AND TRANSMISSION LINE DIAGNOSIS |  |  |  | 13. | 15. | 35 | 13 | 15 | 35
13.15.36 | Line impedance and k-factor up to 100 A ¦ with CP CU1 |  |  |  | 13. | 15. | 36 | 13 | 15 | 36
13.15.37 | Mutual coupling up to 100 A ¦ with CP CU1 |  |  |  | 13. | 15. | 37 | 13 | 15 | 37
13.15.38 | Positive or zero sequence impedance |  |  |  | 13. | 15. | 38 | 13 | 15 | 38
13.15.39 | GROUNDING SYSTEM ANALYSIS |  |  |  | 13. | 15. | 39 | 13 | 15 | 39
13.15.40 | Ground grid impedance for large systems up to 100 A ¦ with CP CU1 |  |  |  | 13. | 15. | 40 | 13 | 15 | 40
13.15.41 | Step and touch voltage up to 100 A ¦ with CP CU1 and HGT1 |  |  |  | 13. | 15. | 41 | 13 | 15 | 41
13.15.42 | Ground grid impedance for small systems up to 6 AAC |  |  |  | 13. | 15. | 42 | 13 | 15 | 42
13.15.43 | Soil resistivity up to 6 AAC Integrity check of grounding connection |  |  |  | 13. | 15. | 43 | 13 | 15 | 43
13.15.44 | up to 400 ADC |  |  |  | 13. | 15. | 44 | 13 | 15 | 44
13.15.45 | Reduction factor / current split factor |  |  |  | 13. | 15. | 45 | 13 | 15 | 45
13.15.46 | Measure multiple current paths with Rogowski coil |  |  |  | 13. | 15. | 46 | 13 | 15 | 46
13.15.47 | SWITCHGEAR/CIRCUIT BREAKER TESTING |  |  |  | 13. | 15. | 47 | 13 | 15 | 47
13.15.48 | Contact resistance up to 400 ADC |  |  |  | 13. | 15. | 48 | 13 | 15 | 48
13.15.49 | Bushing: power/dissipation factor (tan δ) + insulation capacitance |  |  |  | 13. | 15. | 49 | 13 | 15 | 49
13.15.50 | 12 kV/15kV, 300 mA ¦ frequency from 15 Hz to 400 Hz ¦ with CP TD12/15 |  |  |  | 13. | 15. | 50 | 13 | 15 | 50
13.15.51 | Circuit breaker: power/dissipation factor (tan δ) up to 12 kV/15kV, 300 mA ¦ frequency from 15 Hz to 400 Hz ¦ with CP TD12/15 |  |  |  | 13. | 15. | 51 | 13 | 15 | 51
13.15.52 | Insulating fluids: power/dissipation factor (tan δ) |  |  |  | 13. | 15. | 52 | 13 | 15 | 52
13.15.53 | up to 12 kV, 300 mA ¦ with CP TD12/15 and CP TC1223 |  |  |  | 13. | 15. | 53 | 13 | 15 | 53
13.15.54 | COMMISSIONING PROTECTION SYSTEMS |  |  |  | 13. | 15. | 54 | 13 | 15 | 54
13.15.55 | CT ratio (with burden) up to 800 A or 2000 A with the CP CB2, 5 kVA output power |  |  |  | 13. | 15. | 55 | 13 | 15 | 55
13.15.56 | CT burden up to 6 AAC ¦ secondary CT excitation curve (knee point) up to 2 kVAC |  |  |  | 13. | 15. | 56 | 13 | 15 | 56
13.15.57 | VT ratio up to 2 kVAC ¦ polarity and burden |  |  |  | 13. | 15. | 57 | 13 | 15 | 57
13.15.58 | VT burden up to 130 VAC ¦ secondary |  |  |  | 13. | 15. | 58 | 13 | 15 | 58
13.15.59 | Overcurrent relays with primary injection (MV) up to 800 A or 2000 A with the CP CB2, 5 kVA output power |  |  |  | 13. | 15. | 59 | 13 | 15 | 59
13.15.60 | Polarity check with CPOL3 up to 800 A or 2 kVAC , 5 kVA output power |  |  |  | 13. | 15. | 60 | 13 | 15 | 60
13.15.61 | Testing of the entire protection chain by primary fault current injection and live CB tripping |  |  |  | 13. | 15. | 61 | 13 | 15 | 61
13.15.62 | SAMPLED VALUE TESTING |  |  |  | 13. | 15. | 62 | 13 | 15 | 62
13.15.63 | SV CT ratio test and polarity check up to 800 A or up to 2 000 A , 5 kVA output power ¦ with the CP CB2 |  |  |  | 13. | 15. | 63 | 13 | 15 | 63
13.15.64 | SV VT ratio test and polarity check up to 2 Kvac |  |  |  | 13. | 15. | 64 | 13 | 15 | 64
13.15.65 | Automatic MU detection |  |  |  | 13. | 15. | 65 | 13 | 15 | 65
13.15.66 | Automatic voltage / current channel detection |  |  |  | 13. | 15. | 66 | 13 | 15 | 66
13.15.67 | Frequency selective voltage / current meter |  |  |  | 13. | 15. | 67 | 13 | 15 | 67
13.15.68 | Noise level measurement |  |  |  | 13. | 15. | 68 | 13 | 15 | 68
13.15.69 | Amplitude response of the signal processing chain up to 800 A or up to 2 kVAC ¦ frequency from 15 Hz to 400 Hz |  |  |  | 13. | 15. | 69 | 13 | 15 | 69
14. | Transformer and Reactor Mechanical Protection |  |  |  | 14. |  |  | 14 | 14 | 39 | R1
14.1. | Sergi Fire Protection or Equivalent |  |  |  | 14. | 1. |  | 14 | 1 | 40 | R2
[8 empty] | 14 | 1 | 41 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 14 | 1 | 42 | R3
14.1.1 | Maker’s name | To be stated by Bidder |  |  | 14. | 1. | 1 | 14 | 1 | 1
14.1.2 | Maker’s type and reference | To be stated by Bidder |  |  | 14. | 1. | 2 | 14 | 1 | 2
14.1.3 | Country of origin | To be stated by Bidder |  |  | 14. | 1. | 3 | 14 | 1 | 3
14.1.4 | System type | Fast Depressurization & Nitrogen Injection System (NIFPS) |  |  | 14. | 1. | 4 | 14 | 1 | 4
14.1.5 | Standards compliance | NFPA 850 |  |  | 14. | 1. | 5 | 14 | 1 | 5
14.1.6 | Type test (Authority, year, Doc.no) | To be stated by Bidder |  |  | 14. | 1. | 6 | 14 | 1 | 6
14.1.7 | (Deleted) |  |  |  | 14. | 1. | 7 | 14 | 1 | 7
14.1.8 | Coverage area per module | Per transformer unit (0.1 MVA to 1,000 MVA+) |  | m² | 14. | 1. | 8 | 14 | 1 | 8
14.1.9 | Response time (detection-to-discharge) | 0.5 to 20 milliseconds |  | ms | 14. | 1. | 9 | 14 | 1 | 9
14.1.10 | Detection system | Passive mechanical |  |  | 14. | 1. | 10 | 14 | 1 | 10
14.1.11 | Control panel compatibility | EN 54-20, Modbus interface |  |  | 14. | 1. | 11 | 14 | 1 | 11
14.1.12 | (Deleted) |  |  |  | 14. | 1. | 12 | 14 | 1 | 12
14.1.13 | Piping material | Carbon steel / stainless steel depressurization sets and oil-gas separation tank |  |  | 14. | 1. | 13 | 14 | 1 | 13
14.1.14 | Nozzle material/life | Rupture disc and mechanical valve — long service life, project-specific |  |  | 14. | 1. | 14 | 14 | 1 | 14
14.1.15 | Environmental rating (IP) | IP65 (outdoor) |  |  | 14. | 1. | 15 | 14 | 1 | 15
14.1.16 | Fire classes covered | Oil transformer fires (Class B — flammable liquid) |  |  | 14. | 1. | 16 | 14 | 1 | 16
14.1.17 | Certifications | NFPA 850 compliant |  |  | 14. | 1. | 17 | 14 | 1 | 17
14.1.18 | Compatibility | 0.1 MVA to 1,000 MVA+ (all voltage levels including HV/EHV) |  |  | 14. | 1. | 18 | 14 | 1 | 18
14.1.19 | Gross weight | To be stated by Bidder |  |  | 14. | 1. | 19 | 14 | 1 | 19
[8 empty] | 14 | 1 | 20 | tom rad
14.2. | Kelman Online Dissolve Gas Analysis or Equivalent |  |  |  | 14. | 2. |  | 14 | 2 | 21 | R2
[8 empty] | 14 | 2 | 22 | tom rad
Item | Description | Required | Tendered | Unit |  |  |  | 14 | 2 | 23 | R3
14.2.1 | Manufacturer's name | To be stated by Bidder |  |  | 14. | 2. | 1 | 14 | 2 | 1
14.2.2 | Model and series | To be stated by Bidder |  |  | 14. | 2. | 2 | 14 | 2 | 2
14.2.3 | Country of origin | To be stated by Bidder |  |  | 14. | 2. | 3 | 14 | 2 | 3
14.2.4 | System type | Online continuous DGA monitor |  |  | 14. | 2. | 4 | 14 | 2 | 4
14.2.5 | Standards compliance | IEC 60567, IEEE C57.104, IEC 62271 |  |  | 14. | 2. | 5 | 14 | 2 | 5
14.2.6 | Type test certification | To be stated by Bidder (Authority, year) |  |  | 14. | 2. | 6 | 14 | 2 | 6
14.2.7 | Measurement technology | Gas chromatography or equivalent |  |  | 14. | 2. | 7 | 14 | 2 | 7
14.2.8 | Measured gases | H₂, CH₄, C₂H₂, C₂H₄, C₂H₆, CO, CO₂, O₂, N₂ |  |  | 14. | 2. | 8 | 14 | 2 | 8
14.2.9 | Detection range | H₂: 1-2000 ppm, C₂H₂: 0.1-100 ppm (full ranges to be specified) |  | ppm | 14. | 2. | 9 | 14 | 2 | 9
14.2.10 | Measurement accuracy | ±10% or better of reading |  | % | 14. | 2. | 10 | 14 | 2 | 10
14.2.11 | Sampling frequency | Continuous (real-time) with adjustable intervals |  |  | 14. | 2. | 11 | 14 | 2 | 11
14.2.12 | Communication protocols | Modbus RTU/TCP, IEC 61850, DNP3, OPC UA |  |  | 14. | 2. | 12 | 14 | 2 | 12
14.2.13 | Alarm functionality | Programmable thresholds with relay outputs |  |  | 14. | 2. | 13 | 14 | 2 | 13
14.2.14 | Power supply | 100-240V AC, 50/60Hz with battery backup |  |  | 14. | 2. | 14 | 14 | 2 | 14
14.2.15 | Environmental rating | IP65 |  |  | 14. | 2. | 15 | 14 | 2 | 15
14.2.16 | Operating temperature | -20°C to +55°C |  | °C | 14. | 2. | 16 | 14 | 2 | 16
14.2.17 | Calibration | Automatic self-calibration with manual override |  |  | 14. | 2. | 17 | 14 | 2 | 17
14.2.18 | Maintenance interval | ≥6 months between required servicing |  | months | 14. | 2. | 18 | 14 | 2 | 18
14.2.19 | Data storage | Minimum 2 years of historical data |  |  | 14. | 2. | 19 | 14 | 2 | 19
14.2.20 | Warranty period | Minimum 2 years |  |  | 14. | 2. | 20 | 14 | 2 | 20
[8 empty] | 12 | 1 | 21 | tom rad