## SCHEDULE 1
400kV Nakonde-Tanzania border Double-Circuit Overhead Transmission Line (NT)
SCHEDULE 1: Plant and Mandatory Spare Parts Supplied from Abroad
Item No | Description | Code1 | Unit | Qty. (1) | Unit Price2 |  | Total Price2
[5 empty] | [Specify Currency] | (CIP - Nakonde) | [Specify Currency] (1)x(3)
Plant and Installation of 400 kV Nakonde-Tanzania border OHTL
1 | Towers 400 kV Double Circuit OHTL Complete delivery of suspension tower 400DA (0° to 2° angle) as defined in the Scope of Works Supply of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings.
1.01 | Type 400DA Tower Basic body and crossarms ± 0 m body extension + 0 m leg extensions |  | per tower | 31 |  |  | 0
1.02 | Type 400DA Tower 3,0 m Body Extension (only) |  | each | 12 |  |  | 0
1.03 | Type 400DA Tower 6,0 m Body Extension (only) |  | each | 2 |  |  | 0
1.04 | Type 400DA Tower 9,0 m Body Extension (only) |  | each | 2 |  |  | 0
1.05 | Type 400DA Tower 12,0 m Body Extension (only) |  | each | 0 |  |  | 0
1.06 | Type 400DA Tower 15,0 m Body Extension (only) |  | each | 0 |  |  | 0
1.07 | Type 400DA Tower 1,0 m Leg Extension |  | each | 31 |  |  | 0
1.08 | Type 400DA Tower 2,0 m Leg Extension |  | each | 25 |  |  | 0
1.09 | Type 400DA Tower 3,0 m Leg Extension |  | each | 12 |  |  | 0
1.1 | Type 400DA Tower 4,0 m Leg Extension |  | each | 4 |  |  | 0
1.11 | Type 400DA Tower 5,0 m Leg Extension |  | each | 4 |  |  | 0
1.12 | Stubs for Type 400DA tower |  | each | 124 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
2 | Complete delivery of angle/anti-cascading tension tower, 400DB (0° to 10° angle) as defined in the Scope of Works Supply of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings.
2.01 | Type 400DB Tower Basic body and crossarms ± 0 m body extension + 0 m leg extensions |  | per tower | 1 |  |  | 0
2.02 | Type 400DB Tower 3,0 m Body Extension (only) |  | each | 0 |  |  | 0
2.03 | Type 400DB Tower 6,0 m Body Extension (only) |  | each | 0 |  |  | 0
2.04 | Type 400DB Tower 9,0 m Body Extension (only) |  | each | 0 |  |  | 0
2.05 | Type 400DB Tower 12,0 m Body Extension (only) |  | each | 0 |  |  | 0
2.06 | Type 400DB Tower 15,0 m Body Extension (only) |  | each | 0 |  |  | 0
2.07 | Type 400DB Tower 1,0 m Leg Extension |  | each | 1 |  |  | 0
2.08 | Type 400DB Tower 2,0 m Leg Extension |  | each | 1 |  |  | 0
2.09 | Type 400DB Tower 3,0 m Leg Extension |  | each | 1 |  |  | 0
2.1 | Type 400DB Tower 4,0 m Leg Extension |  | each | 0 |  |  | 0
2.11 | Type 400DB Tower 5,0 m Leg Extension |  | each | 0 |  |  | 0
2.12 | Stubs for Type 400DB tower |  | each | 4 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
3 | Complete delivery of angle tension tower 400DC (10° to 30° angle) as defined in the Scope of Works Supply of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings.
3.01 | Type 400DC Tower Basic body and crossarms ± 0 m body extension + 0 m leg extensions |  | per tower | 4 |  |  | 0
3.02 | Type 400DC Tower 3,0 m Body Extension (only) |  | each | 0 |  |  | 0
3.03 | Type 400DC Tower 6,0 m Body Extension (only) |  | each | 1 |  |  | 0
3.04 | Type 400DC Tower 9,0 m Body Extension (only) |  | each | 0 |  |  | 0
3.05 | Type 400DC Tower 12,0 m Body Extension (only) |  | each | 0 |  |  | 0
3.06 | Type 400DC Tower 15,0 m Body Extension (only) |  | each | 0 |  |  | 0
3.07 | Type 400DC Tower 1,0 m Leg Extension |  | each | 4 |  |  | 0
3.08 | Type 400DC Tower 2,0 m Leg Extension |  | each | 3 |  |  | 0
3.09 | Type 400DC Tower 3,0 m Leg Extension |  | each | 2 |  |  | 0
3.1 | Type 400DC Tower 4,0 m Leg Extension |  | each | 0 |  |  | 0
3.11 | Type 400DC Tower 5,0 m Leg Extension |  | each | 0 |  |  | 0
3.12 | Stubs for Type 400DC tower |  | each | 16 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
4 | Complete delivery of angle tension tower 400DD (30° to 60° angle) as defined in the Scope of Works Supply of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings.
4.01 | Type 400DD Tower Basic body and crossarms ± 0 m body extension + 0 m leg extensions |  | per tower | 1 |  |  | 0
4.02 | Type 400DD Tower 3,0 m Body Extension (only) |  | each | 0 |  |  | 0
4.03 | Type 400DD Tower 6,0 m Body Extension (only) |  | each | 0 |  |  | 0
4.04 | Type 400DD Tower 9,0 m Body Extension (only) |  | each | 0 |  |  | 0
4.05 | Type 400DD Tower 12,0 m Body Extension (only) |  | each | 0 |  |  | 0
4.06 | Type 400DD Tower 1,0 m Leg Extension |  | each | 1 |  |  | 0
4.07 | Type 400DD Tower 2,0 m Leg Extension |  | each | 1 |  |  | 0
4.08 | Type 400DD Tower 3,0 m Leg Extension |  | each | 1 |  |  | 0
4.09 | Type 400DD Tower 4,0 m Leg Extension |  | each | 0 |  |  | 0
4.1 | Type 400DD Tower 5,0 m Leg Extension |  | each | 0 |  |  | 0
4.11 | Stubs for Type 400DD tower |  | each | 4 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
5 | Complete delivery of angle tension tower 400DE (60° to 90° angle) as defined in the Scope of Works Supply of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings.
5.01 | Type 400DE Tower Basic bodyand crossarms ± 0 m body extension + 0 m leg extensions |  | per tower | 0 |  |  | 0
5.02 | Type 400DE Tower 3,0 m Body Extension (only) |  | each | 0 |  |  | 0
5.03 | Type 400DE Tower 6,0 m Body Extension (only) |  | each | 0 |  |  | 0
5.04 | Type 400DE Tower 9,0 m Body Extension (only) |  | each | 0 |  |  | 0
5.05 | Type 400DE Tower 12,0 m Body Extension (only) |  | each | 0 |  |  | 0
5.06 | Type 400DE Tower 1,0 m Leg Extension |  | each | 0 |  |  | 0
5.07 | Type 400DE Tower 2,0 m Leg Extension |  | each | 0 |  |  | 0
5.08 | Type 400DE Tower 3,0 m Leg Extension |  | each | 0 |  |  | 0
5.09 | Type 400DE Tower 4,0 m Leg Extension |  | each | 0 |  |  | 0
5.1 | Type 400DE Tower 5,0 m Leg Extension |  | each | 0 |  |  | 0
5.11 | Stubs for Type 400DE tower |  | each | 0 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
6 | Complete delivery of terminal tension tower 400DET (0° to 45° angle) as defined in the Scope of Works Supply of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings.
6.01 | Type 400DET Tower Basic bodyand crossarms ± 0 m body extension + 0 m leg extensions |  | per tower | 2 |  |  | 0
6.02 | Type 400DET Tower 3,0 m Body Extension (only) |  | each | 0 |  |  | 0
6.03 | Type 400DET Tower 6,0 m Body Extension (only) |  | each | 0 |  |  | 0
6.04 | Type 400DET Tower 9,0 m Body Extension (only) |  | each | 0 |  |  | 0
6.05 | Type 400DET Tower 1,0 m Leg Extension |  | each | 2 |  |  | 0
6.06 | Type 400DET Tower 2,0 m Leg Extension |  | each | 2 |  |  | 0
6.07 | Type 400DET Tower 3,0 m Leg Extension |  | each | 1 |  |  | 0
6.08 | Type 400DET Tower 4,0 m Leg Extension |  | each | 0 |  |  | 0
6.09 | Type 400DET Tower 5,0 m Leg Extension |  | each | 0 |  |  | 0
6.1 | Stubs for Type 400DET tower |  | each | 8 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
8A | Foundations 400 kV Double Circuit OHTL All Foundations Material for tower types according to the specification, all necessary reinforcement, shuttering material, complete tower earthing material and their connections to tower.
7 | Complete delivery of foundations for tower type: Suspension tower 400DA (0° to 2° angle) Devilery of complete materials and equipment necessary for the construction of foundations as defined in the Scope of Works and in "8A" above
7.01 | Foundation class 1 |  | set | 1 |  |  | 0
7.02 | Foundation class 2 |  | set | 3 |  |  | 0
7.03 | Foundation class 3 |  | set | 9 |  |  | 0
7.04 | Foundation class 4 |  | set | 4 |  |  | 0
7.05 | Foundation class 4W |  | set | 11 |  |  | 0
7.06 | Foundation class 5 |  | set | 1 |  |  | 0
7.07 | Foundation class 5W |  | set | 1 |  |  | 0
7.08 | Foundation class 6 |  | set | 1 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
8 | Complete delivery of foundations for tower type: angle/anti-cascading tension tower 400DB (0° to 10° angle) Devilery of complete materials and equipment necessary for the construction of foundations as defined in the Scope of Works and in "8A" above
8.01 | Foundation class 1 |  | set | 0 |  |  | 0
8.02 | Foundation class 2 |  | set | 0 |  |  | 0
8.03 | Foundation class 3 |  | set | 1 |  |  | 0
8.04 | Foundation class 4 |  | set | 0 |  |  | 0
8.05 | Foundation class 4W |  | set | 0 |  |  | 0
8.06 | Foundation class 5 |  | set | 0 |  |  | 0
8.07 | Foundation class 5W |  | set | 0 |  |  | 0
8.08 | Foundation class 6 |  | set | 0 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
9 | Complete delivery of foundations for tower type: angle tension tower 400DC (10° to 30° angle) Devilery of complete materials and equipment necessary for the construction of foundations as defined in the Scope of Works and in "8A" above
9.01 | Foundation class 1 |  | set | 0 |  |  | 0
9.02 | Foundation class 2 |  | set | 1 |  |  | 0
9.03 | Foundation class 3 |  | set | 1 |  |  | 0
9.04 | Foundation class 4 |  | set | 1 |  |  | 0
9.05 | Foundation class 4W |  | set | 1 |  |  | 0
9.06 | Foundation class 5 |  | set | 0 |  |  | 0
9.07 | Foundation class 5W |  | set | 0 |  |  | 0
9.08 | Foundation class 6 |  | set | 0 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
10 | Complete delivery of foundations for tower type: angle tension tower 400DD (30° to 60° angle) Devilery of complete materials and equipment necessary for the construction of foundations as defined in the Scope of Works and in "8A" above
10.01 | Foundation class 1 |  | set | 0 |  |  | 0
10.02 | Foundation class 2 |  | set | 0 |  |  | 0
10.03 | Foundation class 3 |  | set | 0 |  |  | 0
10.04 | Foundation class 4 |  | set | 0 |  |  | 0
10.05 | Foundation class 4W |  | set | 1 |  |  | 0
10.06 | Foundation class 5 |  | set | 0 |  |  | 0
10.07 | Foundation class 5W |  | set | 0 |  |  | 0
10.08 | Foundation class 6 |  | set | 0 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
11 | Complete delivery of foundations for tower type: angle tension tower 400DE (60° to 90° angle) Devilery of complete materials and equipment necessary for the construction of foundations as defined in the Scope of Works and in "8A" above
11.01 | Foundation class 1 |  | set | 0 |  |  | 0
11.02 | Foundation class 2 |  | set | 0 |  |  | 0
11.03 | Foundation class 3 |  | set | 0 |  |  | 0
11.04 | Foundation class 4 |  | set | 0 |  |  | 0
11.05 | Foundation class 4W |  | set | 0 |  |  | 0
11.06 | Foundation class 5 |  | set | 0 |  |  | 0
11.07 | Foundation class 5W |  | set | 0 |  |  | 0
11.08 | Foundation class 6 |  | set | 0 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
12 | Complete delivery of foundations for tower type: terminal tension tower 400DET (0° to 45° angle) Devilery of complete materials and equipment necessary for the construction of foundations as defined in the Scope of Works and in "8A" above
12.01 | Foundation class 1 |  | set | 0 |  |  | 0
12.02 | Foundation class 2 |  | set | 0 |  |  | 0
12.03 | Foundation class 3 |  | set | 1 |  |  | 0
12.04 | Foundation class 4 |  | set | 1 |  |  | 0
12.05 | Foundation class 4W |  | set | 0 |  |  | 0
12.06 | Foundation class 5 |  | set | 0 |  |  | 0
12.07 | Foundation class 5W |  | set | 0 |  |  | 0
12.08 | Foundation class 6 |  | set | 0 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
13 | Earthing 400 kV Double circuit OHTL Supply of material for tower groundings, galvanised steel grounding Rod with 20mm diamater, 0.3mm coating thickness, 1,5m length including CCS40 copper clad steel wire strand 7 No.7 AWG, threaded couplers for earth rods, earthing rod clamps, bolted tower connector clamp, C-tap compression connectors, etc. as specified in Employers Requirements.
13.01 | Supply of counterpoise conductor, for connection to the substation earthing grid including CCS40 copper clad steel wire strand 7 No.7 AWG, bolted tower connector clamp, C-tap compression connectors as specified in Employers Requirements |  | km | 1.5 |  |  | 0
13.02 | Supply of material for Earthing Type A, as specified in Employers Requirements. |  | each | 39 |  |  | 0
13.03 | Supply of material for Earthing Type B, as specified in Employers Requirements. |  | each | 27 |  |  | 0
13.04 | Supply of material for Earthing Type C, as specified in Employers Requirements. |  | each | 8 |  |  | 0
13.05 | Earthing enhancements for Type D where required as per specification to achieve specified tower footing resistance |  | each | 4 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
14 | Insulator and Fittings 400 kV Double Circuit OHTL LINE CONDUCTOR INSULATORS AND FITTINGS Supply of Complete Insulator Sets including insulators, all types of clamps, armour rods, extension links, pilot insulator sets, counterweights and all connections to Tower. All cost for Employer's inspector during test shall be covered as per Schedule of Guarantee Characteristics. NOTE; Arcing horns shall be suitable/adjusted for the operating voltage, 330kV, at least 2km out from Nakonde Stepdown substation.
14.01 | Single Suspension insulator set for twin "Bluejay" conductor including all clamps and fittings, armour rods and connections to tower, arcing rings both ends |  | each | 162 |  |  | 0
14.02 | Double Suspension insulator set for twin "Bluejay" conductor including all clamps and fittings, armour rods and connections to tower, arcing rings both ends. |  | each | 24 |  |  | 0
14.03 | Double Tension insulator set for twin "Bluejay" conductor including all clamps and fittings, armour rods and connections to tower, arcing rings both ends |  | each | 96 |  |  | 0
14.04 | Twin spacer damper for "Bluejay" conductor bundle |  | each | 1404 |  |  | 0
14.05 | Counter weights for reduction of insulator swing |  | each | 12 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
15 | CONDUCTOR, OPGW AND GROUND WIRES Supply, stringing and installation including all joints, sleeves, jumper loops, spacers and necessary dampers, earthing connections and all downleads as per Employers Requirements. All cost for Employer's inspector during test shall be covered as per Employers Requirements
15.01 | ACSR Conductor code name Bluejay; twin bundled, stringing of double circuit |  | route km | 15 |  |  | 0
15.02 | Optical Ground Wire (OPGW) type ACSR 95/55, 48 cores (24+24), ITU-T G.655 and ITU-T G.652D s/c rating 200 kA2/sec, including all splicing and connections to joint boxes. |  | route km | 15 |  |  | 0
15.03 | Earth Wire (OHGW) type ACSR 95/55 |  | route km | 15 |  |  | 0
15.04 | Stockbridge type vibration dampers for Bluejay conductor |  | each | 1128 |  |  | 0
15.05 | Stockbridge type vibration dampers for OPGW type ACSR 95/55 |  | each | 153 |  |  | 0
15.06 | Stockbridge type vibration dampers for Earth Wire type ACSR 95/55 |  | each | 94 |  |  | 0
15.07 | Mid - span tension joint for Bluejay conductor |  | each | 93 |  |  | 0
15.08 | Mid - span tension joint for Earth Wire OHGW type ACSR 95/55 |  | each | 4 |  |  | 0
15.09 | Repair sleeve for Bluejay conductor |  | each | 9 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
15.1 | Fall Arrest System |  | set | 5 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
16 | OPGW AND OVER HEAD GROUND WIRE FITTINGS AND ACCESSORIES Supply of complete Sets of Fittings, including all types of clamps, extension links, armor rods, counterweights, earth bonds and all connections to Tower. All cost for Employer's inspector during test shall be covered as per Employers Requirement section VII Part II.
16.01 | Suspension set for OPGW |  | each | 31 |  |  | 0
16.02 | Straight through double tension set for OPGW |  | each | 14 |  |  | 0
16.03 | Double dead end tension set, including down the tower connection to joint box on suspension or tension tower for OPGW |  | each | 8 |  |  | 0
16.04 | Tension terminal dead end down set for OPGW |  | each | 2 |  |  | 0
16.05 | Jointing Box for OPGW/OPGW, for use within the transmission line, including fixing, splicing and downlead clamps, with feed through sets, suitable for up to 48 cores. ITU-T G.655 and ITU 652D s/c rating 200 kA2/sec and OPGW, types as per specification |  | each | 4 |  |  | 0
16.06 | 4 way Jointing Box for OPGW/OPGW/OFC, for use within the transmission line, including fixing, splicing and downlead clamps, with feed through sets, suitable for up to 48 cores. ITU-T G.655 and ITU 652D s/c rating 200 kA2/sec and OPGW, types as per specification |  | each | 2 |  |  | 0
16.07 | Terminal Box for OPGW/OFC, for the connection at substation gantry, including fixing, splicing and downlead clamps, for up to 48 cores. ITU-T G.655 and ITU G-652D s/c rating 200 kA2/sec and OPGW/OFC, types as per specification |  | each | 2 |  |  | 0
16.08 | Suspension set for Earth Wire (OHGW) |  | each | 31 |  |  | 0
16.09 | Straight through double tension set for Earth Wire (OHGW) |  | each | 14 |  |  | 0
16.1 | Double dead end tension set, including down the tower connection to joint box on suspension or tension tower for Earth Wire (OHGW) |  | each | 8 |  |  | 0
16.11 | Tension terminal dead end down set for Earth Wire (OHGW) |  | each | 2 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
17 | Tools and Equipment
17.01 | Conductor "stockings" for pulling conductor to fit ACSR "Bluejay" |  | each | 12 |  |  | 0
17.02 | Pre-formed armourod type Repair Sleeves for ACSR "Bluejay" |  | each | 25 |  |  | 0
17.03 | Compression type repair sleeves for ACSR "Bluejay" |  | each | 25 |  |  | 0
17.04 | come along clamp (Riganti or Klein) for ACSR "Bluejay" conductor |  | each | 12 |  |  | 0
17.05 | tandem come along clamp (Riganti or Klein) for ACSR "Bluejay" conductor |  | each | 12 |  |  | 0
17.06 | come along clamp (Riganti or Klien) for ACSR 95/55 earth wire |  | each | 6 |  |  | 0
17.07 | come along clamp (Riganti or Klein) for OPGW earth wire |  | each | 6 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
18 | SPARES
18.01 | CONDUCTOR , OPGW AND GROUND WIRES
18.02 | Spare double ACSR "Bluejay" Conductor |  | km | 5 |  |  | 0
18.03 | Spare ACSR 95/55 Earth Conductor |  | km | 5 |  |  | 0
18.04 | Spare OPGW Conductor type ACSR 95/55 |  | km | 5 |  |  | 0
18.05 | Counterpoise conductor |  | km | 2.5 |  |  | 0
18.06 | LINE CONDUCTOR INSULATORS AND FITTINGS
18.07 | Double tension insulator set complete with all fittings for ACSR "Bluejay" |  | each | 6 |  |  | 0
18.08 | Single suspension insulator set complete with all fittings for ACSR "Bluejay" |  | each | 10 |  |  | 0
18.09 | Complete tension set for OPGW earth wire (pair) |  | each | 4 |  |  | 0
18.1 | Complete suspension set for OPGW earth wire |  | each | 4 |  |  | 0
18.11 | Complete tension set for ACSR 95/55 earth wire (single) |  | each | 4 |  |  | 0
18.12 | Complete suspension set for ACSR 95/55 earth wire |  | each | 6 |  |  | 0
18.13 | OVERHEAD LINE ACCESSORIES
18.14 | Assortment of tower bolts |  | tonne | 1 |  |  | 0
18.15 | Assortment of anti-theft type tower bolts |  | tonne | 1 |  |  | 0
18.16 | Mid-span joints for ACSR "Bluejay" Compression type. |  | each | 6 |  |  | 0
18.17 | Vibration Dampers for ACSR "Bluejay" |  | each | 24 |  |  | 0
18.18 | Tension Clamps for ACSR "Bluejay" |  | each | 6 |  |  | 0
18.19 | Suspension clamps complete with preformed armour rods for ACSR "Bluejay" |  | each | 12 |  |  | 0
18.2 | Spacers for twin ACSR "Bluejay" |  | each | 20 |  |  | 0
18.21 | Vibration Dampers for ACSR 95/55 Earth wire |  | each | 10 |  |  | 0
18.22 | Vibration Dampers for OPGW Earth wire |  | each | 10 |  |  | 0
18.23 | Midspan joint for ACSR 95/55 earth wire |  | each | 5 |  |  | 0
| SUB-TOTAL | [5 empty] | 0
| TOTAL SCHEDULE 1, CARRIED TO SUMMARY | [5 empty] | 0
Name of Bidder
Signature of Bidder
1 Bidders shall enter a code representing the country of origin of all imported plant and equipment.
2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies

## Country of Origin Declaration
Country of Origin Declaration Form
Item | Description | Code | Country

## SCHEDULE 2
400kV Nakonde-Tanzania border Double-Circuit Overhead Transmission Line (NT)
SCHEDULE 2: Plant and Mandatory Spare Parts Supplied from within the Employer's Country
Item No | Description | Unit | Qty. (1) | Unit Price2 (EXW-Zambia) (2) | Sales and other taxes payable per line item if Contract is awarded (in accordance with ITB 17.5 (b) (ii) (3) | Total Price2 (1)x(2)
|  |  |  | (ZMW) | (ZMW) | (ZMW)
Plant and Installation of 400 kV Nakonde-Tanzania border OHTL
Foundations 400 kV Double Circuit OHTL Locally Supply of Foundation material for steel tower types according to the specification, and according to drawings and regulations of the Employer. All foundation must have a chimney height above ground of minimum 500mm.
1 | Local delivery of foundations material for tower type: Suspension tower 400DA (0° to 2° angle) Including complete materials necessary for the construction of foundations as defined in the Scope of Works
1.01 | Foundation class 1 | set | 1 |  |  | 0
1.02 | Foundation class 2 | set | 3 |  |  | 0
1.03 | Foundation class 3 | set | 9 |  |  | 0
1.04 | Foundation class 4 | set | 4 |  |  | 0
1.05 | Foundation class 4W | set | 11 |  |  | 0
1.06 | Foundation class 5 | set | 1 |  |  | 0
1.07 | Foundation class 5W | set | 1 |  |  | 0
1.08 | Foundation class 6 | set | 1 |  |  | 0
| SUB-TOTAL |  |  |  | 0 | 0
2 | Local delivery of foundations material for tower type: angle/anti-cascading tension tower 400DB (0° to 10° angle) Including complete materials necessary for the construction of foundations as defined in the Scope of Works
2.01 | Foundation class 1 | set | 0 |  |  | 0
2.02 | Foundation class 2 | set | 0 |  |  | 0
2.03 | Foundation class 3 | set | 1 |  |  | 0
2.04 | Foundation class 4 | set | 0 |  |  | 0
2.05 | Foundation class 4W | set | 0 |  |  | 0
2.06 | Foundation class 5 | set | 0 |  |  | 0
2.07 | Foundation class 5W | set | 0 |  |  | 0
2.08 | Foundation class 6 | set | 0 |  |  | 0
| SUB-TOTAL |  |  |  | 0 | 0
3 | Local delivery of foundations material for tower type: angle tension tower 400DC (10° to 30° angle) Including complete materials necessary for the construction of foundations as defined in the Scope of Works
3.01 | Foundation class 1 | set | 0 |  |  | 0
3.02 | Foundation class 2 | set | 1 |  |  | 0
3.03 | Foundation class 3 | set | 1 |  |  | 0
3.04 | Foundation class 4 | set | 1 |  |  | 0
3.05 | Foundation class 4W | set | 1 |  |  | 0
3.06 | Foundation class 5 | set | 0 |  |  | 0
3.07 | Foundation class 5W | set | 0 |  |  | 0
3.08 | Foundation class 6 | set | 0 |  |  | 0
| SUB-TOTAL |  |  |  | 0 | 0
4 | Local delivery of foundations material for tower type: angle tension tower 400DD (30° to 60° angle) Including complete materials necessary for the construction of foundations as defined in the Scope of Works
4.01 | Foundation class 1 | set | 0 |  |  | 0
4.02 | Foundation class 2 | set | 0 |  |  | 0
4.03 | Foundation class 3 | set | 0 |  |  | 0
4.04 | Foundation class 4 | set | 0 |  |  | 0
4.05 | Foundation class 4W | set | 1 |  |  | 0
4.06 | Foundation class 5 | set | 0 |  |  | 0
4.07 | Foundation class 5W | set | 0 |  |  | 0
4.08 | Foundation class 6 | set | 0 |  |  | 0
| SUB-TOTAL |  |  |  | 0 | 0
5 | Local delivery of foundations material for tower type: angle tension tower 400DE (60° to 90° angle) Including complete materials necessary for the construction of foundations as defined in the Scope of Works
5.01 | Foundation class 1 | set | 0 |  |  | 0
5.02 | Foundation class 2 | set | 0 |  |  | 0
5.03 | Foundation class 3 | set | 0 |  |  | 0
5.04 | Foundation class 4 | set | 0 |  |  | 0
5.05 | Foundation class 4W | set | 0 |  |  | 0
5.06 | Foundation class 5 | set | 0 |  |  | 0
5.07 | Foundation class 5W | set | 0 |  |  | 0
5.08 | Foundation class 6 | set | 0 |  |  | 0
| SUB-TOTAL |  |  |  | 0 | 0
6 | Local delivery of foundations material for tower type: terminal tension tower 400DET (0° to 45° angle) Including complete materials necessary for the construction of foundations as defined in the Scope of Works
6.01 | Foundation class 1 | set | 0 |  |  | 0
6.02 | Foundation class 2 | set | 0 |  |  | 0
6.03 | Foundation class 3 | set | 1 |  |  | 0
6.04 | Foundation class 4 | set | 1 |  |  | 0
6.05 | Foundation class 4W | set | 0 |  |  | 0
6.06 | Foundation class 5 | set | 0 |  |  | 0
6.07 | Foundation class 5W | set | 0 |  |  | 0
6.08 | Foundation class 6 | set | 0 |  |  | 0
| SUB-TOTAL |  |  |  | 0 | 0
7
7.01 | [5 empty] | 0
7.02 | [5 empty] | 0
7.03 | [5 empty] | 0
7.04 | [5 empty] | 0
7.05 | [5 empty] | 0
7.06 | [5 empty] | 0
7.07 | [5 empty] | 0
7.08 | [5 empty] | 0
7.09 | [5 empty] | 0
7.1 | [5 empty] | 0
| SUBTOTAL |  |  |  | 0 | 0
8
8.01 | [5 empty] | 0
8.02 | [5 empty] | 0
8.03 | [5 empty] | 0
8.04 | [5 empty] | 0
8.05 | [5 empty] | 0
8.06 | [5 empty] | 0
8.07 | [5 empty] | 0
8.08 | [5 empty] | 0
8.09 | [5 empty] | 0
8.1 | [5 empty] | 0
| SUBTOTAL |  |  |  | 0 | 0
9
9.01 | [5 empty] | 0
9.02 | [5 empty] | 0
9.03 | [5 empty] | 0
9.04 | [5 empty] | 0
9.05 | [5 empty] | 0
9.06 | [5 empty] | 0
9.07 | [5 empty] | 0
9.08 | [5 empty] | 0
9.09 | [5 empty] | 0
9.1 | [5 empty] | 0
[5 empty] | 0 | 0
10
10.01 | [5 empty] | 0
10.02 | [5 empty] | 0
10.03 | [5 empty] | 0
10.04 | [5 empty] | 0
10.05 | [5 empty] | 0
10.06 | [5 empty] | 0
10.07 | [5 empty] | 0
10.08 | [5 empty] | 0
10.09 | [5 empty] | 0
10.1 | [5 empty] | 0
[5 empty] | 0 | 0
| TOTAL SCHEDULE 2, CARRIED TO SUMMARY |  |  |  | 0 | 0
Name of Bidder
Signature of Bidder
2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies

## SCHEDULE 3
400kV Nakonde-Tanzania border Double-Circuit Overhead Transmission Line (NT)
SCHEDULE 3: Design Services
Item No | Description | Unit | Qty. (1) | Unit Price2 |  | Total Price2
[6 empty] | Local Portion | Foreign Portion
|  |  |  | Local Currency Portion | Foreign Currency Portion | [Specify Currency] | [Specify Currency]
1 | Survey activities like tower spotting, survey of crossing objects including pegging of towers, diagonal profiles and all necessary documentation for the OHTL, soil investigations and route clearing & access roads. |  | 1) | 2) | 3) | (1)x(2) | (1)x(3)
1.1 | Survey, final alignment, tower plotting, preparation of plan, and profile drawings and tower schedule. | route km | 15 |  |  | 0 | 0
1.2 | Sub-soil investigation at support locations by means of in situ DCPT (Dynamic Cone Penetrometer Test), vane test or bearing test as defined in the scope of works | tower | 39 |  |  | 0 | 0
1.3 | Sub-soil investigation at support locations by means of machine boring, including all necessary drilling, sampling, soil penetration test (SPT), establishment of ground water level, laboratory testing and determinationof soil/water aggresiveness | tower | 39 |  |  | 0 | 0
1.4 | Clearing the right-of-way & construction of all required access and maintance roads including Installation of wayleave demarcation reinforced cement concrete markers . | Lot | 1 |  |  | 0 | 0
1.5 | Geotechnical Survey, Analysis and reportng | Lot | 1 |  |  | 0 | 0
2 | Foundation Design (All types) | Lot | 1 |  |  | 0 | 0
3 | Tower Design (All types) | Lot | 1 |  |  | 0 | 0
4 | Insulator Design (All types) | Lot | 1 |  |  | 0 | 0
5 | Foundation Design type test to ultimate or destructive for all foundations other than pad and chimney, including mobilization and erection of all test equipment and installation of the standard footing (the number of test specimen shall be the greater of (i) 1% of the total number of foundations and (ii) two (2). | Lot | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
| TOTAL SCHEDULE 3, CARRIED TO SUMMARY |  |  |  |  | 0 | 0
Name of Bidder
Signature of Bidder
2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies

## SCHEDULE 4
400kV Nakonde-Tanzania border Double-Circuit Overhead Transmission Line (NT)
SCHEDULE 4: Installation Services (Erection, Testing and Commissioning)
Item | Description | Unit | Qty. (1) | Unit Price2 |  | Total Price2
[6 empty] | Local Portion | Foreign Portion
|  |  |  | Local Currency Portion | Foreign Currency Portion | [Specify Currency] | [Specify Currency]
0 | Preliminaries 400 kV Nakonde-Tanzania border OHTL |  | 1) | 2) | 3) | (1)x(2) | (1)x(3)
Site Mobilization
0.01 | Mobilization, Store Yards, contractor personal, Site Office for contractor at localized area. Note: Shall be included in the 330 kV Kasama-Nakonde line Price Schedule. | Lot | 0 |  |  | 0 | 0
0.02 | Mobilization of construction equipment as per evaluation and qualification criteria. Note: Shall be included in the 330 kV Kasama-Nakonde line Price Schedule. | Lot | 0 |  |  | 0 | 0
0.03A | Construction of access roads complete with the finger access roads from public roads as per Employer’s Re-quirements | Lot | 1 |  |  | 0 | 0
0.03B | Bush clearing as per Employer’s Requirements | Lot | 1 |  |  | 0 | 0
0.04 | Insurance. Note: Shall be included in the 330 kV Kasama-Nakonde line Price Schedule. | Lot | 0 |  |  | 0 | 0
0.05 | Site demobilization. Note: Shall be included in the 330 kV Kasama-Nakonde line Price Schedule. | Lot | 0 |  |  | 0 | 0
0.06 | Water and Builder's supply. Note: Shall be included in the 330 kV Kasama-Nakonde line Price Schedule. | Lot | 0 |  |  | 0 | 0
0.07 | Appropriate slope or tower footing protection against erosion for one-third of the total towers | Lot | 1 |  |  | 0 | 0
0.071 | Grassing | Lot | 1 |  |  | 0 | 0
0.072 | Stone pitching | Lot | 1 |  |  | 0 | 0
0.073 | Rip‑rap | Lot | 1 |  |  | 0 | 0
0.074 | Gabions | Lot | 1 |  |  | 0 | 0
0.075 | Terracing/cribbing | Lot | 1 |  |  | 0 | 0
0.08 | Installation of reinforced concrete markers along the ROW | Lot | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
Installation and other services of 400kV Nakonde-Tanzania border OHTL
1A | Foundations 400 kV Double Circuit OHTL All Foundations for tower types according to the specification, including all transport, excavation, installation of stubs, all necessary reinforcement, shuttering, concreting, backfilling, compacting, erosion protection, complete tower earthing and their connections to tower, measuring of earth resistance and submitting of records to Employer/Engineer, according to drawings and regulations of the Employer. Soil class definition concerning permissible soil pressure is according to Employer's design and specifications. All foundation must have a chimney height above ground of minimum 500mm.
1 | Complete installation of foundations for tower type: Suspension tower 400DA (0° to 2° angle) Including complete materials, all necessary transport to site, excavation, installation and backfill and all other works and equipment necessary for the construction of foundations as defined in the Scope of Works
1.01 | Foundation class 1 | set | 1 |  |  | 0 | 0
1.02 | Foundation class 2 | set | 3 |  |  | 0 | 0
1.03 | Foundation class 3 | set | 9 |  |  | 0 | 0
1.04 | Foundation class 4 | set | 4 |  |  | 0 | 0
1.05 | Foundation class 4W | set | 11 |  |  | 0 | 0
1.06 | Foundation class 5 | set | 1 |  |  | 0 | 0
1.07 | Foundation class 5W | set | 1 |  |  | 0 | 0
1.08 | Foundation class 6 | set | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
2 | Complete installation of foundations for tower type: angle/anti-cascading tension tower 400DB (0° to 10° angle) Including complete materials, all necessary transport to site, excavation, installation and backfill and all other works and equipment necessary for the construction of foundations as defined in the Scope of Works
2.01 | Foundation class 1 | set | 0 |  |  | 0 | 0
2.02 | Foundation class 2 | set | 0 |  |  | 0 | 0
2.03 | Foundation class 3 | set | 1 |  |  | 0 | 0
2.04 | Foundation class 4 | set | 0 |  |  | 0 | 0
2.05 | Foundation class 4W | set | 0 |  |  | 0 | 0
2.06 | Foundation class 5 | set | 0 |  |  | 0 | 0
2.07 | Foundation class 5W | set | 0 |  |  | 0 | 0
2.08 | Foundation class 6 | set | 0 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
3 | Complete installation of foundations for tower type: angle tension tower 400DC (10° to 30° angle) Including complete materials, all necessary transport to site, excavation, installation and backfill and all other works and equipment necessary for the construction of foundations as defined in the Scope of Works
3.01 | Foundation class 1 | set | 0 |  |  | 0 | 0
3.02 | Foundation class 2 | set | 1 |  |  | 0 | 0
3.03 | Foundation class 3 | set | 1 |  |  | 0 | 0
3.04 | Foundation class 4 | set | 1 |  |  | 0 | 0
3.05 | Foundation class 4W | set | 1 |  |  | 0 | 0
3.06 | Foundation class 5 | set | 0 |  |  | 0 | 0
3.07 | Foundation class 5W | set | 0 |  |  | 0 | 0
3.08 | Foundation class 6 | set | 0 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
4 | Complete installation of foundations for tower type: angle tension tower 400DD (30° to 60° angle) Including complete materials, all necessary transport to site, excavation, installation and backfill and all other works and equipment necessary for the construction of foundations as defined in the Scope of Works
4.01 | Foundation class 1 | set | 0 |  |  | 0 | 0
4.02 | Foundation class 2 | set | 0 |  |  | 0 | 0
4.03 | Foundation class 3 | set | 0 |  |  | 0 | 0
4.04 | Foundation class 4 | set | 0 |  |  | 0 | 0
4.05 | Foundation class 4W | set | 1 |  |  | 0 | 0
4.06 | Foundation class 5 | set | 0 |  |  | 0 | 0
4.07 | Foundation class 5W | set | 0 |  |  | 0 | 0
4.08 | Foundation class 6 | set | 0 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
5 | Complete installation of foundations for tower type: angle tension tower 400DE (60° to 90° angle) Including complete materials, all necessary transport to site, excavation, installation and backfill and all other works and equipment necessary for the construction of foundations as defined in the Scope of Works
5.01 | Foundation class 1 | set | 0 |  |  | 0 | 0
5.02 | Foundation class 2 | set | 0 |  |  | 0 | 0
5.03 | Foundation class 3 | set | 0 |  |  | 0 | 0
5.04 | Foundation class 4 | set | 0 |  |  | 0 | 0
5.05 | Foundation class 4W | set | 0 |  |  | 0 | 0
5.06 | Foundation class 5 | set | 0 |  |  | 0 | 0
5.07 | Foundation class 5W | set | 0 |  |  | 0 | 0
5.08 | Foundation class 6 | set | 0 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
6 | Complete installation of foundations for tower type: terminal tension tower 400DET (0° to 45° angle) Including complete materials, all necessary transport to site, excavation, installation and backfill and all other works and equipment necessary for the construction of foundations as defined in the Scope of Works
6.01 | Foundation class 1 | set | 0 |  |  | 0 | 0
6.02 | Foundation class 2 | set | 0 |  |  | 0 | 0
6.03 | Foundation class 3 | set | 1 |  |  | 0 | 0
6.04 | Foundation class 4 | set | 1 |  |  | 0 | 0
6.05 | Foundation class 4W | set | 0 |  |  | 0 | 0
6.06 | Foundation class 5 | set | 0 |  |  | 0 | 0
6.07 | Foundation class 5W | set | 0 |  |  | 0 | 0
6.08 | Foundation class 6 | set | 0 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
7 | 400kV Twin Bundled Conductor DC Towers Complete installation of suspension tower 400DA (0° to 2° angle) as defined in the Scope of Works Erection of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections and measuring of earth resistance and submittance of record to Employer/ Engineer, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings. Securing against vandalism by punching of bolts for leg extensions and first tower section. Note: design of special tower must consider all circumstances specified as per Employer Requirements
7.01 | Type 400DA Tower Basic body and crossarms ± 0 m body extension + 0 m leg extensions | per tower | 31 |  |  | 0 | 0
7.02 | Type 400DA Tower 3,0 m Body Extension (only) | each | 12 |  |  | 0 | 0
7.03 | Type 400DA Tower 6,0 m Body Extension (only) | each | 2 |  |  | 0 | 0
7.04 | Type 400DA Tower 9,0 m Body Extension (only) | each | 2 |  |  | 0 | 0
7.05 | Type 400DA Tower 12,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
7.06 | Type 400DA Tower 15,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
7.07 | Type 400DA Tower 1,0 m Leg Extension | each | 31 |  |  | 0 | 0
7.08 | Type 400DA Tower 2,0 m Leg Extension | each | 25 |  |  | 0 | 0
7.09 | Type 400DA Tower 3,0 m Leg Extension | each | 12 |  |  | 0 | 0
7.1 | Type 400DA Tower 4,0 m Leg Extension | each | 4 |  |  | 0 | 0
7.11 | Type 400DA Tower 5,0 m Leg Extension | each | 4 |  |  | 0 | 0
7.12 | Stubs for Type 400DA tower | each | 124 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
8 | Complete installation of angle/anti-cascading tension tower, 400DB (0° to 10° angle) as defined in the Scope of Works Erection of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections and measuring of earth resistance and submittance of record to Employer/ Engineer, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings. Securing against vandalism by punching of bolts for leg extensions and first tower section. Note: design of special tower must consider all circumstances specified as per Employer Requirements
8.01 | Type 400DB Tower Basic body and crossarms ± 0 m body extension + 0 m leg extensions | per tower | 1 |  |  | 0 | 0
8.02 | Type 400DB Tower 3,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
8.03 | Type 400DB Tower 6,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
8.04 | Type 400DB Tower 9,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
8.05 | Type 400DB Tower 12,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
8.06 | Type 400DB Tower 15,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
8.07 | Type 400DB Tower 1,0 m Leg Extension | each | 1 |  |  | 0 | 0
8.08 | Type 400DB Tower 2,0 m Leg Extension | each | 1 |  |  | 0 | 0
8.09 | Type 400DB Tower 3,0 m Leg Extension | each | 1 |  |  | 0 | 0
8.1 | Type 400DB Tower 4,0 m Leg Extension | each | 0 |  |  | 0 | 0
8.11 | Type 400DB Tower 5,0 m Leg Extension | each | 0 |  |  | 0 | 0
8.12 | Stubs for Type 400DB tower | each | 4 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
9 | Complete delivery and installation of angle tension tower 400DC (10° to 30° angle) as defined in the Scope of Works Erection of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections and measuring of earth resistance and submittance of record to Employer/ Engineer, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings. Securing against vandalism by punching of bolts for leg extensions and first tower section. Note: design of special tower must consider all circumstances specified as per Employer Requirements
9.01 | Type 400DC Tower Basic body and crossarms ± 0 m body extension + 0 m leg extensions | per tower | 4 |  |  | 0 | 0
9.02 | Type 400DC Tower 3,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
9.03 | Type 400DC Tower 6,0 m Body Extension (only) | each | 1 |  |  | 0 | 0
9.04 | Type 400DC Tower 9,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
9.05 | Type 400DC Tower 12,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
9.06 | Type 400DC Tower 15,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
9.07 | Type 400DC Tower 1,0 m Leg Extension | each | 4 |  |  | 0 | 0
9.08 | Type 400DC Tower 2,0 m Leg Extension | each | 3 |  |  | 0 | 0
9.09 | Type 400DC Tower 3,0 m Leg Extension | each | 2 |  |  | 0 | 0
9.1 | Type 400DC Tower 4,0 m Leg Extension | each | 0 |  |  | 0 | 0
9.11 | Type 400DC Tower 5,0 m Leg Extension | each | 0 |  |  | 0 | 0
9.11 | Stubs for Type 400DC tower | each | 16 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
10 | Complete delivery and installation of angle tension tower 400DD (30° to 60° angle) as defined in the Scope of Works Erection of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections and measuring of earth resistance and submittance of record to Employer/ Engineer, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings. Securing against vandalism by punching of bolts for leg extensions and first tower section. Note: design of special tower must consider all circumstances specified as per Employer Requirements
10.01 | Type 400DD Tower Basic body and crossarms ± 0 m body extension + 0 m leg extensions | per tower | 1 |  |  | 0 | 0
10.02 | Type 400DD Tower 3,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
10.03 | Type 400DD Tower 6,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
10.04 | Type 400DD Tower 9,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
10.05 | Type 400DD Tower 12,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
10.06 | Type 400DD Tower 1,0 m Leg Extension | each | 1 |  |  | 0 | 0
10.07 | Type 400DD Tower 2,0 m Leg Extension | each | 1 |  |  | 0 | 0
10.08 | Type 400DD Tower 3,0 m Leg Extension | each | 1 |  |  | 0 | 0
10.09 | Type 400DD Tower 4,0 m Leg Extension | each | 0 |  |  | 0 | 0
10.1 | Type 400DD Tower 5,0 m Leg Extension | each | 0 |  |  | 0 | 0
10.11 | Stubs for Type 400DD tower | each | 4 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
11 | Complete delivery and installation of angle tension tower 400DE (60° to 90° angle) as defined in the Scope of Works Erection of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections and measuring of earth resistance and submittance of record to Employer/ Engineer, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings. Securing against vandalism by punching of bolts for leg extensions and first tower section. Note: design of special tower must consider all circumstances specified as per Employer Requirements
11.01 | Type 400DE Tower Basic bodyand crossarms ± 0 m body extension + 0 m leg extensions | per tower | 0 |  |  | 0 | 0
11.02 | Type 400DE Tower 3,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
11.03 | Type 400DE Tower 6,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
11.04 | Type 400DE Tower 9,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
11.05 | Type 400DE Tower 12,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
11.06 | Type 400DE Tower 1,0 m Leg Extension | each | 0 |  |  | 0 | 0
11.07 | Type 400DE Tower 2,0 m Leg Extension | each | 0 |  |  | 0 | 0
11.08 | Type 400DE Tower 3,0 m Leg Extension | each | 0 |  |  | 0 | 0
11.09 | Type 400DE Tower 4,0 m Leg Extension | each | 0 |  |  | 0 | 0
11.1 | Type 400DE Tower 5,0 m Leg Extension | each | 0 |  |  | 0 | 0
11.11 | Stubs for Type 400DE tower | each | 0 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
12 | Complete delivery and installation of terminal tension tower 400DET (0° to 45° angle) as defined in the Scope of Works Erection of hot dip galvanised lattice steel towers according to the design including stubs, stub extensions, leg extensions, earthing connections and measuring of earth resistance and submittance of record to Employer/ Engineer, warning and danger plates, bird guard protections, number plates, phase plates, circuit plates, aerial plates, step bolts, all necessary fittings, and all connections to the insulator strings. Securing against vandalism by punching of bolts for leg extensions and first tower section. Note: design of special tower must consider all circumstances specified as per Employer Requirements
12.01 | Type 400DET Tower Basic bodyand crossarms ± 0 m body extension + 0 m leg extensions | per tower | 2 |  |  | 0 | 0
12.02 | Type 400DET Tower 3,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
12.03 | Type 400DET Tower 6,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
12.04 | Type 400DET Tower 9,0 m Body Extension (only) | each | 0 |  |  | 0 | 0
12.05 | Type 400DET Tower 1,0 m Leg Extension | each | 2 |  |  | 0 | 0
12.06 | Type 400DET Tower 2,0 m Leg Extension | each | 2 |  |  | 0 | 0
12.07 | Type 400DET Tower 3,0 m Leg Extension | each | 1 |  |  | 0 | 0
12.08 | Type 400DET Tower 4,0 m Leg Extension | each | 0 |  |  | 0 | 0
12.09 | Type 400DET Tower 5,0 m Leg Extension | each | 0 |  |  | 0 | 0
12.1 | Stubs for Type 400DET tower | each | 8 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
13 | TOWER LOAD TESTS AND FAT Tower Factory Acceptance Test (FAT)and Type test to ultimate loading including, supply, erection and dismantling. The test shall include a minimum of 6 (six) combination of loading cases, the testing station shall be accredited internatinally to be used for tower test and all cost for Employer's inspector during test shall be as per Employer's Requirements.
13.01 | Tower type 400DA | Lot | 1 |  |  | 0 | 0
13.02 | Tower type 400DB | Lot | 1 |  |  | 0 | 0
13.03 | Tower type 400DC | Lot | 1 |  |  | 0 | 0
13.04 | Tower type 400DD | Lot | 1 |  |  | 0 | 0
13.05 | Tower type 400DE | Lot | 0 |  |  | 0 | 0
13.06 | Tower type 400DET | Lot | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
14 | Earthing 400 kV Double circuit OHTL Installation Works - tower groundings including excavation, laying of counterpoise, connection to towers including all clamps and other connections, corrosion protection, backfilling, compaction and measuring of ohmic value. The protection against corrosion of chemical attack to the earthing systems shall be taken into consideration as specified Employer Requirements Sections VII.
14.01 | Installation of counterpoise conductor over the first 1.5 km, or 5 spans, whichever is longer, of the line route out of any substation, all towers, including the terminal tower, shall be connected together by continuous counterpoise cable, which also shall be connected to the substation earthing grid including CCS40 copper clad steel wire strand 7 No.7 AWG, bolted tower connector clamp, C-tap compression connectors as specified in Employers Requirements. | km | 1.5
14.02 | Installation of Supply of material for Earthing Type A, as specified in Employers Requirements. | each | 39 |  |  | 0 | 0
14.03 | Installation of Supply of material for Earthing Type B, as specified in Employers Requirements. | each | 27 |  |  | 0 | 0
14.04 | Installation of Supply of material for Earthing Type C, as specified in Employers Requirements. | each | 8 |  |  | 0 | 0
14.05 | Installation of Earthing enhancements for Type D where required as per specification to achieve specified tower footing resistance | each | 4 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
15 | Insulator and Fittings 400 kV Double circuit OHTL LINE CONDUCTOR INSULATORS AND FITTINGS Installation of Complete Insulator Sets including insulators, all types of clamps, armour rods, extension links, pilot insulator sets, counterweights and all connections to Tower. All cost for Employer's inspector during test shall be covered as per Schedule of Guarantee Characteristics. NOTE; Arcing horns shall be suitable/adjusted for the operating voltage 330kV, about 2km out from Nakonde Stepdown substation.
15.01 | Single Suspension insulator set for twin "Bluejay" conductor including all clamps and fittings, armour rods and connections to tower, arcing rings both ends | each | 162 |  |  | 0 | 0
15.02 | Double Suspension insulator set for twin "Bluejay" conductor including all clamps and fittings, armour rods and connections to tower, arcing rings both ends. | each | 24 |  |  | 0 | 0
15.03 | Double Tension insulator set for twin "Bluejay" conductor including all clamps and fittings, armour rods and connections to tower, arcing rings both ends | each | 96 |  |  | 0 | 0
15.04 | Twin spacer damper for "Bluejay" conductor bundle | each | 1404 |  |  | 0 | 0
15.05 | Counter weights for reduction of insulator swing | each | 12 |  |  | 0 | 0
15.06 | Factory acceptance tests (FAT) for Insulators as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
15.07 | Factory acceptance tests (FAT) Fittings and Acceories for Insulator as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
15.08 | Test for arcing horn as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
15.09 | Type Test for Insulator Strings as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
15.1 | Fall Arrest System | set | 5 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
16 | CONDUCTOR , OPGW AND GROUND WIRES Supply, stringing and installation including all joints, sleeves, jumper loops, spacers and necessary dampers, earthing connections and all downleads as per Employers Requirements. All cost for Employer's inspector during test shall be covered as per Employers Requirements
16.01 | ACSR Conductor code name Bluejay; twin bundled, stringing of double circuit | route km | 15 |  |  | 0 | 0
16.02 | Optical Ground Wire (OPGW) type ACSR 95/55, 48 cores (24+24), ITU-T G.655 and ITU-T G.652D s/c rating 200 kA2/sec, including all splicing and connections to joint boxes. | route km | 15 |  |  | 0 | 0
16.03 | Earth Wire (OHGW) type ACSR 95/55 | route km | 15 |  |  | 0 | 0
16.04 | Stockbridge type vibration dampers for Bluejay conductor | each | 1128 |  |  | 0 | 0
16.05 | Stockbridge type vibration dampers for OPGW type ACSR 95/55 | each | 153 |  |  | 0 | 0
16.06 | Stockbridge type vibration dampers for Earth Wire type ACSR 95/55 | each | 94 |  |  | 0 | 0
16.07 | Mid - span tension joint for Bluejay conductor | each | 93 |  |  | 0 | 0
16.08 | Mid - span tension joint for Earth Wire OHGW type ACSR 95/55 | each | 4 |  |  | 0 | 0
16.09 | Repair sleeve for Bluejay conductor | each | 9 |  |  | 0 | 0
16.1 | Type test, Conductors as per Employer Requirement section VII Part II | Lot | 1 |  |  | 0 | 0
16.11 | Type test , OPGW as per Employer Requirement section VII Part II | Lot | 1 |  |  | 0 | 0
16.12 | Type test, OHGW conductors as per Employer Requirement section VII Part II | Lot | 1 |  |  | 0 | 0
16.13 | Factory acceptance tests (FAT), Conductor test as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.14 | Factory acceptance tests (FAT), OPGW test as per Employer Requirement; Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.15 | Factory acceptance tests (FAT), Earth wire (OHGW) test as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.16 | Factory acceptance tests (FAT), for space damper as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.17 | Factory acceptance tests (FAT), for vibration damper as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.18 | Factory acceptance tests (FAT), on suspension clamp for Bluejay conductor as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.19 | Factory acceptance tests (FAT), on tension clamp for Bluejay conductor as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.2 | Factory acceptance tests (FAT), on suspension clamp for overhead ground wire as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.21 | Factory acceptance tests (FAT), on tension clamp for overhead ground wire as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
16.22 | Factory acceptance tests (FAT), Test for joint sleeves for Condutor and Earth wire (OHGW) as per Employer Requirement, Section VII, Part II | Lot | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
17 | OPGW AND OVER HEAD GROUND WIRE FITTINGS AND ACCESSORIES Installation of complete Sets of Fittings, including all types of clamps, extension links, armor rods, counterweights, earth bonds and all connections to Tower. All cost for Employer's inspector during test shall be covered as per Employers Requirement section VII Part II.
17.01 | Suspension set for OPGW | each | 31 |  |  | 0 | 0
17.02 | Straight through double tension set for OPGW | each | 14 |  |  | 0 | 0
17.03 | Double dead end tension set, including down the tower connection to joint box on suspension or tension tower for OPGW | each | 8 |  |  | 0 | 0
17.04 | Tension terminal dead end down set for OPGW | each | 2 |  |  | 0 | 0
17.05 | Jointing Box for OPGW/OPGW, for use within the transmission line, including fixing, splicing and downlead clamps, with feed through sets, suitable for up to 48 cores. ITU-T G.655 and ITU 652D s/c rating 200 kA2/sec and OPGW, types as per specification | each | 4 |  |  | 0 | 0
17.06 | 4 way Jointing Box for OPGW/OPGW/OFC, for use within the transmission line, including fixing, splicing and downlead clamps, with feed through sets, suitable for up to 48 cores. ITU-T G.655 and ITU 652D s/c rating 200 kA2/sec and OPGW, types as per specification | each | 2 |  |  | 0 | 0
17.07 | Terminal Box for OPGW/OFC, for the connection at substation gantry, including fixing, splicing and downlead clamps, for up to 48 cores. ITU-T G.655 and ITU G-652D s/c rating 200 kA2/sec and OPGW/OFC, types as per specification | each | 2 |  |  | 0 | 0
17.08 | Suspension set for Earth Wire (OHGW) | each | 31 |  |  | 0 | 0
17.09 | Straight through double tension set for Earth Wire (OHGW) | each | 14 |  |  | 0 | 0
17.1 | Double dead end tension set, including down the tower connection to joint box on suspension or tension tower for Earth Wire (OHGW) | each | 8 |  |  | 0 | 0
17.11 | Tension terminal dead end down set for Earth Wire (OHGW) | each | 2 |  |  | 0 | 0
17.12 | Factory acceptance tests (FAT), Test on joint boxes and splices for Optical Fibre as per TS-1 | Lot | 1 |  |  | 0 | 0
17.13 | FAT Fittings & Accessories for OHGW | Lot | 1 |  |  | 0 | 0
17.14 | FAT Fittings & Accessories for OPGW | Lot | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
18 | Site Offices
18.01 | Site offices for the Engineer / Employer’s staff at site, fully furnished as described in Section VII of the Bidding Documents - Employer Requirements section VII part II. Note: Shall be included in the 330 kV Kasama-Nakonde line Price Schedule. | Lot | 0 |  |  | 0 | 0
18.02 | Office equipment as per Table 3 in the Bidding Documents - Employer's Requirements section VII part II. Note: Shall be included in the 330 kV Kasama-Nakonde line Price Schedule. | Lot | 0 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
19 | As Built documentation
19.01 | All necessery as built documentation including drawings, data sheets, maps maintenance instructions, spare part list etc. | Lot | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
20 | Testing and commissioning
20.01 | Testing, final inspection, Energizing and commissioning | Lot | 1 |  |  | 0 | 0
| SUB-TOTAL |  |  |  |  | 0 | 0
| TOTAL SCHEDULE 4, CARRIED TO SUMMARY |  |  |  |  | 0 | 0
Name of Bidder
Signature of Bidder
2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies

## 5 GRAND SUMMARY
400kV Nakonde-Tanzania border Double-Circuit Overhead Transmission Line (NT)
SCHEDULE: No. 5 Grand Summary
Item | Description | Total Price¹
|  | Local (ZMW) | Foreign [Specify Currency]
¹ Specify currency in accordance with requirements stipulated in Bid Data Sheet under ITB 18.1 & 18.2.
| Total Schedule No. 1. Plant, and Mandatory Spare Parts Supplied from Abroad |  | 0
| Total Schedule No. 2. Plant, and Mandatory Spare Parts Supplied from Within the Employer’s Country | 0
| Total Schedule No. 3. Design Services | 0 | 0
| Total Schedule No. 4. Installation and Other Services | 0 | 0
| Total | 0 | 0
Name of Bidder
Signature of Bidder
1 Specify currency in accordance with ITB 18. Create and use as many columns for Foreign Currency requirement as there are foreign currencies

## 6 REC. SPARE PARTS
400kV Nakonde-Tanzania border Double-Circuit Overhead Transmission Line (NT)
SCHEDULE No. 6: Recommended Spare Parts and Special Tools
Item No | Description | Qty. | Unit Price2 |  | Total Price2
|  |  | Foreign Parts | Local Parts
|  |  | (CIP - Nakonde) | (EXW, Zambia)
|  |  | [Specify Currency] | (ZMW) | [Specify Currency] | (ZMW)
|  | -1 | -2 | -3 | (1)x(2) | (1)x(3)
| TOTAL, RECOMMENDED SPARE PARTS AND SPECIAL TOOLS |  |  |  | 0 | 0
Name of Bidder
Signature of Bidder
1 Bidders shall enter a code representing the country of origin of all imported plant and equipment.
2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies

## 7 DAYWORK RATES
400kV Nakonde-Tanzania border Double-Circuit Overhead Transmission Line (NT)
SCHEDULE No. 7 - Dayworks Rates (Not for Evaluation)
7 | DAYWORK RATES | QTY | UOM | UNIT RATE
7.1 | Prices for miscellaneous steel work, prices for special towers, special extensions and modifications (inclusive of design)
7,1,1 | Structural high yield steel | 1 | tonne
7,1,2 | Structural mild steel | 1 | tonne
7.2 | Miscellaneous prices for foundation work inclusive of design
7,2,1 | Special foundation work including pile caps, beams and modifications to normal foundations to adapt specified foundation classes to cater for particular soil conditions.
7,2,1,1 | Lean concrete (grade C12/15), including formwork | 1 | cubic m.
7,2,1,2 | Reinforced concrete (grade C30/37), including formwork | 1 | cubic m.
7,2,1,3 | Excavation in normal soils (including reinstatement) | 1 | cubic m.
7,2,1,2 | Excavation in hard rock, excluding class 1 foundations (including reinstatement) | 1 | cubic m.
7,2,1,5 | Steel reinforcement bars including supply, bending and placing | 1 | tonne
7,2,1,6 | Imported backfill | 1 | cubic m.
7,2,1,7 | Rip-rap stone work, 0.5m deep over tower base area to protect against erosion | 1 | square meter
7,2,1,8 | 1m x 1m x 2m rock filled gabion baskets, installed, to protect foundations against erosion | 1 | linear m.
7.3 | Transmission Line Diversions: Complete profile survey and setting out of a diversion to the original line route including preparation of profiles and drawings, including complete ground line and conductor clearance checks, selection of tower types, pegging of tower positions, preparation of diagonal profiles including sub-soil investigations. | 1 | Route km
7.4 | Transmission Line Diversions: Route clearance and construction of all required access and maintenance roads | 1 | Route km
7.5 | Galvanized steel gates to be installed where access routes cross fenced property boundaries | 1 | Lot
7.6 | 200mm wearing coarse layer to be installed on access roads | 1 | km
7.7 | Cost of earthing metallic roofs of buildings | 1 | per building
7.8 | Cost of earthing metallic fences | 1 | per connection
7.9 | Special Foundations Rates (Not classified under foundation classes 1 - 6)
7.9.1 | Additional depth concrete (m³) | 1 | (m³)
7.9.2 | Rock excavation (m³) | 1 | (m³)
7.9.3 | Micro‑piles (m) | 1 | m
7.9.4 | Soil improvement (m³) | 1 | (m³)
7.9.5 | Dewatering (LS per location) | 1 | LS per location
7.9.6 | Re‑spotting (each) | 1 | each
Name of Bidder
Signature of Bidder

## Price Adjustment
Price Adjustment
If price adjustment applies in accordance with ITB 17.9, the Bidder shall indicate the sources of indices and source of exchnage rate (if applicable) and the base date indices in its Bid.
Item | Source of Indices | Base date Indices | Source of exchange rate (if applicable)
Name of Bidder: _________________
Signature of Bidder: __________________