BIDDING DOCUMENT

___________________________________

TENDER NO. ZESCO/002/2024

TENDER FOR ENGINEERING, PROCUREMENT AND CONSTRUCTION (EPC) WORKS OF COPPERBELT NETWORK REINFORCEMENT PROJECT (LOT A) -  ZESCO LIMITED

ZESCO Limited

Stand Number 6949

Great East Road

P. O Box 33304

Lusaka, Zambia

Tel: 260 211 223971

Fax: 260 211 223971

Part 2: Employers Requirements: Substations

JANUARY 2024

SECTION I	SCOPE OF WORK AND SUPPLY	3

SECTION II	GENERAL SPECIFICATIONS OF FACILITIES	510

SECTION III	GENERAL TECHNICAL SPECIFICATIONS	520

SECTION IV	PARTICULAR TECHNICAL SPECIFICATIONS	546

SECTION V	PARTICULAR TECHNICAL SPECIFICATIONS, TELECOMMUNICATIONS	674

SECTION VI	TECHINCAL SCHEDULES	686

SECTION VII	PARTICULAR TECHNICAL SPECIFICATIONS: CIVIL WORKS AND STEEL STUCTURE	990

SECTION VIII	STEEL STUCTURE       SPECIFICATIONS	1085

SCOPE OF WORK AND SUPPLY

SECTION I CONTENT

1 SCOPE OF WORK AND SUPPLY	11

1.1 GENERAL	11

1.1.1 Substations on a Turnkey Basis	11

1.2 Luano 330/220kV Substation	11

1.2.1 Power Equipment	12

1.2.2 Substation Automation, Control and Protection	14

1.2.3 Metering	15

1.2.4 Structural Steelwork and Civil Works	16

1.2.5 Telecommunications	17

1.3 Chingola 330/132/33kV Substation	19

1.3.1 Power Equipment	19

1.3.2 Substation Automation, Control and Protection	28

1.3.3 Metering	32

1.3.4 Structural Steelwork and Civil Works	34

1.3.5 Telecommunications	36

1.4 Refractory 132/11kV Substation	39

1.4.1 Power Equipment	40

1.4.2 Substation Automation, Control and Protection	44

1.4.3 Metering	47

1.4.4 Structural Steelwork and Civil Works	48

1.4.5 Telecommunications	50

1.5 Nchanga 132/33/11kV Substation	52

1.5.1 Power Equipment	52

1.5.2 Substation Automation, Control and Protection	59

1.5.3 Metering	62

1.5.4 Structural Steelwork and Civil Works	63

1.5.5 Telecommunications	65

1.6 Kabundi 132/33/11kV Substation	67

1.6.1 Power Equipment	67

1.6.2 Substation Automation, Control and Protection	74

1.6.3 Metering	77

1.6.4 Structural Steelwork and Civil Works	79

1.6.5 Telecommunications	81

1.7 Lulamba 33/11kV Substation	82

1.7.1 Power Equipment	83

1.7.2 Substation Automation, Control and Protection	86

1.7.3 Metering	89

1.7.4 Structural Steelwork and Civil Works	90

1.7.5 Telecommunications	92

1.8 Fitobaula 33/11kV Substation	93

1.8.1 Power Equipment	94

1.8.2 Substation Automation, Control and Protection	97

1.8.3 Metering	99

1.8.4 Structural Steelwork and Civil Works	100

1.8.5 Telecommunications	102

1.9 Mulonga 33kV Switching Station	104

1.9.1 Power Equipment	104

1.9.2 Substation Automation, Control and Protection	106

1.9.3 Metering	107

1.9.4 Structural Steelwork and Civil Works	108

1.9.5 Telecommunications	110

1.10 Chililabombwe 132/33/11kV Substation	111

1.10.1 Power Equipment	112

1.10.2 Substation Automation, Control and Protection	118

1.10.3 Metering	121

1.10.4 Structural Steelwork and Civil Works	123

1.10.5 Telecommunications	124

1.11 Kakoso 132/33/11kV Substation	126

1.11.1 Power Equipment	127

1.11.2 Substation Automation, Control and Protection	133

1.11.3 Metering	137

1.11.4 Structural Steelwork and Civil Works	138

1.11.5 Telecommunications	140

1.12 Chililabombwe Central 33/11kV Substation	142

1.12.1 Power Equipment	142

1.12.2 Substation Automation, Control and Protection	146

1.12.3 Metering	148

1.12.4 Structural Steelwork and Civil Works	149

1.12.5 Telecommunications	151

1.13 Chililabombwe North 33/11kV Substation	152

1.13.1 Power Equipment	153

1.13.2 Substation Automation, Control and Protection	156

1.13.3 Metering	158

1.13.4 Structural Steelwork and Civil Works	160

1.13.5 Telecommunications	161

1.14 Kawama 33/11kV Substation	163

1.14.1 Power Equipment	163

1.14.2 Substation Automation, Control and Protection	167

1.14.3 Metering	169

1.14.4 Structural Steelwork and Civil Works	170

1.14.5 Telecommunications	172

1.15 Kasumbalesa 33/11kV Substation	173

1.15.1 Power Equipment	174

1.15.2 Substation Automation, Control and Protection	177

1.15.3 Metering	179

1.15.4 Structural Steelwork and Civil Works	181

1.15.5 Telecommunications	183

1.16 Mwambashi132/33kV Substation	184

1.16.1 Power Equipment	185

1.16.2 Substation Automation, Control and Protection	191

1.16.3 Metering	194

1.16.4 Structural Steelwork and Civil Works	196

1.16.5 Telecommunications	198

1.17 New Kitwe 132/33/11kV Substation	200

1.17.1 Power Equipment	200

1.17.2 Substation Automation, Control and Protection	206

1.17.3 Metering	210

1.17.4 Structural Steelwork and Civil Works	211

1.17.5 Telecommunications	213

1.18 New Chimwemwe 33/11kV Substation	215

1.18.1 Power Equipment	215

1.18.2 Substation Automation, Control and Protection	219

1.18.3 Metering	221

1.18.4 Structural Steelwork and Civil Works	222

1.18.5 Telecommunications	224

1.19 New Scaw 33/11kV Substation	226

1.19.1 Power Equipment	226

1.19.2 Substation Automation, Control and Protection	230

1.19.3 Metering	232

1.19.4 Structural Steelwork and Civil Works	233

1.19.5 Telecommunications	235

1.20 Nkana Mine 33/11kV Substation	236

1.20.1 Power Equipment	237

1.20.2 Substation Automation, Control and Protection	241

1.20.3 Metering	243

1.20.4 Structural Steelwork and Civil Works	244

1.20.5 Telecommunications	246

1.21 Nkana East 33/11kV Substation	247

1.21.1 Power Equipment	248

1.21.2 Substation Automation, Control and Protection	251

1.21.3 Metering	253

1.21.4 Structural Steelwork and Civil Works	255

1.21.5 Telecommunications	257

1.22 Luangwa 33/11kV Substation	258

1.22.1 Power Equipment	259

1.22.2 Substation Automation, Control and Protection	262

1.22.3 Metering	264

1.22.4 Structural Steelwork and Civil Works	266

1.22.5 Telecommunications	268

1.23 Kalulushi 132/33/11kV Substation	269

1.23.1 Power Equipment	270

1.23.2 Substation Automation, Control and Protection	276

1.23.3 Metering	279

1.23.4 Structural Steelwork and Civil Works	281

1.23.5 Telecommunications	282

1.24 Kalulushi North 33/11kV Substation	284

1.24.1 Power Equipment	285

1.24.2 Substation Automation, Control and Protection	288

1.24.3 Metering	290

1.24.4 Structural Steelwork and Civil Works	292

1.24.5 Telecommunications	294

1.25 New Chibuluma 33/11kV Substation	295

1.25.1 Power Equipment	296

1.25.2 Substation Automation, Control and Protection	299

1.25.3 Metering	301

1.25.4 Structural Steelwork and Civil Works	303

1.25.5 Telecommunications	305

1.26 Lwamisamba 33/11kV Substation	306

1.26.1 Power Equipment	306

1.26.2 Substation Automation, Control and Protection	310

1.26.3 Metering	312

1.26.4 Structural Steelwork and Civil Works	313

1.26.5 Telecommunications	315

1.27 Kalulushi Airport 33/11kV Substation	317

1.27.1 Power Equipment	317

1.27.2 Substation Automation, Control and Protection	321

1.27.3 Metering	323

1.27.4 Structural Steelwork and Civil Works	324

1.27.5 Telecommunications	326

1.28 Chambishi East 330/132/33kV Substation	328

1.28.1 Power Equipment	328

1.28.2 Substation Automation, Control and Protection	333

1.28.3 Metering	336

1.28.4 Structural Steelwork and Civil Works	337

1.28.5 Telecommunications	339

1.29 Chambishi Primary 33/11kV Substation	341

1.29.1 Power Equipment	342

1.29.2 Substation Automation, Control and Protection	345

1.29.3 Metering	347

1.29.4 Structural Steelwork and Civil Works	349

1.29.5 Telecommunications	351

1.30 Musonda 33/11kV Substation	352

1.30.1 Power Equipment	352

1.30.2 Substation Automation, Control and Protection	356

1.30.3 Metering	358

1.30.4 Structural Steelwork and Civil Works	359

1.30.5 Telecommunications	361

1.31 Mufulira 132/33kV Substation	362

1.31.1 Power Equipment	363

1.31.2 Substation Automation, Control and Protection	368

1.31.3 Metering	371

1.31.4 Structural Steelwork and Civil Works	372

1.32 Mufulira West 33/11kV Substation	374

1.32.1 Power Equipment	375

1.32.2 Substation Automation, Control and Protection	378

1.32.3 Metering	380

1.32.4 Structural Steelwork and Civil Works	382

1.32.5 Telecommunications	384

1.32.6 Telecommunications	385

1.33 Nsato 33/11kV Substation	387

1.33.1 Power Equipment	387

1.33.2 Substation Automation, Control and Protection	391

1.33.3 Metering	393

1.33.4 Structural Steelwork and Civil Works	394

1.33.5 Telecommunications	396

1.34 Ndeke 33/11kV Substation	398

1.34.1 Power Equipment	398

1.34.2 Substation Automation, Control and Protection	402

1.34.3 Metering	404

1.34.4 Structural Steelwork and Civil Works	405

1.34.5 Telecommunications	407

1.35 Mokambo 33/11kV Substation	408

1.35.1 Power Equipment	409

1.35.2 Substation Automation, Control and Protection	412

1.35.3 Metering	415

1.35.4 Structural Steelwork and Civil Works	416

1.35.5 Telecommunications	418

1.36 Lufwanyama 132/33kV Substation	419

1.36.1 Power Equipment	420

1.36.2 Substation Automation, Control and Protection	425

1.36.3 Metering	428

1.36.4 Structural Steelwork and Civil Works	429

1.36.5 Telecommunications	431

1.37 Funda 33/11kV Substation	433

1.37.1 Power Equipment	433

1.37.2 Substation Automation, Control and Protection	437

1.37.3 Metering	439

1.37.4 Structural Steelwork and Civil Works	440

1.37.5 Telecommunications	442

1.38 E1 Switching Station	444

1.38.1 Power Equipment	444

1.38.2 Substation Automation, Control and Protection	445

1.38.3 Metering	447

1.38.4 Structural Steelwork and Civil Works	448

1.38.5 Telecommunications	449

1.39 North Hospital Switching Station	451

1.39.1 Power Equipment	451

1.39.2 Substation Automation, Control and Protection	452

1.39.3 Metering	454

1.39.4 Structural Steelwork and Civil Works	454

1.39.5 Telecommunications	456

1.40 General Offices Switching Station	457

1.40.1 Power Equipment	458

1.40.2 Substation Automation, Control and Protection	459

1.40.3 Metering	460

1.40.4 Structural Steelwork and Civil Works	461

1.40.5 Telecommunications	463

1.41 Scaw Factory Switching Station	464

1.41.1 Power Equipment	465

1.41.2 Substation Automation, Control and Protection	466

1.41.3 Metering	467

1.41.4 Structural Steelwork and Civil Works	468

1.41.5 Telecommunications	470

1.42 UBZ Switching Station	471

1.42.1 Power Equipment	471

1.42.2 Substation Automation, Control and Protection	473

1.42.3 Metering	474

1.42.4 Structural Steelwork and Civil Works	475

1.42.5 Telecommunications	477

1.43 N48 Switching Station	478

1.43.1 Power Equipment	478

1.43.2 Substation Automation, Control and Protection	479

1.43.3 Metering	481

1.43.4 Structural Steelwork and Civil Works	481

1.43.5 Telecommunications	483

1.44 Women Welfare Switching Station	485

1.44.1 Power Equipment	485

1.44.2 Substation Automation, Control and Protection	486

1.44.3 Metering	487

1.44.4 Structural Steelwork and Civil Works	488

1.44.5 Telecommunications	490

1.45 Kankoyo Switching Station	491

1.45.1 Power Equipment	492

1.45.2 Substation Automation, Control and Protection	493

1.45.3 Metering	494

1.45.4 Structural Steelwork and Civil Works	495

1.45.5 Telecommunications	497

1.46 Kansunswa 33/11kV Substation	499

1.46.1 Power Equipment	499

1.46.2 Substation Automation and Control	503

1.46.3 Metering	505

1.46.4 Structural Steelwork and Civil Works	506

1.46.5 Telecommunications	508

# SCOPE OF WORK AND SUPPLY

## GENERAL

The Bidder shall examine the specifications of this section in close connection with the other documents and particulars forming these Bid Documents.

Special attention shall be paid to General Specification of Facilities and Particular Technical Specifications, in which the general technical requirements are specified. The drawings in “drawings section” are for tendering purpose only.

If the Specifications and/or Drawings do not contain particulars of materials or works which are necessary for the proper and safe completion, operation, and maintenance of the equipment in question, all such materials and works shall be deemed to be included in the supply for the turn-key based substations.

In the event of any difference between the Drawings and the Specifications, the latter shall prevail.

In the event of any difference between scaled dimensions and figures on the Drawings, the figures shall prevail.

Should the Bidder find discrepancies in or omissions from these Specifications or from the other Documents, or should he be in doubt as to their meaning, he should immediately contact the Project Manager for interpretation, clarification, or correction thereof before submitting his Bid. Such action shall, however, in no case be considered as a cause for altering the closing date of the Bid.

Items described as optional in the scope of works can be left out or included during the contract negotiations, the only price consequences being the item prices themselves.

### Substations on a Turnkey Basis

The Facilities shall cover engineering design, manufacture, testing before shipment, packing seaworthy or otherwise as required, transport from work to port of shipment, delivery DDP, transport from port of delivery to site, erection, installation, pre-commissioning testing and commissioning of all equipment as specified in the preceding chapters for the substations. The Facilities shall also cover Civil Works.

## Luano 330/220kV Substation

The acquired substation land is 500mx500m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Luano substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 330kV voltage level. The 330kV bus bar installation will allow for ease of additional future installations for two (2) future 330kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The scope of work shall be but not limited to:

- Extension of the 330kV busbar to accommodate Chingola 2x 330kV line bays.

- Rearranging of the existing Chambishi East and Kabwe 330kV line bays to create space for Chingola 2x 330kV line bays to between the existing Kansanshi 330kV line bay and the existing 66kV Kasompe line bay

- Integration works for 2x 330kV line bays

- Associated civil works, foundations, and steel gantry structures for the new bay equipment.

### Power Equipment

      - 2 no’s 330 kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl 0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for busbar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying busbars and for the connections to and between the apparatus and to the feeder and the busbars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying busbars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal towers of transmission line to substation line bay.

Note: There shall be a provision for one (1) unequipped 330kV future line bay.

      - 2 no’s 330 kV Busbars (main and reserve) consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 330 kV     conductors.

      - 1 lot Extension of the substation earthing and lightning protection system to the new bays

      - 1 lot extension and integration of the control and protection system to accommodate the new bays.

      - 1 lot Control Cables and fittings for all substation secondary Equipment.

      - SF6 gas equipment comprising the following:

        - 1 set per Substation of SF6 gas filling equipment

        - 1 set of SF6 leak detector equipment.

        - 1 x 45 kg SF6 gas bottle filled with Sf6 gas.

The gas treatment plant(s) to be supplied shall have sufficient storage facilities for the maximum quantity of gas that could be removed when carrying out maintenance or repair work on the largest section of the switchgear.

All the necessary pipes, couplings, flexible tubes, and valves for coupling to the switchgear for filling or evacuating all the gases to be used, with all necessary instructions for the storage of this equipment, shall be provided.

      - Installation of item 1.2.1.1 to item 1.2.1.4

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control and protection system for the two Luano - Chingola 330kV lines for the extension of the 330kV system, top of range IEC 61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works.

- Design, Supply, install, test, and commission 2Nos. 330kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system to consist of the of:

- Line Differential Protection (main 1) on optic fibre.

- Line Distance Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Carry out system integration for all the new 330kV system Control and Protection IEDs into the existing Substation Automation System. The existing SAS is the PCS-9700 by NR Electric. It is based on the IEC61850-8-1 communication Protocol and was commissioned in 2015. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out the necessary modifications of the SAS and protection systems taking into account any reconfiguration of the primary circuits in the substation.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems

- Design and supply and install equipment for the extension of the existing Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the existing LAN architecture.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs.

- Design and supply spare adequate SAS spares (BCUs, LAN Switches, etc.) for the station.

- Design and Supply, install required equipment for integration of new circuits into existing Fault recorder system for the 330kV system. Commission new circuits in Fault recorder system.

- Integrate the new 330kV line bays into the existing 330kV busbar protection type NR PCS915S.

- Integrate the new 330kV line bays into the existing Protection Management System

- Integrate the new 330kV line bays into the existing 330kV Fault recorder.

### Metering

The metering system shall comprise but not limited to the following.

      - 4 nos Digital Programmable Energy import and export Meter for the 330kV lines, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES [These meters are for statistical purposes and line performance assessments only]

      - All energy meters shall be installed in the meter enclosure segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system. The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 4no’s Programmable Transducer Class 0.2 c/w software for 330kV lines monitoring of measurands to NCC.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of item 1.2.4.1 to item 1.2.4.7

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lightning mast, security light masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently. Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

Supply of optical fibre approach cables from the gantries on (330kV and 132kV line bays) Chingola line bay to the telecoms room.

      - Optical Transport Network (OTN) equipment with the following characteristics/requirements

- Not less than 4000G of transmission capacity in all directions

- The equipment must be able to transmits for distances of over 300km without any signal degradation.

- The equipment must have cross connection capabilities.

- Must be open for integration and monitoring on the already operational ZTE Network Management System (NMS)

- The equipment must be linked to the already operational ZXONE9700 equipment at substations.

- Service interface modules:

        - 2 x 155M – 2.5G Modules/Cards

        - 2 x 10G Modules/Cards

        - 3 x 100G Modules/Cards

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - One (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x 4 port OPIC (With Multi Mode SFP)

- 1x 4 port OPIC (with single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - 1 PCM Access Multiplexer with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fibre Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Chingola 330/132/33kV Substation

The acquired substation land is 500mx500m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Chingola substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 330kV and 132kV voltage levels. The 33kV busbars will be single busbars. The 330kV bus bar installation will allow for ease of additional future installations for two (2) future 330kV and two (2) 132kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (3) 330/132/11kV, 160MVA Transformers and three (3) 132/33kV power transformers.

The scope of work shall be but not limited to:

### Power Equipment

      - 4 no’s 330 kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl 0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for busbar protection PX.

        - 3 (three) lightning arresters, each with a six digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying busbars and for the connections to and between the apparatus and to the feeder and the busbars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying busbars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal towers of transmission line to substation line bay.

Note: There shall be a provision for one (1) unequipped 330kV future line bay.

      - 1 no’s 330 kV bus coupler bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switch complete with local position indication and operating cubicle  with integral earth switch (circuit breaker line isolator).

        - 2 sets by 3 (three) single-phase current transformers, each with 6 cores, one set on each side of the bus coupler. Two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection Cl X.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying conductors and for the connections to and between the apparatus and bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 330 kV bus section bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switch complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 2 sets by 3 (three) single-phase current transformers, each with 6 cores, one set on each side of the bus coupler. Two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection Cl X.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying conductors and for the connections to and between the apparatus and bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 3 no’s 330 kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker transformer isolator).

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle (circuit breaker busbar isolator).

        - 3 (three) current transformers each with six cores, two cores for     transformer protection 5P20, one for metering class 1 and two     cores for busbar protection (class X), one spare Metering core class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio  kV, each with two windings, one and one Cl0.2s.

        - 3 (three) lightning arresters, each with six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer               bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 330kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting  clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped 330kV future transformer bay.

      - 2 no’s 330 kV Busbars (main and reserve) consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 330 kV     conductors.

        - 2 no’s set of 3 (three) single-phase capacitive voltage     transformers for main and reserve bus bars. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

      - 3 no’s 330/132/11kV power transformers:

Rated voltage:	330/132/11kV (+10, -10 x1.5%)

Rated power:	125/160/5MVA.

Vector group:	YNyn0d1

Cooling:	ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Busbars (main and reserve) each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 nos 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 nos 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus. 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 6 no’s 132kV Transformer Bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped 132kV future transformer bay.

      - 10 no’s 132kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20, two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio  kV, each with two windings, one 3P and one Cl 0.5.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for three future 132kV line bays.

      - 3 no’s 132/33kV power transformers:

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power: 31.5/40MVA

Vector group:	Dyn11

Cooling:	ONAN/ONAF

Tap Changer:	On load.

      - 3 no’s 33kV Transformer Bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, one cores for transformer protection 5P20 one for metering 0.2S and one cores for differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers, ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped 33kV future transformer bay.

      - 1 no’s 33 kV Busbars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two windings, one for measuring Cl0.2s and one for protection 5P20. Ratio  kV, to be installed on different phases.

        - 1 (one) 33kV three-phase isolating switch complete with local position indication and operating cubicle.

- 1 no 33kV Bus section Bay consisting of:

- 1 (one) SF6 three-phase circuit breaker with operating cubicle.

- 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

- 3 (three) current transformers each with three cores, two cores for protection and one for metering.

- 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

- 1 (one) cable marshalling kiosk.

- 1 Lot post insulators.

- 1 (one) complete set of three-phase line including clamps for    the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

- 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 2 no’s 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two future 33kV line bays.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 3nos Neutral Current Transformers for main Transformers; 330kV and 132kV sides for the 330/132kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary Equipment.

      - SF6 gas equipment comprising the following:

        - 1 set per substation of SF6 gas filling equipment

        - 1 set of SF6 leak detector equipment

        - 1 x 45 kg SF6 gas bottle filled with Sf6 gas.

The gas treatment plant(s) to be supplied shall have sufficient storage facilities for the maximum quantity of gas that could be removed when carrying out maintenance or repair work on the largest section of the switchgear.

All the necessary pipes, couplings, flexible tubes, and valves for coupling to the switchgear for filling or evacuating all the gases to be used, with all necessary instructions for the storage of this equipment, shall be provided.

      - 2nos 11/0.4kV 500kVA Transformers Auxiliary transformers complete with 2nos 11kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 1no 500kVA diesel generator complete with accessories.

      - Installation of Item 1.3.1.1 to Item 1.3.1.21.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control and protection system for the 330kV, 132kV and 33kV system, top of range IEC 61850 based.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall provide top-of-the-range Bay Control Units (BCUs), redundant gateways or upstream communication units, redundant station HMI servers, dual operator workstations, single engineering workstation, redundant LAN switches/communication system, legacy protocol converters (where required) and dual DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The Hot-Standby redundant configuration HMIs and Gateways should be implemented on the new control system (which has already been mentioned) should be open and expandable (future proof) and should be IEC-61850 compliant.

Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works.

- Design, Supply, install, test, and commission SAS Panels housing Station Gateways/RTUs, Common alarms BCU, GPS Clock, LAN Switches etc, as per approved design.

- Design, Supply, install, test, and commission a modern IEC-61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Design, Supply, install, test, and commission 4Nos. 330kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Distance Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

The 330kV Line facing Kansanshi substation shall be equipped with a protection system matching the existing system on the remote end at Kansanshi.

- Design, Supply, install, test, and commission 1No. 330kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 3Nos. 330kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Current Differential Protection (main 1).

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 3Nos. 132kV Transformer Incomer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types for the LV side:

- Feeder management relay.

- Bay Control Unit.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, Supply, install, test, and commission 10Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 3Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

Design, Supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 2No. 132kV Bus Sections Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 2Nos. 33kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 2Nos. 11kV Line Bay control and protection panels housing both the protection and bay control IEDs (for Auxiliary Transformer supply). The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 330kV busbar protection system with circuit breaker fail protection function.

- Design and Supply, install and commission a new 132kV busbar protection system with circuit breaker fail protection function.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Design and Supply, install and commission a new Fault recorder for the 330kV system.

- Design and Supply, install and commission a new Protection Management System for the 330kV system.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers (MCB).

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

All protection relays shall be numerical type.

- Design, Supply, install, test, and commission 2 Nos. AVR Systems with a dedicated IEC-61850 compliant IED installed for each of the transformers. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, Supply, install, commission, and test 1 No. Common Alarms Bay Control Unit Panel for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 330kV, 132kV and 33kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with dispatch centres

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Design and supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

### Metering

The metering system shall comprise but not limited to the following.

      - 8 nos Digital Programmable Energy import and export Meter for the 330kV lines, Class 0.2s (kWh/kVArh), single rate tariff,                                              All values read shall be PRIMARY VALUES [These meters are for statistical purposes and line performance assessments only]

      - 6 nos Digital Programmable Energy import and export Meter for each 160MVA; 330/132/11kV transformers, Class 0.2 (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES.  These meters shall be installed on the 132kV side only. [These meters are for statistical purposes only]

      - 6 nos Digital Programmable Energy import and export Meter for each 40MVA; 132/33kV transformers, Class 0.2 (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES.  These meters shall be installed on the 33kV side only. [These meters are for statistical purposes only]

      - 4 Nos Digital programmable energy import and Export meters for each 500kVA; 11/0.4kV Auxiliary Transformers.  Class 0.2 (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 20 Nos Digital Programmable Energy import and export meters for the 132kV lines. Class 0.2 (kWh/kVArh), single rate tariff                                                                                                        All values read shall be PRIMARY VALUES

      - All the energy meters shall be installed in metering enclosures segregated according to voltage levesl

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system. The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software (inclusive of Licences) for both digital programmable energy meters and the remote meter reading system

      - 6 no WTI [Winding Temperature Indicators] for power transformer winding temperature monitoring c/w capillary and probe   These temperature values shall be read locally and remotely.

      - 6 no OTI [Oil Temperature Indicators] for power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - 4no’s Programmable Transducer Class 0.2                                             c/w software for 330kV lines monitoring of measurands to NCC.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of Item 1.3.3.1 to Item 1.3.3.12

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lightning mast, security light masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on (330kV/132 line bays) for Kansanshi, Refractory, Chililabombwe, Nchanga, Lufwanyama, Kabundi line bays to the telecoms room.

      - Optical Transport Network (OTN) equipment with the following characteristics/requirements

- Not less than 4000G of transmission capacity in all directions

- The equipment must be able to transmits for distances of over 300km without any signal degradation.

- The equipment must have cross connection capabilities.

- Must be open for integration and monitoring on the already operational ZTE Network Management System (NMS)

- The equipment must be linked to the already operational ZXONE9700 equipment at substations.

- Service interface modules:

        - 2 x 155M – 2.5G Modules/Cards

        - 2 x 10G Modules/Cards

        - 3 x 100G Modules/Cards

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) Synchronous Digital Hierarchy (SDH) multiplexer with STM-64 optical transmission capacity  and the following interfaces:

- Optical Transmission Modules:

- 2 x 2 ports STM-64

- 4 x 4 ports STM-16

- Service Interfaces:

- 63 x E1 ports

- 2 x 8 ports STM-1

- 8 x 100 Base TX ports (Fast Ethernet - Electrical)

- 8 x 100 Base FX ports (Fast Ethernet – Optical)

- 2 x Gigabit Ethernet ports x 4 control modules

- Engineer’s Order Wire

      - Two (2) FOX 615 STM-16 optical transmission capacity and each with the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - HARDWARE REQUIREMENTS AND RELATED ACCESSORIES

|  | ITEM | QUANTITY |
| --- | --- | --- |
| 1 | The PABX with Basic Modules including the rack with a Cabinet suitable for the installation of the PABX. The cabinet should be equipped with a top fun unit. | 01 |
| 2 | Desktop computer and laptop with suitable specifications for the onsite management of the PBX. | 02 |
| 4 | Terminal block Surge protectors | 30 |
| 2 | Analogue Subscriber Interface channels. | 128 |
| 3 | Digital Subscriber (2B+D) Interface channels | 128 |
| 4 | 2 Mbps (30B+D) Digital ISDN Ports | 04 |
| 5 | 2 Mbps (30B+D) Digital ISDN cards | 02 |
| 6 | Ethernet Interface ports | 02 |
| 7 | 2 – Wire Analogue PSTN Trunk Lines | 4 |
| 8 | Standard Analogue Telephone sets complete with all accessories and line Jacks | 61 |
| 9 | Digital Telephone Sets complete with all accessories and line Jacks. | 42 |
| 10 | IP Telephone Sets complete with all accessories and power supply. | 61 |
| 11 | Operator Consoles | 01 |
| 12 | IP Premium user license | 60 |
| 13 | NPRAE E1 card for NCC Alcatel Crystal hardware PABX for establishing the E1 connectivity with the PABX to be supplied. | 01 |
| 14 | Optical to E1 converters with LC interface | 02 |

|  | ITEM |
| --- | --- |
| 1 | Call Logging and Accounting Software |
| 2 | Voice Mail |
| 3 | Traffic Measurement, Recording and call charge management Software |
| 4 | Maintenance and Management software |
| 5 | H.323 or SIP Client PC Software (Telephony Software) |
| 6 | Relevant Software Licenses |
| 7 | PC for Management Software |
| 8 | Support for network signalling based on QSIG – ITU protocol |
| 9 | Budgetary control software or Prepayment software |
| 10 | Intelligent Call routing |
| 11 | Support of Standard SIP endpoints |
| 12 | Voice-centric system |

      - Two (2) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fibre Equipment installation.

      - Installation of items 2.5.1 to 2.5.9 above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Refractory 132/11kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Refractory substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 11kV board. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV bays and extension of the 11kV board. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (4) 132/11kV, 40MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 4nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for one (1) 132kV unequipped future line bay.

      - 4 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker transformer isolator).

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle (circuit breaker busbar isolator).

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20, one for metering class 1 and two cores for busbar protection (class X), one spare Metering core class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio   kV, each with two windings, one and one Cl0.2s.

        - 3 (three) lightning arresters, each with six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from         the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer              bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV  transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting  clamps, grading devices, etc.

Note: There shall be a provision for one (1) 132kV unequipped future transformer bay.

      - 4 no’s 132/11kV power transformers

Rated voltage:	132/11kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 2 (two) complete sets three phase voltage transformers, with two cores,

        - one for measuring Cl0.5. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 3 (three) bus riser.

        - 1 (one) earthing panel

      - 4 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for protection 5P20, one for metering class 0.2 and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.5.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering.

        - 3 (three) lightning arresters.

      - 3 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 4nos Neutral Current Transformers for the 132/11kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 11kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 4nos earthing resistors complete with accessories for limiting earth fault current to 40MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.4.1.1to Item 1.4.1.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works.

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 4Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 4Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV busbar protection system with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Design, supply, install, test, and commission 4Nos. 11kV Transformer incomer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

Each Transformer main protection system shall include but not limited to the following discrete relays.

- Overcurrent and Earth Fault protection relay for each winding

- Electrically and mechanically resettable tripping Relays

- Trip Circuit Supervision Relay

- Design, supply, install, test, and commission 3No. 11kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Design, supply, install, test, and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 11kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1Nos. AVR Systems with a dedicated IEC-61850 compliant IED installed for each of the transformers. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the enew LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

All protection relays shall be numerical type

### Metering

The metering system shall comprise but not limited to;

      - 8 nos Digital Programmable Energy import and export Meter for the 132kV Chingola and Nchanga lines, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES.                                   [These meters are for statistical purposes and line performance assessments only]

      - 8 nos Digital Programmable Energy import and export Meter for each 40MVA; 132/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES          These meters shall be installed on the 11kV sides only.

      - 8 No Digital Programmable Energy import and export meters for the 11kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                                        All values read shall be PRIMARY VALUES

      - All energy meters shall be installed in metering enclosures segregated according to the voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 4 No WTI [Winding Temperature Indicators] for 4 x 40MVA power transformer winding temperature monitoring c/w capillary and probe.                                                                                                These temperature values shall be read locally and remotely.

      - 4 No OTI [Oil Temperature Indicators] for 4 x 40MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of Item 1.4.3.1 to 10

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits , fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - one (1) PCM Access Multiplexer with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items 3.5.1 to 3.5.9 above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Nchanga 132/33/11kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Nchanga substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (3) 132/11kV, 40MVA transformers and two (2) 132/33kV, 40MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 4nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for one (1) 132kV unequipped future line bay.

      - 5 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker transformer isolator).

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle (circuit breaker busbar isolator).

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20, one for metering class 0.2s and two cores for busbar protection (class X), one spare Metering core class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio kV  , each with two cores, one of which will be Cl0.2s and the other protection 3P.

        - 3 (three) lightning arresters, each with six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from         the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer               bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 132kV unequipped future transformer bay.

      - 2 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 3 no’s 132/11kV power transformers

Rated voltage:	132/11kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch.

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two windings, one for measuring Cl0.2s and one for Protection 3P. Ratio kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 132/33kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four cores, one core for transformer backup protection 5P20, one for metering and two cores for main protection (class X).

        - 3 (three) single-phase voltage transformers.    Ratio 132/√3 to 0.11/√3, each with two windings, one 3P    and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV   transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering 0.2s.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arrester to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV Flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring Cl0.2s and one for Protection 3P. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 2 (one) bus riser.

        - 1 (one) earthing panel

      - 3 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer backup protection 5P20, one for metering class 0.2s and two cores for main protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 6 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with two cores, one core for protection 5P20 and one for metering class 0.2.

        - 3 (three) lightning arresters.

      - 2 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with two cores, one core for protection (5P20) and one for metering class 0.2.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 5nos Neutral Current Transformers for main Transformers; 132kV, 33kV and 11kV sides for the 132/33/11kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 5nos earthing resistors complete with accessories for limiting earth fault current to 40MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.5.1.1 to Item 1.5.1.22

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV, 33kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works;

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

Design, supply, install, test, and commission 4Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 5Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 2No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV busbar protection system with circuit breaker fail protection function

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Design, supply, install, test, and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 3Nos. 11kV Transformer incomer Bay control and protection boards housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

Design, supply, install, test, and commission 2No. 11kV Bus Section Bay control and protection boards housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- 2nos Complete Battery/charger systems consisting of respective.

- 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Design, supply, install, test, and commission 6Nos. 11kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 2 Nos. AVR Systems with a dedicated IEC-61850 compliant IED installed for each of the transformer. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV, 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 8 nos Digital Programmable Energy import and export Meter for the 132kV Chingola and Refractory lines, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES. These meters are for statistical purposes and line performance assessments only]

      - 10 nos Digital Programmable Energy import and export Meter for each 40MVA; 132/33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 11/0.4kV Auxiliary Transformers. Class 0.2 (kWh/kVArh), single rate tariff    All values read shall be PRIMARY VALUES These meters shall be installed on the 11kV sides only.

      - 8 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - 12 No Digital Programmable Energy import and export meters for the 11kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                             All values read shall be PRIMARY VALUES

      - All the smart energy meters shall be installed in metering enclosures segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Item 4.3.8	5 No WTI [Winding Temperature Indicators] for 5 x 40MVA power transformer winding temperature monitoring c/w capillary and probe.                                                                                                These temperature values shall be read locally and remotely.

      - 5 No OTI [Oil Temperature Indicators] for 5 x 40MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 5 x 40MVA Transformer energy meters.

      - Probes and communication software for the 4 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of Item 1.5.3.1 to Item 1.5.3.14

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - Item 4.5.3	One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kabundi 132/33/11kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Kabundi substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 132/33kV, 40MVA transformers and two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 6nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each     with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for two (2) 132kV unequipped future line bay.

      - 2 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker transformer isolator).

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle (circuit breaker busbar isolator).

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20, one for metering class 0.2s and two cores for busbar protection (class X), one spare Metering core class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio kV, each with two windings, one of which will be Cl0.2s.

        - 3 (three) lightning arresters, each with six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from         the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer               bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 132kV unequipped future transformer bay.

      - 2 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two windings, one for measuring Cl0.2s and one for protection 3P. Ratio kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 132/33kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20 one for metering and two cores for protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer protection 5P20 one for metering and one core for protection (class X).

        - 3 (three) single-phase voltage transformers.    Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection and one for metering.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores,

        - one for measuring Cl0.2s and one for Protection 3P. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20, one for metering class 0.2s and two cores for protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 10 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores core for protection (5P20) and one for metering class 0.2.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 4nos Neutral Current Transformers for main Transformers; 132kV, 33kV and 11kV sides for the 132/33/11kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 4nos earthing resistors complete with accessories for limiting earth fault current to transformers full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.6.1.1 to Item 1.6.1.22

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 33kV, 88kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works;

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 6Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 2Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV Busbar Protection System with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- 2nos Complete Battery/charger systems consisting of respective DC distribution boards with section and feeder breakers.

- Design, supply, install, test, and commission 4Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 2Nos. 11kV Transformer incomer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 11kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 10Nos. 11kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 2Nos. AVR Systems with a dedicated IEC-61850 compliant IED installed for each of the transformers. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV, 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 12 nos Digital Programmable Energy import and export Meter for the 132kV Chingola and Refractory lines, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES  [These meters are for statistical purposes and line performance assessments only]

      - 8 nos Digital Programmable Energy import and export Meter for each 40MVA; 132/33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 33/0.4kV Auxiliary Transformers. Class 0.2 (kWh/kVArh), single rate tariff    All values read shall be PRIMARY VALUES These meters shall be installed on the 33kV sides only.

      - 2 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - 20 No Digital Programmable Energy import and export meters for the 11kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                             All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in metering enclosures segregated according voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 5 No WTI [Winding Temperature Indicators] for 5 x 40MVA power transformer winding temperature monitoring c/w capillary and probe.                                                                                                These temperature values shall be read locally and remotely.

      - 5 No OTI [Oil Temperature Indicators] for 5 x 40MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 5 x 40MVA Transformer energy meters.

      - Probes and communication software for the 4 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of Item 1.6.3.1 to Item 1.6.3.14

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers’ laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Lulamba 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Lulamba substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and one for protection 3P. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four cores, two cores for protection 5P20 one for metering and one cores for Differential Protection.

        - 3 (three) single-phase voltage transformers, ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each three cores, two cores core for protection 5P20 and one for metering.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores core for protection 5P20 and one for metering.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20, one core for metering class 0.2 and two cores for main protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one core for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.7.1.1 1.2.1.Item 1.7.1.17

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - Item 6.2.1	1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 4Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, test and commission 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to.

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 4 Nos Digital Programmable Energy import and export meters for 2x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 8 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 8 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of 1.2.1.Item 1.7.3.1 to 1.2.1.Item 1.7.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kVline bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - Item 6.5.4	One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers’ Laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Fitobaula 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Fitobaula substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for three (3) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 nos 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and one for Protection 3P. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four cores, two cores for protection 5P20 one for metering 0.2S and one core for protection (class X).

        - 3 (three) single-phase voltage transformers; Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering 0.2S.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV copper busbars.1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20, one core for metering class 0.2 and two cores for protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.5.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, two for metering class 0.2S.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20), one for metering class 0.2.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of item 1.8.1.1 to item 1.8.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 50kVA; 33/0.4kV Auxiliary Transformers. Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 4 Nos Digital Programmable Energy import and export meters for 4 x 33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 8 x 11kV feeders.  Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe .These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 4 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 1.8.3.1 to 1.8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop with maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Mulonga 33kV Switching Station

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Mulonga Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The Contractor can propose an alternative layout, as long as it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 nos 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and one for Protection 3P. Ratio  kV, to be installed on different phases.

      - 4 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering class 0.2s

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - three (3) current transformers each with three cores, two cores for protection 5P20, one for metering 0.2S.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 1 Lot XLPE 33kV Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.9.1.1 to 1.9.1.8.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 3.3kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works.

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers. Class 0.2 s(kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 6 Nos Digital Programmable Energy import and export meters for 4 x 33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs   All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.  The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the 3 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 1.9.3.1 to 1.9.3.7

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - Item 8.4.2	1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - one (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Chililabombwe 132/33/11kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Chililabombwe substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have four (4) 132/11kV, 40MVA transformers and three (3) 132/33kV, 40MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 4nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for two (2) 132kV unequipped future line bay.

      - 7 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20, two for metering class 0.2s and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) 132kV unequipped future transformer bay.

      - Item 4.1.3	3 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - Item 4.1.3	4 no’s 132/11kV power transformers

Rated voltage:	132/11kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle , with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - Item 4.1.5	1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus. 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and one for protection (3P). Ratio  kV, to be installed on different phases.

      - 3 no’s 33kV Transformer Bays for 132/33kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering class 0.2s and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) 33kV unequipped future transformer bay.

      - 6 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering 0.2s.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers with two cores for protection and one for metering.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 2 (two) complete sets three phase voltage transformers, with two windings,

        - one for measuring Cl0.5. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 3 (three) bus riser.

        - 1 (one) earthing panel

      - 4 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for protection 5P20, one for metering class 0.2s and two for protection (Class X)

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.5.

        - 3 (three) surge arresters.

      - 6 nos’ complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 3 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 7nos Neutral Current Transformers for main Transformers; 132kV, 33kV and 11kV sides for the 132/33/11kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 7nos earthing resistors complete with accessories for limiting earth fault current to 40MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.10.1.1 item 1.10.1.21

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single  line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV, 33kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works.

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 4Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 7Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 2No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV Busbar Protection System with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Design, supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Design, supply, install, test, and commission 8Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

- Design, supply, install, test, and commission 4Nos. 11kV Transformer incomer Bay control and protection boards housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

Each Transformer main protection system shall include but not limited to the following discrete relays.

- Overcurrent and Earth Fault protection relay for each winding

- Electrically and mechanically resettable tripping Relays

- Trip Circuit Supervision Relay

Design, supply, install, test, and commission 3No. 11kV Bus Section Bay control and protection boards housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 4Nos. 11kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

i.	Feeder management protection.

ii.	Electrically and mechanically resettable tripping Relay.

iii.	Trip circuit supervision relays.

- Design, supply, install, test, and commission 2 Nos. AVR Systems with a dedicated IEC-61850 compliant IED installed for each of the transformers. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV, 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 8 nos Digital Programmable Energy import and export Meter for the 132kV Chingola and Kakoso lines, Class 0.2s (kWh/kVArh), single rate tariff,  All values read shall be PRIMARY VALUES  [These meters are for statistical purposes and line performance assessments only]

      - 14 nos Digital Programmable Energy import and export Meter for 40MVA; 132/33/11kV transformers, two for each Transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES.These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 11/0.4kV Auxiliary Transformers. Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES These meters shall be installed on the 11kV sides only.

      - 12 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for the 11kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                             All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 7 No WTI [Winding Temperature Indicators] for 7 x 40MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 7 No OTI [Oil Temperature Indicators] for 7 x 40MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 7 x 40MVA Transformer energy meters.

      - Probes and communication software for the 4 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers’ Laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kakoso 132/33/11kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Kakoso substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (3) 132/33kV, 40MVA transformers and two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 4nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for two (2) 132kV unequipped future line bay.

      - 3 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering class 0.2s and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) 132kV unequipped future transformer bay.

      - 3 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus. 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Cl0.2s) and for protection(3P). Ratio  kV, to be installed on different phases.

      - 5 no’s 33kV Transformer Bays for 132/33kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) 33kV unequipped future transformer bay.

      - 5 nos complete 33kV line bays each consisting of:

- 1 (one) SF6 three-phase circuit breaker with operating cubicle.

- 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

- 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

d)  	3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering 0.2s.

- 3 (three) single-phase voltage transformers.

Ratio  kV, each with two cores, one 3P

and one Cl 0.2s.

- 3 (three) lightning arresters.

- 3 (three) conductors, insulated and placed on insulators,

from the arresters to the switchyard earthing system.

- 1 (one) cable marshalling kiosk.

- 1 Lot post insulators.

- 1 (one) complete set of three-phase line including clamps

for the flying busbars and for connection to the busbars and between the apparatus.

- 1 (one) complete set of string insulators for the 33kV bus

bars and line bay conductors.

- 1 (one) complete lot of clamps, fittings, apparatus

connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection and one for metering.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 2 (two) complete sets three phase voltage transformers, with two cores; one for measuring Cl0.5 and one for protection(3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for protection 5P20 and one for metering.

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 5nos Neutral Current Transformers for main Transformers; 132kV, 33kV and 11kV sides for the 132/33/11kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 5nos earthing resistors complete with accessories for limiting earth fault current to 40MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.11.1.1 to 1.11.1.21.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV, 33kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works.

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 4Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 3Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV Busbar Protection System with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Design, supply, install, test, and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.  Each Transformer main protection system shall include but not limited to the following discrete relays.

    - Low impedance Differential/restricted earth fault Protection.

    - Overcurrent and Earth Fault protection relay for each winding.

    - Electrically and mechanically resettable tripping Relays

- Trip Circuit Supervision Relay.

- Design, supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 7Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 2Nos. 11kV Transformer incomer Bay control and protection panels housing both the protection and bay control IEDs.

Each Transformer main protection system shall include but not limited to the following discrete relays.

ii.	Low impedance Differential/restricted earth fault Protection

iii.	Overcurrent and Earth Fault protection relay for each winding

iv.	Electrically and mechanically resettable tripping Relays

v.	Trip Circuit Supervision Relay

- Design, supply, install, test, and commission 1No. 11kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

i.	Feeder management protection.

ii.	Electrically and mechanically resettable tripping Relay.

iii.	Trip circuit supervision relays

- Design, supply, install, test, and commission 4Nos. 11kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

i.	Feeder management protection.

ii.	Electrically and mechanically resettable tripping Relay.

iii.	Trip circuit supervision relays

- Design, supply, install, test, and commission 2Nos. AVR Systems with a dedicated IEC-61850 compliant IED for each transformer. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV, 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 8 nos Digital Programmable Energy import and export Meter for the 132kV Chingola and Kakoso lines, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES [These meters are for statistical purposes and line performance assessments only]

      - 10 nos Digital Programmable Energy import and export Meter for 40MVA/31.5MVA; 132/33kV and 33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES. These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 33/0.4kV Auxiliary Transformers. Class 0.2s (kWh/kVArh), single rate tariff . All values read shall be PRIMARY VALUES These meters shall be installed on the 11kV sides only.

      - 10 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for the 11kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                             All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 5 No WTI [Winding Temperature Indicators] for 5 x 40/31.5MVA power transformer winding temperature monitoring c/w capillary and probe.                                                                                            These temperature values shall be read locally and remotely.

      - 5 No OTI [Oil Temperature Indicators] for 5 x 40/31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 5 x 40MVA Transformer energy meters.

      - Probes and communication software for the 5 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Chililabombwe Central 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Chililabombwe Central substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two(2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and one for protection 5P20. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four (4) cores, two cores for transformer protection 5P20, one for metering class 0.2s and one cores for transformer differential protection (class X).

        - 3 (three) single-phase voltage transformers, Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering 0.2S

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arrestors to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20, one core for metering class 0.2s and two cores for protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 6 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with two cores, one core for transformer protection 5P20 and one core for metering class 0.2s

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.12.1.1. to item 1.12.1.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 6Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to.

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 4 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 8 Nos Digital Programmable Energy import and export meters for 4x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 6 No Digital Programmable Energy import and export meters for 3 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 8 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - one (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items  above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Chililabombwe North 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Chililabombwe North substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and one for protection 3P. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for protection 5P20 one for metering and one core for protection (class X).

        - 3 (three) single-phase voltage transformers, ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 8 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for transformer protection 5P20, one for metering 0.2s

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering 0.2s

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20, one for metering class 0.2 and two cores for protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2.

        - 3 (three) surge arresters.

      - 5 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2S.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20), one for metering class 0.2S.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2nos Neutral Current Transformers for main Transformers.

      - 1 Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.13.1.1. to 1.13.1.16

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 10Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 5Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 14 Nos Digital Programmable Energy import and export meters for 7x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 10 No Digital Programmable Energy import and export meters for 5 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 8 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

        - - One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items  above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kawama 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Kawama substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four cores, two cores for protection 5P20, one for metering class 0.2s and one core for protection (class X).

        - 3 (three) single-phase voltage transformers, ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the bushings, to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of flat copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20, one for metering class 0.2s and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2nos Neutral Current Transformers for main Transformers.

      - 1 Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.14.1.1 to item 1.14.1.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 4Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 8 Nos Digital Programmable Energy import and export meters for 4x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 4 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to the voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer  with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items  above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kasumbalesa 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Kasumbalesa substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and one for protection 5P20. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four cores, two cores for transformer backup protection 5P20, one for metering class 0.2s and one core for transformer main protection (class X).

        - 3 (three) single-phase voltage transformers, ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one core for metering 0.2s

        - 3 (three) single-phase voltage transformers and ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer backup protection 5P20, one core for metering class 0.2s and two cores for main transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.15.1.1.to item 1.15.1.16

      - Pre-Commissioning Tests and Checks (full documentation of test  results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 4Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 4Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 4 Nos Digital Programmable Energy import and export meters for 2x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 4 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of item above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Mwambashi132/33kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Mwambashi substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have four (4) 132/33kV, 40MVA transformers and two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 4nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - d)	3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for two (2) 132kV unequipped future line bay.

      - 4 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 132kV unequipped future transformer bay.

      - 4 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two windings, one for measuring Cl0.2s and for protection(3P). Ratio  kV, to be installed on different phases.

      - 4 no’s 33kV Transformer Bays for 132/33kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3(three) current transformers each with four cores, one core for protection (5P20), one for metering and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 6 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3(three) current transformers each with three cores, two cores for protection 5P20, one for metering class 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring Cl0.2. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for protection 5P20, one for metering class 0.2s and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 10 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3(three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 6nos Neutral Current Transformers for main Transformers; 132kV, 33kV and 11kV sides for the 132/33/11kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 6nos earthing resistors complete with accessories for limiting earth fault current to transformers full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.16.1.1 to item 1.16.1.22

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 33kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works.

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 4Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 4Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply install and commission a new 132kV Busbar Protection System with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Design, supply, install, test, and commission 2No. 33kV Bus Section Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Decommission old control cables between 33kV primary equipment and existing control panels. The decommissioned cables shall be stored at a location to be designated by the employer.

- Design, Supply and install new control cables of suitable type and size between 33kV primary equipment and new Marshalling Kiosks and between the Marshalling kiosks and the control and protection panels.

- Design, supply, install, test, and commission 13Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

i.	Feeder management protection.

ii.	Electrically and mechanically resettable tripping Relay.

iii.	Trip circuit supervision relays.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Design, supply, install, test, and commission 10Nos. 11kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

i.	Feeder management protection.

ii.	Electrically and mechanically resettable tripping Relay.

iii.	Trip circuit supervision relays.

- Design, supply, install, test, and commission 2Nos. AVR Systems with a dedicated IEC-61850 compliant IED for each transformer. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV and 33kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 8 nos Digital Programmable Energy import and export Meter for the 132kV Chambishi East and Kalulushi lines, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES [These meters are for statistical purposes and line performance assessments only]

      - 12 nos Digital Programmable Energy import and export Meter for 132/33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 33/0.4kV Auxiliary Transformers. Class 0.2s (kWh/kVArh), single rate tariff    All values read shall be PRIMARY VALUES These meters shall be installed on the 33kV sides only.

      - 12 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - 20 No Digital Programmable Energy import and export meters for the 11kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 6 No WTI [Winding Temperature Indicators] for 6 x 40MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 6 No OTI [Oil Temperature Indicators] for 4 x 40MVA and 2 x 31.5MVA power transformer oil temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 4 x 40MVA Transformer energy meters.

      - Probes and communication software for the 4 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of item above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation

      - Installation of items  above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-

- IEC TS 6100

## New Kitwe 132/33/11kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The New Kitwe substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (3) 132/11kV, 40MVA transformers and four (4) 132/33kV, 40MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 4nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - d)	3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for one (1) 132kV unequipped future line bay.

      - 7 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 132kV unequipped future transformer bay.

      - 4 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 3 no’s 132/11kV power transformers

Rated voltage:	132/11kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and for protection(3P). Ratio  kV, to be installed on different phases.

      - 4 no’s 33kV Transformer Bays for 132/33kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection and one for metering.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring Cl0.2s and one for protection (3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 2 (one) bus riser.

        - 1 (one) earthing panel

      - 3 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for protection 5P20, one for metering class 0.2s and two cores for transformer main protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2.

        - 3 (three) lightning arresters.

      - 2 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 7nos Neutral Current Transformers for main Transformers; 132kV, 33kV and 11kV sides for the 132/33/11kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 7nos earthing resistors complete with accessories for limiting earth fault current to 40MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.17.1.1 to item 1.17.1.21

      - Pre-Commissioning Tests and Checks (full documentation of test   results, function checks, as-built drawings (layout, plans, single   line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV, 33kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works.

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 4Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 7Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV Busbar Protection System with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Design, supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

i.	Feeder management protection.

ii.	Electrically and mechanically resettable tripping Relay.

iii.	Trip circuit supervision relays.

- Design, supply, install, test, and commission 3Nos. 11kV Transformer incomer Bay control and protection boards housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

Each Transformer main protection system shall include but not limited to the following discrete relays.

- Low impedance Differential/restricted earth fault Protection

- Overcurrent and Earth Fault protection relay for each winding

- Electrically and mechanically resettable tripping Relays

- Trip Circuit Supervision Relay.

- Design, supply, install, test, and commission 2No. 11kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 4Nos. 11kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs.

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 2Nos. AVR Systems with a dedicated IEC-61850 compliant IED for each transformer. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Carry out system integration for all the 132kV, 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 8 nos Digital Programmable Energy import and export Meter for the 132kV Chichele and Mufulira lines, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES  [These meters are for statistical purposes and line performance assessments only]

      - 14 nos Digital Programmable Energy import and export Meter for 40MVA; 132/33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 11/0.4kV Auxiliary Transformers. Class 0.2s (kWh/kVArh), single rate tariff    All values read shall be PRIMARY VALUES These meters shall be installed on the 11kV sides only.

      - 8 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for the 11kV lines. Class 0.2s (kWh/kVArh), single rate tariff All values read shall be PRIMARY VALUES

      - All smart meters shall be installed in meter enclosures according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 7 No WTI [Winding Temperature Indicators] for 7 x 40MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 7 No OTI [Oil Temperature Indicators] for 7 x 40MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 5 x 40MVA Transformer energy meters.

      - Probes and communication software for the 4 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of item above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts

        - Cable trenches and covers

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with conditioning

-	One Relay room c/w air conditioning

-	One Control Room complete with conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 c/w air conditioning

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One store room (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated to the substation automation system and capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineer Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## New Chimwemwe 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The New Chimwemwe substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores; one for measuring Cl0.2s and one for protection class 3P Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four cores; two cores for protection 5P20 one for metering Cl0.2s and one core for main transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores; one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering Cl0.2s

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores; one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters and conductors to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering Cl0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters and conductors to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring Cl0.2 and one for protection Cl3P. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores; one core for protection 5P20, one for metering class 0.2s and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 10 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2nos Neutral Current Transformers for main Transformers.

      - 1 Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.18.1.1 to item 1.18.1.16

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay.

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 10Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 8 Nos Digital Programmable Energy import and export meters for 4x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 20 No Digital Programmable Energy import and export meters for 10 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineer Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## New Scaw 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The New Scaw substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and one for protection class 3P. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four cores; two cores for protection 5P20, one for metering Cl0.2s and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering Cl0.2s.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbar and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores; one for measuring Cl0.2 and class 3P for protection. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores; one core for protection 5P20, one for metering class 0.2s and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 15 nos’ complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2 nos Neutral Current Transformers for main Transformers.

      - 1 Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2 nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.19.1.1 to item 1.19.1.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay.

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 15Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 8 Nos Digital Programmable Energy import and export meters for 4x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 30 No Digital Programmable Energy import and export meters for 15 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of item above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - one (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Nkana Mine 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Nkana Mine substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring Cl0.2s and class 3P for protection. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) current transformers each with four cores; two cores for transformer protection 5P20 one for metering class 0.2s and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings; one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 6 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores one for measuring Cl0.2s and class 3P for protection. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four core, one core for protection 5P20, one for metering class 0.2s and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3(three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2 nos Neutral Current Transformers for main Transformers.

      - 1 Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.20.1.1 to item 1.20.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 7Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay.

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays.

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 10 Nos Digital Programmable Energy import and export meters for 5x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 16 No Digital Programmable Energy import and export meters for 8 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Nkana East 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Nkana East substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (3) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 3 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Cl0.2s). and one for protection (Cl3P). Ratio  kV, to be installed on different phases.

      - 3 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer protection 5P20 one for metering class 0.2s and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3(three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars, to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring Cl0.5 and one for protection class 3P. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 3 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for protection 5P20 and one for metering class 0.2s and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 5 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing System and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 3nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 3nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.21.1.1. to item 1.21.1.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 5Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. AVR Systems with IEC61850 compliant IEDs for 3x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 6 no’s Digital Programmable Energy import and export Meter for 3 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 8 Nos Digital Programmable Energy import and export meters for 4x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 10 No Digital Programmable Energy import and export meters for 5 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 3 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 3 No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - one (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Luangwa 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Luangwa substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (3) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 3 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Cl0.2s) and one for protection (Cl3P) Ratio  kV, to be installed on different phases.

      - 3 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for protection 5P20, one for metering and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering Cl0.2s.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3(three) current transformers each with three cores, two cores for protection 5P20; one for metering Cl0.2s

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores one for measuring Cl0.2 and one for protection Cl3P. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

- 3 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores; one core for protection 5P20 and one for metering class 0.2s and two for transformer protection (Class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 10 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3(three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to designed to cater for switchyard lighting

      - 3nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 3nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.22.1.1 to item 1.22.1.15

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- upply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

Supply, install, test and commission 3Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 10Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. AVR Systems with IEC61850 compliant IEDs for 3x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 6 no’s Digital Programmable Energy import and export Meter for 3 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 8 Nos Digital Programmable Energy import and export meters for 4x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 20 No Digital Programmable Energy import and export meters for 10 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 3 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 3 No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers’ laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kalulushi 132/33/11kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Kalulushi substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (3) 132/33kV, 40MVA transformers and two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - d)	3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for two (2) 132kV unequipped future line bay.

      - 3 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 132kV unequipped future transformer bay.

      - 3 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Class: 0.2S) and one for protection (Class:3P). Ratio  kV, to be installed on different phases.

      - 5 no’s 33kV Transformer Bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection (Class: 5P20), one for metering (Cl 0.2s) and two cores for transformer differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 4 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for transformer protection (Class: 5P20) and one for metering (Class: 0.2s)

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (Class: 0.2S).

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying flat copper busbars.

        - 1 (one) complete set of insulators for 11kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring (Class: 0.2) and one for protection (Class: 3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for transformer protection (Class: 5P20) and one for metering (Class: 0.2S).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for transformer protection (Class: 5P20) and one for metering (Class: 0.2S).

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for transformer protection (Class: 5P20) and one for metering (Class: 0.2S).

      - 1 lot complete Substation Earthing and Lightning Protection System. Lightning masts shall be designed to accommodate switchyard lighting.

      - 5nos Neutral Current Transformers for main Transformers; 132kV, 33kV and 11kV sides for the 132/33/11kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 5nos earthing resistors complete with accessories for limiting earth fault current to 40MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.23.1.1. to item 1.23.1.21.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV, 33kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works.

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 2Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 6Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV Busbar Protection System with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Design, supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Design, supply, install, test, and commission 3Nos. 11kV Transformer incomer Bay control and protection boards housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 1No. 11kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 8Nos. 11kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- 2nos Complete Battery/charger systems consisting of respective.

- AC and DC distribution boards with section and feeder breakers.

- Design, supply, install, test, and commission 2Nos. AVR Systems with a dedicated IEC-61850 compliant IED for each transformer. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV, 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACS as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 4 nos Digital Programmable Energy import and export Meter for the 132kV Mwambashi lines, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES [These meters are for statistical purposes and line performance assessments only]

      - 10 nos Digital Programmable Energy import and export Meter for 132/33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 11/0.4kV Auxiliary Transformers. Class 0.2s (kWh/kVArh), single rate tariff .All values read shall be PRIMARY VALUES These meters shall be installed on the 11kV sides only.

      - 8 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for the 11kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                             All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels.

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 5 No WTI [Winding Temperature Indicators] for 5 x 40MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 5 No OTI [Oil Temperature Indicators] for 5 x 40MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 5 x 40MVA Transformer energy meters.

      - Probes and communication software for the 4 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One store room (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated to the substation automation system and capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of item above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kalulushi North 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Kalulushi North substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for protection 5P20 one for metering and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 1 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for transformer protection 5P20, one for metering.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for transformer protection 5P20, one for metering.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores,

        - one for measuring Cl0.5. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 3 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for transformer protection 5P20,one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2 nos Neutral Current Transformers for main Transformers.

      - 1 Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.24.1.1 to item 1.24.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 3Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 2 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 6 No Digital Programmable Energy import and export meters for 3 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of item above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## New Chibuluma 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The New Chibuluma substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s and the other for protection class 3P. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer protection 5P20, one for metering class 0.2s. and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for transformer protection 5P20, one for metering.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores.

        - one for measuring Cl0.5. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20, two for metering class 0.2s and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20, two for metering class 0.2s and two cores for busbar protection (class X).

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.25.1.1 to item 1.25.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 4Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 4Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 4 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 4 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in the meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items 6.5.1 to 6.5.9 above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Lwamisamba 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Lwamisamba substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - Item 6.1.1	2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores: one for measuring Cl0.2s and one for protection Cl3P. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for protection (Cl5P20) one for metering (Cl 0.2s) and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 6 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for feeder protection (Class: 5P20), one for metering (Class: 0.2S).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for busbar protection (Class: 5P20), one for metering (Class: 0.2S).

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying flat copper busbars.

        - 1 (one) complete set of insulators for 11kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring Cl0.2 and one for protection Cl3P. Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20, one for metering class 0.2S and two cores for differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3kV, each with two cores, one 3P and one Cl 0.2.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering class 0.2.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20), one for metering class 0.2S.

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.26.1.1. to 1.26.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 8Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 4Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete 110VDC Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 12 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 4 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kalulushi Airport 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Kalulushi Airport substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores: one for measuring Cl0.2S and one for protection Cl3P. Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer protection (Cl5P20) one for metering (Cl 0.2S) and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3kV, each with two cores, one 3P and one Cl 0.2S.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 6 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (Class: 0.2S).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one core for protection (Class:3P) and one for metering (Class: 0.2).

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering class 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper conductors.

        - 2 (two) complete sets single phase voltage transformers, with two cores, one for metering Cl0.5 and one for protection (Class: 3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection (Class: 5P20) and one for metering (class 0.2S) and two cores for differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one for protection (Class: 3P) and one for metering (Class 0.2s).

        - 3 (three) surge arresters.

      - 5 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for feeder protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2).

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.27.1.1 to 1.27.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 8Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply, install, test and commission 2nos Complete 110VDC Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 12 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES

      - 10 No Digital Programmable Energy import and export meters for 5x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs  All values read shall be PRIMARY VALUES

      - All smart energy meters shall installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items 6.5.1 to 6.5.9 above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

Item 6.5.12	Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Chambishi East 330/132/33kV Substation

The acquired substation land is 500mx500m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Chambishi East substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 330kV and 132kV voltage levels. The 33kV busbars will be single busbars. The 330kV bus bar installation will allow for ease of additional future installations for two (2) future 330kV and two (2) 132kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (3) 330/132/11kV, 160MVA Transformers.

The scope of work shall be but not limited to:

- Extension of the 02x 330kV busbar to accommodate 3x 330/132/11kV transformer bays and 02 x 330kV unequipped line bays

- Integration of the new bays into the existing substation control and protection system

- Associated civil works, foundations, and steel gantry structures for the new bay equipment.

### Power Equipment

      - 3 no’s 330 kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker transformer isolator).

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle (circuit breaker busbar isolator).

        - 3 (three) current transformers each with six cores, two cores for     transformer protection 5P20, one for metering class 1 and two     cores for busbar protection (class X), one spare Metering core class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio  kV, each with two windings, one and one Cl0.2s.

        - 3 (three) lightning arresters, each with six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer               bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 330kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped 330kV future transformer bay.

      - Extension of 02 no’s 330 kV Busbars (main and reserve) by 05    bays consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 330 kV     conductors.

        - 2 no’s set of 3 (three) single-phase capacitive voltage     transformers for main and reserve bus bars. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

      - 3 no’s 330/132/11kV power transformers:

Rated voltage:	330/132/11kV (+10, -10 x1.5%)

Rated power:	125/160/5MVA

Vector group:	YNyn0d1

Cooling:	ONAN/ONAF

Tap Changer:	On load.

      - 6 no’s 132 kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - 3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for three (3) unequipped 132kV future line bays.

      - 1 no’s 132 kV bus coupler bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132 kV bus section bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 3 no’s 132 kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped 132kV future transformer bay.

      - 2 no’s 132 kV Busbars (main and reserve) consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 lot complete Substation Earthing and Lightning Protection   System extension. The Lightning masts shall design to accommodate switchyard lighting.

      - 3nos Neutral Current Transformers for main Transformers; 330kV and 132kV sides for the 330/132kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary Equipment.

      - SF6 gas equipment comprising the following:

        - 1 set per substation of SF6 gas filling equipment

        - 1 set of SF6 leak detector equipment.

        - 1 x 45 kg SF6 gas bottle filled with Sf6 gas.

The gas treatment plant(s) to be supplied shall have sufficient storage facilities for the maximum quantity of gas that could be removed when carrying out maintenance or repair work on the largest section of the switchgear.

All the necessary pipes, couplings, flexible tubes, and valves for coupling to the switchgear for filling or evacuating all the gases to be used, with all necessary instructions for the storage of this equipment, shall be provided.

      - 2nos 11/0.4kV 500kVA Transformers Auxiliary transformers complete with 2nos 11kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 1no 500kVA diesel generator complete with accessories.

      - Installation of Item 1.28.1.1 to 1.28.1.14

      - Pre-Commissioning Tests and Checks (full documentation of test  results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the extension of the 330kV system, top of range IEC 61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works.

- Design, Supply, install, test, and commission 1No. 330kV Bus Section Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 3Nos. 330kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Current Differential Protection (main 1).

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install required equipment for integration of new circuits into existing busbar protection system for the 330kV system. Commission new circuits in on the existing system.

- Design, Supply, install, test, and commission 3Nos. 132kV Transformer Incomer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types for the LV side:

- Feeder management relay.

- Bay Control Unit.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, Supply, install, test, and commission 6Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, Supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, Supply, install, test, and commission 1No. 132kV Bus Sections Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Integrate the 330kV side of the new transformers into the existing 330kV Busbar Protection System type PCS915S.

- Design and Supply, install and commission a new 132kV Busbar Protection System with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Supply, install, test and commission 2Nos. 11kV Line Feeder Bay Control and Protection Panels (Auxiliary Transformer supply) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, Supply, install, test, and commission 1Nos. AVR Systems with a dedicated IEC-61850 compliant IED for each transformer. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Carry out system integration for all the new 330kV system Control and Protection IEDs into the existing Substation Automation System. The existing SAS is the PCS-9700 by NR Electric. It is based on the IEC61850-8-2 communication Protocol and was commissioned in 2024. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Design and supply and install equipment for the extension of the existing Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the existing LAN architecture.

- Design and supply spare adequate SAS spares (BCUs, LAN Switches, etc.) for the station.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Design and Supply, install required equipment for integration of new circuits into existing Fault recorder system for the 330kV system. Commission new circuits in Fault recorder system.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to the following.

      - 12 nos Digital Programmable Energy import and export Meter for the 132kV lines, Class 0.2s (kWh/kVArh), single rate tariff,                                            All values read shall be PRIMARY VALUES.                                       [These meters are for statistical purposes and line performance assessments only]

      - 6 nos Digital Programmable Energy import and export Meter for each 160MVA; 330/132/11kV transformers, Class 0.2 (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES.  These meters shall be installed on the 132kV side only. [These meters are for statistical purposes only]

      - 4Nos Digital programmable energy import and Export meters for each 500kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2 (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software (inclusive of Licences) for both digital programmable energy meters and the remote meter reading system

      - 3nos WTI [Winding Temperature Indicators] for power transformer winding temperature monitoring c/w capillary and probe                                                                                             These temperature values shall be read locally and remotely.

      - 3nos OTI [Oil Temperature Indicators] for power transformer oil temperature monitoring c/w capillary and probe.                                           These temperature values shall be read locally and remotely.

      - 4no’s Programmable Transducer Class 0.2s c/w software for 132kV lines monitoring of measurands to NCC.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lightning mast, security light masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female, each 2m2 complete with extractor

-	Two Shower Rooms, Each, 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

-  One 11kV switchgear room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences 2m high and 3m apart), 75mm diameter steel intermediate and 100mm diameter gate and corner poles, mounted at 4m intervals enclosed by the outer diamond mesh wire not less than 1000m in perimeter with two access gates, complete with standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road ,and within and 1km of tarred road outside the substation. The approach road length to match dimension at site from existing public road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, equal to the equivalent of substation area.

        - Clean Water supply system using a borehole drilled to not less than 80 metre depth and cased, in 8’’ diameter borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound but done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter steel intermediate and 100mm diameter gate and corner poles, mounted at 4m intervals.

        - The substation shall be constructed complete with automatic fire detection and suppression system integrated into the substation automation system and capable of communicating with NCC through the substation SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on (330kV and 132kV line bays) Kansanshi, Luano, Lufwanyama, Refractory, Nchanga, Chililabombwe and Kabundi line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - One (1) Synchronous Digital Hierarchy (SDH) multiplexer with STM-64 optical transmission capacity each and the following interfaces:

- Optical Transmission Modules:

- 2 x 2 ports STM-64

- 4 x 4 ports STM-16

- Service Interfaces:

- 63 x E1 ports

- 2 x 8 ports STM-1

- 8 x 100 Base TX ports (Fast Ethernet - Electrical)

- 8 x 100 Base FX ports (Fast Ethernet – Optical)

- 2 x Gigabit Ethernet ports x 4 control modules

- Engineer’s Order Wire

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fibre Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Chambishi Primary 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Chambishi Primary substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Class: 0.2S) and one for protection (Class: 3P). Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer protection (Class: 5P20) one for metering (Class: 0.2S) and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2S.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 3 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one core for metering (Class: 0.2S).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one for protection (Class: 3P) and one for metering (Class: 0.2S).

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection three cores, two cores to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (Class: 0.2S).

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for 11kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring (Class: 0.2) and one for protection (Class: 3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one core for transformer protection (Class: 5P20), one for metering (class 0.2S) and two cores for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for transformer protection (Class: 5P20) and one for metering (class: 0.2S).

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2).

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.29.1.1 to item 1.29.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 5Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. v:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete 110 VDC Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 6 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 4x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Musonda 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Musonda substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for protection (Class: 5P20), one for metering (Class: 0.2S) and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 3 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one core for metering (Class: 0.2S).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (Class: 0.2s).

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying flat copper busbars.

        - 1 (one) complete set of insulators for 11kV flat copper conductors

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring (Class: 0.2) and one for protection (Class: 3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one cores for protection (Class: 5P20), one for metering (class: 0.2s) and two cores for transformer differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class: 0.2s).

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2).

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.30.1.1 to 1.30.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 5Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete 110 VDC Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES  These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 6 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 4x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop with Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Mufulira 132/33kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Mufulira substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have four (4) 132/33kV, 40MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 4nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - d)	3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three cores, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for two (2) 132kV unequipped future line bay.

      - 4 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 132kV unequipped future transformer bay.

      - 4 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle, with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering class 0.2s and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio  kV, to be installed on different phases.

      - 4 no’s 33kV Transformer Bays for 132/33kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection (Class: 5P20) one for metering (Class: 0.2s) and two cores for transformer differential and restricted earth fault protection (class X) and one spare.

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 6 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one core for metering (Class: 0.2s).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for transformer protection (Class: 5P20) and one for metering (Class: 0.2s).

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 lot complete Substation Earthing System and and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 4nos Neutral Current Transformers for main Transformers; 132kV and 33kV sides for the 132/33kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 4nos earthing resistors complete with accessories for limiting earth fault current to transformers full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.31.1.1. to item 1.31.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

### Substation Automation, Control and Protection

      - Item 3.2.1	1 lot Complete control system for the 33kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works.

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 4Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 4Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV busbar protection with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Design, supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 8Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1Nos. AVR Systems with a dedicated IEC-61850 compliant IED for each transformer. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV and 33kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective AC and DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 8 nos Digital Programmable Energy import and export Meter for the 132kV Chambishi East and New Kitwe, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES [These meters are for statistical purposes and line performance assessments only]

      - 8 nos Digital Programmable Energy import and export Meter for 132/33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 33/0.4kV Auxiliary Transformers. Class 0.2s (kWh/kVArh), single rate tariff    All values read shall be PRIMARY VALUES These meters shall be installed on the 33kV sides only.

      - 12 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 4 No WTI [Winding Temperature Indicators] for 6 x 40MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 4 No OTI [Oil Temperature Indicators] for 4 x 40MVA and 2 x 31.5MVA power transformer oil temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 4 x 40MVA Transformer energy meters.

      - Probes and communication software for the 4 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

## Mufulira West 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Mufulira West substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for protection (Class: 5P20), one for metering (Class: 0.2s) and one core for transformer differential protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 5 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one core for metering (Class: 0.2s).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (Class: 0.2s).

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one cores for transformer backup protection (Class: 5P20), one for metering (class: 0.2s) and two cores for transformer differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2.

        - 3 (three) surge arresters.

      - 6 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for transformer protection 5P20, one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.32.1.1. to 1.32.1.13.

      - Pre-Commissioning Tests and Checks (full documentation of test    results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 7Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 6Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete 110VDC Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 10 Nos Digital Programmable Energy import and export meters for 5x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 12 No Digital Programmable Energy import and export meters for 6 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meters enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 5 x 33kV lines energy meters.

      - Probes and configuration software for the 6 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

-Relay and distribution room complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connector (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software ON Engineers Laptop.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-

- IEC TS 6100

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software on Engineers Laptop.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Nsato 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Nsato substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer backup protection (Class: 5P20), one for metering (Class: 0.2s) and one core for transformer protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection, to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of  insulators for the 11 kV flat copper busbars.

        - 1 (one) complete set of string insulators for the 11 kV conductors.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class:3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one cores for transformer backup protection (Class: 5P20), one for metering (class: 0.2s) and two cores for transformer differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) t three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary

equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.33.1.1 to item 1.33.1.13.

      - Pre-Commissioning Tests and Checks (full documentation of test   results, function checks, as-built drawings (layout, plans, single   line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 4Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete 110VDC Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 4 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8 No Digital Programmable Energy import and export meters for 4x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the 2 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Ndeke 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Ndeke substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have three (2) 33/11kV, 31.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	25/31.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two windings, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio  kV, to be installed on different phases.

Item 6.1.3	2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer backup protection (Class: 5P20), one for metering (Class: 0.2s) and one core for transformer differential protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 5 no’s complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of insulators for the 11 kV flat copper conductors.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, one cores for transformer backup protection (Class: 5P20), one for metering (class: 0.2s) and two cores for transformer differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 10 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 31.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.34.1.1. to 1.34.1.15.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 7Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 10Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 31.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete 110VDC Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 31.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 10 Nos Digital Programmable Energy import and export meters for 5x33kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 20 No Digital Programmable Energy import and export meters for 10 x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 31.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 31.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 31.5MVA Transformer energy meters

      - Probes and configuration software for the 5 x 33kV lines energy meters.

      - Probes and configuration software for the 6 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits , fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Mokambo 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Mokambo substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio  kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer backup protection (Class: 5P20), one for metering (Class: 0.2S) and one core for transformer differential protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 33/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 1 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) single-phase voltage transformers.    Ratio  kV, each with two cores, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of current carrying busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 2 (two) complete sets three phase voltage transformers, with two cores, one for measuring (Class: 0.2s) and one for protection (Class: 3P). Ratio 11√3/0.11√3/0.11√3/0.113 kV,to be installed on different phases.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with four cores, one cores for transformer backup protection (Class: 5P20), one for metering (class: 0.2s) and two cores for transformer differential and restricted earth fault protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two cores, one 3P and one Cl 0.5.

        - 3 (three) surge arresters.

      - 4 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection (Class: 5P20) and one for metering (class 0.2s).

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.35.1.14 to 1.35.1.13

      - Pre-Commissioning Tests and Checks (full documentation of test   results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 3Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relays

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. The protection system will consist of the following discrete relay types:

  - Feeder management protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete 110VDC Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES  These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 2 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 8No Digital Programmable Energy import and export meters for 4x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the 1 x 33kV lines energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Lufwanyama 132/33kV Substation

The acquired substation land is about 200mx200m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports)

The Lufwanyama substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with double bus bars on 132kV and single bus bar on 33kV. The bus bars installation will allow for ease of additional future installations for two (2) future 132kV and three (3) future 33kV bays. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have four (4) 132/33kV, 40MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2nos 132 kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle (circuit breaker line isolator).

        - 4 (four) three-phase isolating switches complete with local position indication and operating cubicles.

        - d)	3 (three) single-phase capacitive voltage transformers. Ratio kV, each with three windings, two for protection 3P and one for measuring Cl0.2s.

        - 3 (three) single-phase current transformers, each with 6 cores, two for measuring Cl0.2s/FS5, two for feeder protection 5P20 and two for bus bar protection PX.

        - 3 (three) lightning arresters, each with a six-digit surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the six-digit surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) set of three-phase line for the flying bus bars and for the connections to and between the apparatus and to the feeder and the bus bars.

        - 1 (one) cable marshalling kiosk.

        - 1 (one) complete set of string insulators for the main and flying bus bars.

        - 2 (two) post insulators.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

        - Connection of terminal tower of transmission line to substation line bay.

Note: There shall be a provision for two (2) 132kV unequipped future line bay.

      - 3 no’s 132kV Transformer bays, each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 4 (four) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 132/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 132kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 132kV unequipped future transformer bay.

      - 3 no’s 132/33kV power transformers

Rated voltage:	132/33kV (+10, -10 x1.5%)

Rated power:	31.5/40MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 2 no’s 132 kV Bus bars each consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 132 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 1 no’s 132kV Bus Coupler Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle with integral earth switch

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 132kV Bus Section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection (5P20), one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot of post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33 kV conductors.

        - 2 (two) complete sets of single-phase capacitive voltage transformers, with two windings, one for measuring Cl0.2s. Ratio  kV, to be installed on different phases.

      - 3 no’s 33kV Transformer Bays for 132/33kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with six cores, two cores for transformer protection 5P20 two for metering and two cores for busbar protection (class X).

        - 3 (three) single-phase voltage transformers.

        - Ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters, each with surge counter.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 2 nos complete 33kV line bays each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1 (one) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 one core for metering

        - 3 (three) single-phase voltage transformers ratio 33/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for two (2) unequipped future 33kV line bays.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 6 (six) current transformers each with six cores, two cores for transformer protection 5P20, one for metering and two cores for busbar protection (class X), one spare core.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the surge counters, and conductors from the counters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting.

      - 3nos Neutral Current Transformers for main Transformers; 132kV and 33kV sides for the 132/33kV Transformers.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 3nos earthing resistors complete with accessories for limiting earth fault current to transformers full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.36.1.1. to 1.36.1.16.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc).

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV, 33kV and 132kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The Contractor shall advise the best solution and carry out all the works subject to ZESCO’s SCADA and Protection Engineers approval. The contractor shall also provide suitable range Bay Control Units (BCUs) for sub-transmission voltage levels, single station HMI server, single operator workstation, single engineering workstation, LAN switches/communication system, legacy protocol converter (where required) and a DC to 230V AC inverters rated at 2500VA.

All IEDs must be IEC-61850 compliant and fully capable of reporting to a minimum of 6 MMS clients.

A solution for HMI should be an Industrial PC with RAID technology. The HMI will do its own data acquisition independent of Gateway acquisition. In other words, in an event that the Gateways are not running, the station can still be monitored by the local HMIs. Conversely, when the local HMIs are not running, the station can still be monitored by the dispatch centres (National Control Centre (NCC) and Regional Control Centre (RCC) via the station gateways. The new control system should be open and expandable (future proof) and should be IEC-61850 compliant.

The contractor shall be required to carry out the following works.

- Design, supply, install, integrate to existing SAS, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for new bays in the substation.

- Design, supply, install, test, and commission 2Nos. 132kV Line Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Line Differential Protection (main 1) on optic fibre.

- Line Differential Protection (main 2) on Optic fibre.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

- Design, supply, install, test, and commission 4Nos. 132kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of numerical IEDs of the following discrete relay types:

- Current Differential Protection (main 1)

- Current Differential Protection (main 2).

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays

The control and protection system for 33kV incomers shall be housed in the same panels as the 132kV.

- Design, supply, install, test, and commission 1No. 132kV Bus Coupler Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Line Distance Protection (main 1) on optic fibre.

- Feeder Management relay

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1No. 132kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design and Supply, install and commission a new 132kV Busbar Protection System with circuit breaker fail protection function.

- Design and Supply, install and commission a new Protection Management System for the 132kV system.

- Design, supply, install, test, and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 6Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay control and protection panels housing both the protection and bay control IEDs. The protection system will consist of the following discrete relay types:

- Feeder management protection.

- Electrically and mechanically resettable tripping Relay.

- Trip circuit supervision relays.

- Design, supply, install, test, and commission 1Nos. AVR Systems with a dedicated IEC-61850 compliant IED for each transformer. The AVR IEDs for regulation at each voltage level shall be installed in the same panel.

- Design, supply, install, commission, and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 132kV, 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Design, Supply, install, test and integrate required equipment for integration into existing ZESCO WAMPACs as specified under Particular Technical Specifications – Protection.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Design and supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the new LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, GPS Clock etc.) for the station.

### Metering

The metering system shall comprise but not limited to;

      - 4 nos Digital Programmable Energy import and export Meter for the 132kV Chingola lines, Class 0.2s (kWh/kVArh), single rate tariff, All values read shall be PRIMARY VALUES [These meters are for statistical purposes and line performance assessments only]

      - 6 nos Digital Programmable Energy import and export Meter for 132/33/11kV transformers, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES                                                                    These meters shall be installed on the LV side of transformers (11 and 33kV) only. [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for each 100kVA; 33/0.4kV Auxiliary Transformers. Class 0.2s (kWh/kVArh), single rate tariff    All values read shall be PRIMARY VALUES These meters shall be installed on the 33kV sides only.

      - 4 No Digital Programmable Energy import and export meters for the 33kV lines. Class 0.2s (kWh/kVArh), single rate tariff                                                                                     All values read shall be PRIMARY VALUES

      - All smart meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - 3 No WTI [Winding Temperature Indicators] for 3 x 40MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 3 No OTI [Oil Temperature Indicators] for 3 x 40MVA power transformer oil temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - Probes and communication software for configuration of 132kV lines energy meters.

      - Probes and communication software for 3 x 40MVA Transformer energy meters.

      - Probes and communication software for the 3 x 33kV lines energy meters.

      - 1 Lot Cables, Fittings etc. for the entire substation installations.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc.).

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 132kV and 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - one (1) FOX 615 STM-16 optical transmission capacity and the following interfaces:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1x4 port OPIC (With Multi Mode SFP’s)

- 1x4 port OPIC (single mode SFP)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connector(FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software ON Engineers Laptop.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical or optical parts required for a complete Optic Fiber Equipment installation

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-

- IEC TS 6100

## Funda 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Funda substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA.

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

a) 	1 (one) complete set of current carrying conductors.

b) 	1 (one) complete set of string insulators for the 33kV

conductors.

c)    2 (two) complete sets of single-phase voltage transformers, with two windings,

one for measuring Cl0.5. Ratio kV, and one for protection Cl 3P to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer protection 5P20, one core for metering and one core for transformer differential protection (class X).

        - 3 (three) single-phase voltage transformers Ratio 33/√3 to 0.11/√3, each with two windings, one 3P    and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV    transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus       connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 1 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20 and one core for metering.

        - 3 (three) single-phase voltage transformers.  Ratio  kV, each with two windings, one 3P and one Cl0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators,

        - from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps

        - for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (Three) current transformers each with three cores, two cores for protection 5P20 and one for metering class 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars consisting of:

        - 1 (one) complete set of flat copper busbar.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars.

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with four cores, one core for transformer protection 5P20, one core for metering class 0.2s and two cores for transformer REF and Differential protection (class X).

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 6 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20), one core for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting.

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary

equipment.

      - 2nos 33/0.4kV 100kVA Transformers Auxiliary transformers complete with 2nos 33kV switchgear.

      - 400VAC board complete with 2Nos 400V incomers from Auxiliary Transformers, 1Nos Incomer (MCCBs) from Diesel Generator (MCCB), 1Nos bus section and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Item 1.37.1.1 to 1.37.1.17

      - Pre-Commissioning Tests and Checks (full documentation test results, function checks, as-built drawings (layout, plans, sing line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 3Nos. (includes 2Nos for Auxiliary Transformer supply) 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs. 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

  - Each Transformer main protection system shall include but not limited to the following discrete relays.

  - Low impedance Differential/restricted earth fault Protection

  - Overcurrent and Earth Fault protection relay for each winding

  - Electrically and mechanically resettable tripping Relays

  - Trip Circuit Supervision Relay

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 3Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs. Protection shall Feeder management consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision relays

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply, install, test and commission 2nos Complete Battery/charger systems consisting of respective DC distribution boards with bus section and feeder breakers.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station.

All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 2 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 6 No Digital Programmable Energy import and export meters for 3x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart meters shall be installed in meter enclosures segregated according to voltage levels

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the smart energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

        - A Local Area Network (LAN) for the IT systems shall be installed in facilitating connectivity from all the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## E1 Switching Station

The acquired substation land is about 20mx50m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The E1 Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The 11kV E1 Switching Station shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The busbar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective busbars.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 no’s 11kV Indoor Busbars house in a distribution board consisting of:

- 1 (one) complete set of flat copper busbars.

- 1 (one) complete set of insulators for the 11 kV flat copper busbars

- 1 (one) bus riser.

- 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

- 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

- 1 (one) three-phase earthing switch, complete with local position indication

- 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

- 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

- 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

- 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

- 1 (one) three-phase earthing switch, complete with local position indication.

- 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

- 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

- 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

- 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single

line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

11 no’s 11kV Feeder protection consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers.

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 1 x 100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 20 Nos Digital Programmable Energy import and export meters for 2x11kV incomers and 8 feeders. Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES

      - All energy meters shall be installed in one meter enclosure/cabinet.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the 22 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 8.3.1 to 8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system.

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of GE

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE

- Line and Service Interface modules

- 4 x 8 ports GE module

- 1 x 4 port STM-1

- 1 x 16 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## North Hospital Switching Station

The acquired substation land is about 20mx50m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The North Hospital Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The 11kV North Hospital Switching Station shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The busbar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective busbars.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 no’s 11kV Indoor Busbars housed in a distribution board consisting of:

        - 1 (one) complete set of flat copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single

line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

11 no’s 11kV Feeder protection consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers.

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 1 x 100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 20 Nos Digital Programmable Energy import and export meters for 2 x 11kV incomers and 8 feeders.                                                                                              Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in a meter enclosure/cabinet.

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the smart energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 8.3.1 to 8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables wooden poles on 11kV line to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of GE

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE

- Line and Service Interface modules

- 4 x 8 ports GE module

- 1 x 4 port STM-1

- 1 x 16 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## General Offices Switching Station

The acquired substation land is about 20mx50m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The General Offices Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The 11kV General Offices Switching Station shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The busbar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective busbars.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 no’s 11kV Indoor Busbars house in a distribution board consisting of:

        - 1 (one) complete set of flat copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single

line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

11 no’s 11kV Feeder protection consisting of but not limited to:

- Feeder protection

- Electrically and mechanically resettable tripping relays

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers.

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 1x100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 20 Nos Digital Programmable Energy import and export meters for 2 x 11kV incomers and 8 feeders.                                                                                              Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in a meter cabinet/enclosure

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the smart energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 8.3.1 to 8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from wooden poles on 11kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of GE

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE

- Line and Service Interface modules

- 4 x 8 ports GE module

- 1 x 4 port STM-1

- 1 x 16 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Scaw Factory Switching Station

The acquired substation land is about 20mx50m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Scaw Factory Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The 11kV Scaw Factory Switching Station shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The busbar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective busbars.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 no’s 11kV Indoor Busbars house in a distribution board consisting of:

        - 1 (one) complete set of flat copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with two cores, one core for protection (5P20) and one for metering class 0.2

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single

line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

11 no’s 11kV Feeder protection consisting of but not limited to:

- Feeder protection

- Electrically and mechanically resettable tripping relays

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers.

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 1 x 100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 24Nos Digital Programmable Energy import and export meters for 4 x 11kV incomer and 8 feeders.                                                                                              Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in a meter enclosure/cabinet

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the smart energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 8.3.1 to 8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the wooden poles on 11kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of GE

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE

- Line and Service Interface modules

- 4 x 8 ports GE module

- 1 x 4 port STM-1

- 1 x 16 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## UBZ Switching Station

The acquired substation land is about 20mx50m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The UBZ Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The 11kV UBZ Switching Station shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The busbar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective busbars.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 no’s 11kV Indoor Busbars house in a distribution board consisting of:

        - 1 (one) complete set of flat copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single

line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

11 no’s 11kV Feeder protection consisting of but not limited to:

- Feeder protection

- Electrically and mechanically resettable tripping relays

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers.

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 1 x 100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 20 Nos Digital Programmable Energy import and export meters for 2 x 11kV and 8 11kV feeders.                                                                                              Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in a meter cabinet

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the smart energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 8.3.1 to 8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of GE

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE

- Line and Service Interface modules

- 4 x 8 ports GE module

- 1 x 4 port STM-1

- 1 x 16 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## N48 Switching Station

The acquired substation land is about 20mx50m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The N48 Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The 11kV N48 Switching Station shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The busbar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective busbars.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 no’s 11kV Indoor Busbars house in a distribution board consisting of:

        - 1 (one) complete set of flat copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.5.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single

line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

11 no’s 11kV Feeder protection consisting of but not limited to:

- Feeder protection

- Electrically and mechanically resettable tripping relays

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers. Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 1 x 100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 20 Nos Digital Programmable Energy import and export meters for 2 x 11kV incomers and 8x11kV feeders.                                                                                              Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart meters shall be installed in metering panel/enclosure

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the smart energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 8.3.1 to 8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

        - - One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of GE

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE

- Line and Service Interface modules

- 4 x 8 ports GE module

- 1 x 4 port STM-1

- 1 x 16 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Women Welfare Switching Station

The acquired substation land is about 20mx50m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Women Welfare Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The 11kV Women Welfare Switching Station shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The busbar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective busbars.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 no’s 11kV Indoor Busbars house in a distribution board consisting of:

        - 1 (one) complete set of flat copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single

line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

11 no’s 11kV Feeder protection consisting of but not limited to:

  - Feeder protection

  - Electrically and mechanically resettable tripping relays

  - Trip circuit supervision

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers.

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 1 x 100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 20 Nos Digital Programmable Energy import and export meters for 2 x 11kV incomers and 8x11kV feeders.                                                                                              Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart meters shall be installed in meter cabinet/enclosure

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the smart energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 8.3.1 to 8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from wooden poles on 11kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of GE

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE

- Line and Service Interface modules

- 4 x 8 ports GE module

- 1 x 4 port STM-1

- 1 x 16 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kankoyo Switching Station

The acquired substation land is about 20mx50m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Kankoyo Switching Station shall be supplied on a turnkey basis including earth work, road works, buildings, foundations and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The 11kV Kankoyo Switching Station shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The busbar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective busbars.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 1 no’s 11kV Indoor Busbars house in a distribution board consisting of:

        - 1 (one) complete set of flat copper busbars.

        - 1 (one) complete set of insulators for the 11 kV flat copper busbars

        - 1 (one) bus riser.

        - 1 (one) earthing panel

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) surge arresters.

      - 8 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20) and one for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection   System, Lightning masts to accommodate switchyard lighting

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single

line, key, wiring etc)

### Substation Automation, Control and Protection

      - 1 lot Complete control system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 8Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850 communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

All protection relays shall be numerical type.

11 no’s 11kV Feeder protection consisting of but not limited to:

- Feeder protection

- Electrically and mechanically resettable tripping relays

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers.

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Metering

The metering system shall comprise but not limited to;

      - 2 Nos Digital programmable energy import and Export meters for 1 x 100kVA; 11/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs All values read shall be PRIMARY VALUES.  These meters shall be installed on the 11kV sides only.

      - 20 Nos Digital Programmable Energy import and export meters for 2 x 11kV incomers and 8 x 11kV feeders.                                                                                              Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters shall be installed in a cabinet/enclosure

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software                                           for both digital programmable energy meters and the remote meter reading system

      - Probes and configuration software for the smart energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items 8.3.1 to 8.3.13

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning.

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables wooden poles on 11kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of GE

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE

- Line and Service Interface modules

- 4 x 8 ports GE module

- 1 x 4 port STM-1

- 1 x 16 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Engineers Laptop and Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

## Kansunswa 33/11kV Substation

The acquired substation land is about 100mx100m. Refer to the appendices for the substations site maps and coordinates.

The contractor shall fence the fore mentioned substation co-ordinates land with diamond mesh wire (4mmsqd gauge by 2metres with steel pole supports).

The Kansunswa substation shall be supplied on a turnkey basis including earth work, road works, buildings, foundations, and other civil works as well as design, supply, erection and commissioning of structural steel works and electrical equipment.

The station will be equipped with single outdoor bus bars on 33kV. The 33kV bus bars installation will allow for ease of additional future installations for two (2) future 33kV bays. The 11kV bus bars shall be indoor. The installation shall be done in such a way that, in future, no significant safety restrictions, no outages shall be required for any future construction works except for the purpose of commissioning and final connection. The bus bar arrangement and overall substation setup shall positively allow for this future expansion without extending the respective bus bars.

The station shall have two (2) 33/11kV, 12.5MVA transformers.

The Contractor can propose an alternative layout, if it fulfils the functions indicated on the single line diagram. The scope of work is defined as follows:

### Power Equipment

      - 2 no’s 33/11kV power transformers

Rated voltage:	33/11kV (+10, -10 x1.5%)

Rated power:	10/12.5MVA

Vector group:	Dyn11

Cooling:		ONAN/ONAF

Tap Changer:	On load.

      - 1 no’s 33 kV Bus bars consisting of:

        - 1 (one) complete set of current carrying conductors.

        - 1 (one) complete set of string insulators for the 33kV

        - conductors.

        - 2 (two) complete sets of single-phase voltage transformers, with two windings, one for measuring Cl0.2s and Cl3P for protection. Ratio kV, to be installed on different phases.

      - 2 no’s 33kV Transformer Bays for 33/11kV transformers each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with four cores, two cores for transformer protection 5P20, one core for metering and one cores for transformer differential protection (class X).

        - 3 (three) single-phase voltage transformers ratio 33/√3 to 0.11/√3, each with two windings, one 3P    and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for the flying busbars and for connection to the transformer bushings, to the busbars and to and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV    transformer and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus       connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) 33kV unequipped future transformer bay.

      - 1 no’s complete 33kV line bay each consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 1 (one) three-phase isolating switch with three-phase earthing switch, complete with local position indication and operating cubicle.

        - 1(One) three-phase isolating switch complete with local position indication and operating cubicle.

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, and one core for metering

        - 3 (three) single-phase voltage transformers.     Ratio  kV, each with two windings, one 3P and one Cl 0.2s.

        - 3 (three) lightning arresters.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps      for the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete set of string insulators for the 33kV bus

        - bars and line bay conductors.

        - 1 (one) complete lot of clamps, fittings, apparatus   connecting clamps, grading devices, etc.

Note: There shall be a provision for one (1) unequipped future 33kV line bay.

      - 1 no 33kV Bus section Bay consisting of:

        - 1 (one) SF6 three-phase circuit breaker with operating cubicle.

        - 2 (two) three-phase isolating switches, complete with local position indication and operating cubicle (busbar isolators).

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering class 0.2s.

        - 3 (three) conductors, insulated and placed on insulators, from the arresters to the switchyard earthing system.

        - 1 (one) cable marshalling kiosk.

        - 1 Lot post insulators.

        - 1 (one) complete set of three-phase line including clamps for   the flying busbars and for connection to the busbars and between the apparatus.

        - 1 (one) complete lot of clamps, fittings, apparatus connecting clamps, grading devices, etc.

      - 1 no’s 11kV Indoor Busbars housed in a distribution board consisting of:

        - 1 (one) complete set of insulated flat copper busbars.

        - 1 (one) complete set of insulators for the 11kV flat copper busbars.

        - 1 (one) bus riser.

        - 1 (one) earthing panel.

      - 2 no’s 11kV Indoor incomer panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one core for metering class 0.2

        - 3 (three) single-phase voltage transformers. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s. Ratio 11/√3 to 0.11/√3, each with two windings, one 3P and one Cl 0.2s

        - 3 (three) surge arresters.

      - 6 no’s complete 11kV indoor feeder panels each consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 1 (one) three-phase earthing switch, complete with local position indication

        - 3 (three) current transformers each with three cores, two cores for protection 5P20, one for metering class 0.2s.

        - 3 (three) lightning arresters.

      - 1 no 11kV Bus section panel consisting of:

        - 1 (one) three-phase rackable vacuum circuit breaker with operating cubicle and protection/control compartment and devices.

        - 3 (three) current transformers each with three cores, two cores for protection (5P20), one core for metering class 0.2s.

      - 1 lot complete Substation Earthing and Lightning Protection System, Lightning masts to be designed to cater for switchyard lighting

      - 2nos Neutral Current Transformers for main Transformers.

      - 1Lot XLPE 33kV and 11kV 1C Power cables rated for full load of the respective windings of the Transformers, 200m of each voltage level.

      - 1 lot Control Cables and fittings for all substation secondary equipment.

      - 1nos 11/0.4kV 100kVA Transformers Auxiliary transformers complete with 1nos 11kV switchgear.

      - 400VAC board complete with 1Nos 400V incomers from Auxiliary Transformers (MCCB) and feeder circuit breakers (MCB).

      - 2nos earthing resistors complete with accessories for limiting earth fault current to 12.5MVA transformer full load current.

      - 1no 100kVA diesel generator complete with accessories.

      - Installation of Items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

### Substation Automation and Control

      - 1 lot Complete control and protection system for the 11kV and 33kV system, top of range IEC61850 based. Technical details are as specified in the technical specifications.

The contractor shall be required to carry out the following works;

- Supply, install, test and commission 1No. SAS Panel housing Station Gateways/RTUs, LAN Switches etc.

- Supply, install, test and commission a modern IEC61850 based substation automation system (SAS) complete with bay control IEDs and other system requirements adequate to cater for all substation bays in the new substation.

- Supply, install, test and commission 1Nos. 33kV Line Feeder Bay Control and Protection Panels housing both bay control and protection IEDs.

- Supply, install, test and commission 2Nos. 33kV Transformer Bay control and protection panels housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 33kV Bus Section Bay control and protection panel housing both the protection and bay control IEDs.

- Supply, install, test and commission 2Nos. 11kV Transformer Incomer Bay control and protection panels (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 1No. 11kV Bus Section Bay control and protection panel (Indoor Switchgear) housing both the protection and bay control IEDs.

- Supply, install, test and commission 6Nos. 11kV Line Feeder Bay Control and Protection Panels (Indoor Switchgear) housing both bay control and protection IEDs.

- Supply, install, test and commission 2Nos. AVR Systems with IEC61850 compliant IEDs for 2x 12.5MVA 33/11kV Transformers.

- Supply, install, commission and test 1 No. Common Alarms Bay Control Unit for Station Common Alarms and DC Charger Alarms.

- Carry out system integration for all the 33kV and 11kV system Control and Protection IEDs into the Substation Automation System (SAS) to be supplied. The SAS shall be based on IEC61850communication Protocol. Due care shall be taken to ensure that all supplied bay control and protection IEDs are of compatible firmware and software versions to achieve seamless integration into the SAS.

- Carry out point-to-point tests for all control and protection signals with the dispatch centre systems.

- Supply a new Station and Process Communication LAN system complete with communication cables to allow for seamless connection and interface of the new IEDs into the LAN architecture.

- Supply spare adequate SAS spares (BCUs, LAN Switches, Computers, etc.) for the station

- 2 no’s Transformers Protection Systems for the 33/11kV transformers, numerical type consisting of:

- Each Transformer main protection system shall include but not limited to the following discrete relays.

        - Low impedance Differential/restricted earth fault Protection

        - Overcurrent and Earth Fault protection relay for each winding

        - Electrically and mechanically resettable tripping Relays

- 2 no’s auxiliary transformer protection consisting of:

- Feeder protection

- Electrically and mechanically resettable tripping relays

- 4 no’s 33kV Feeder protection consisting of but not limited to:

- Feeder protection

- Electrically and mechanically resettable tripping relays

- Trip circuit supervision relays

- 6 no’s 11kV Feeder protection for 2no. 11kV transformer incomers, 1no bus section and 3no outgoing feeders consisting of but not limited to:

- Feeder protection

- Electrically and mechanically resettable tripping relays

- 2 no’s AVR systems for 2x 12.5MVA 33/11kV transformers

- with complete parallel operation and control accessories

- Supply, install, test and commission 1nos Complete Battery/charger systems consisting of respective DC distribution boards with feeder breakers.

- Installation of items above.

- Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

- Engineer’s laptop with Maintenance software.

- All protection relays shall be numerical type.

### Metering

The metering system shall comprise but not limited to;

      - 4 no’s Digital Programmable Energy import and export Meter for 2 x 12.5MVA; 33/11kV transformer, Class 0.2s (kWh/kVArh), single rate tariff. All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV side only.                     [These meters are for statistical purposes only]

      - 2 Nos Digital programmable energy import and Export meters for 2 x 100kVA; 33/0.4kV Auxiliary Transformers.                                      Class 0.2s (kWh/kVArh), single rate tariffs.  All values read shall be PRIMARY VALUES. These meters shall be installed on the 11kV sides only.

      - 2 Nos Digital Programmable Energy import and export meters for 33kV feeder. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - 12 No Digital Programmable Energy import and export meters for 2x11kV transformer incomers and 6x11kV feeders. Class 0.2s (kWh/kVArh), single rate tariffs                                                                                                        All values read shall be PRIMARY VALUES

      - All smart energy meters to be installed in metering cabinet

      - 1 Lot Workstation for monitoring all substation meters

      - 1 Lot Substation Remote meter reading system.                               The system shall be able to read such values as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical data from the meters, carry out summations and derive & record simultaneous maximum demand of multiple circuits over the billing period.

      - 1 Lot Maintenance and interrogating Software for both digital programmable energy meters and the remote meter reading system

      - 2 No WTI [Winding Temperature Indicators] for each 12.5MVA power transformer winding temperature monitoring c/w capillary and probe. These temperature values shall be read locally and remotely.

      - 2 No OTI [Oil Temperature Indicators] for each 12.5MVA power transformer oil temperature monitoring c/w capillary and probe                                                                                   These temperature values shall be read locally and remotely.

      - Probes and configuration software for each 12.5MVA Transformer energy meters

      - Probes and configuration software for the smart energy meters.

      - Probes and configuration software for the 2 x 11kV lines energy meters.

      - 1 Lot Cables, Fittings etc for the entire substation installations.

      - Installation of items above.

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Applicable Standards

Electromagnetic compatibility                                                                                    IEC 62052-11,                                                                                      IEC 62053-21,                                                                                                IEC 62053-22,                                                                                             IEC 62053-23,                                                                                             IEC 62053-61,                                                                                             IEC 62056                                                                                                                  IEC 60688

### Structural Steelwork and Civil Works

      - 1 lot Structural Steelwork

        - (one) complete lot of supports for the isolating switches, circuit breakers, current and voltage transformers, operating cubicles, telecoms masts, lighting masts, lightning masts, etc., including foundations bolts and other fixing material.

        - (one) complete lot of gantry towers and support structures for the busbars, line bays, bus coupler and transformer bays.

      - 1 lot Civil Works

        - Bush clearing, including anthills and all trees.

        - Earthwork on the platform.

        - Complete soil testing and results for engineering foundations

        - Roads as required for approach and within the switchyard.

        - Necessary subsurface and surface drainage

        - Transformer oil pits, fire walls and foundations

        - Support and Gantry foundations, including holding-down bolts.

        - Cable trenches and covers.

        - Control building, with floor area of 460m2, with the following minimum room requirements:

-	Two battery rooms complete with extractor fans

-	One AC/DC room complete with air conditioning

-	One Relay room complete with air conditioning

-	One Control Room complete with air conditioning

-	One Communication Room complete with air conditioning

-	Two Toilets, male and female each 2m2 complete with extractor fans

-	Two Shower Rooms, each 2m2

-	One Kitchen, (max 9m2)

-	Two Offices (min 16m2 each) complete with air conditioning

-	One storeroom (min 30m2)

- One 11kV boards room (min 30m2) complete with air conditioning

        - A Local Area Network (LAN) for the IT systems shall be installed in the control building to facilitate connectivity to the ZESCO Corporate IT network from the offices and shall comprise the following:

  - 12 Unit Wall cabinet with glass visor

  - 24-port Ethernet Switch as per technical specifications

  - 24-port ethernet patch panel

  - 24-port Fiber optical patch panel

  - Single mode Fiber Optic patch cords

  - Fiber Optic-Ethernet Media Converters as required.

  - Double compartment trunking

  - Category 6 UTP cable

  - RJ-45 Wall jacks.

  - 230V AC Power supply for the equipment in the wall cabinet.

  - Accessories required to completion of installation.

        - Relay and distribution room complete with air conditioning

        - Guard’s Building (with waterborne toilet), 9m2, located inside and part outer panel wall fencing.

        - Fencing all substation in diamond mesh wire (inner and outer fences each 2m high and 3m apart), 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals enclosed by

        - the outer, not less than 700m in perimeter with two access gates, complete with a standard electric fence mounting with intruder alarm system.

        - Roadworks, road kerbs, road markings and signs for the approach road and within substation. The approach road length to match dimensions at site from existing main road.

        - Stone chippings, substation area, dia 30-40mm, 150mm thick layer, approx. area not less than 2500m2

        - Clean Water supply system using borehole source drilled to not less than 80m depth and cased with 8” borehole casing and approved sewerage disposal system using septic tanks and soakaways for both the substation and housing compound done independently.

        - Landscaping and replanting of vegetation and grass around.

        - Fencing of the entire substation land together with housing plot with 2.5mmsq. diamond wire on 75mm diameter intermediate and 100mm diameter gate and corner steel poles, mounted at 4m intervals.

        - The control building shall be constructed complete with automatic fire detection and suppression system integrated in the substation automation system capable of reporting to NCC through the SCADA system

      - Installation of items itemized above.

### Telecommunications

      - Supply of optical fibre approach cables from the gantries on 33kV line bays to the telecoms room.

      - One Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G.

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A.

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V.

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries.

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - One (1) PCM Access Multiplexer each with interfaces for SCADA, Speech and Data as follows:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- Engineer’s Order Wire

      - One (1) Optical Distribution Frame (ODF) with optical connectors (FC) and pigtails for complete multiplexer unit installation

      - One (1) Digital Distribution Frame (DDF) with electrical connectors and patch cables for complete installation.

      - One (1) Main Distribution Frame (MDF) with Krone type terminal blocks for terminating telephone cables and low speed RS 232 data lines.

      - Maintenance software.

      - Wiring for power cables and distribution blocks, data circuits, telephones, etc.

      - 1 lot Mechanical accessories, cabling, splice boxes and any other electrical, mechanical, or optical parts required for a complete Optic Fiber Equipment installation.

      - Installation of items above

      - Pre-Commissioning Tests and Checks (full documentation of test results, function checks, as-built drawings (layout, plans, single line, key, wiring etc)

      - Normative References

- Electromagnetic Compatibility

- ESTI EN 300385

- IEC 6100-6-2, EN 6100-6-2,

- IEC TS 6100

GENERAL SPECIFICATIONS OF FACILITIES

SECTION II CONTENT

2 GENERAL SPECIFICATIONS OF FACILITIES	109

2.1 GENERAL SPECIFICATIONS	109

2.1.1 Completeness of Contract	109

2.1.1.1 Equipment	109

2.1.1.2 Materials and Labour	109

2.1.1.3 Schedules	109

2.1.2 Drawings	109

2.1.3 Operation and Maintenance Manuals	111

2.1.4 Quality of Materials	111

2.1.5 Contractor's Quality Assurance Procedures.	111

2.1.6 Guarantees and Particulars.	111

2.1.7 Places of Manufacture and Sub-Contractors.	112

2.1.8 Factory Tests.	112

2.1.9 Installation, Testing at Site, Commissioning.	113

2.1.10 Work on Live Substations	114

2.1.11 Accommodation of Contractor's Personnel.	115

2.1.12 Packing, Transportation and Storage.	115

# GENERAL SPECIFICATIONS OF FACILITIES

## GENERAL SPECIFICATIONS

### Completeness of Contract

#### Equipment

All apparatus, accessories or fittings which may not have been specifically mentioned, but which are usual or necessary in the respective equipment for the completeness of the finished work in an operable status, shall be deemed to be included in the Contract and shall be provided by the Contractor without any extra charge. All equipment shall be complete in all details, whether or not such details are mentioned in the Specifications.

All special tools required for operation and maintenance of each type of equipment/facility shall be supplied as part of the equipment/facilities.

#### Materials and Labour

All materials, tools and skilled labour, whether of temporary or permanent nature, required by the Contractor for the design, manufacture, erection and testing at site of the plant and equipment shall be supplied and paid for by the Contractor.

#### Schedules

Any reference in the quantity and price schedules, the delivery period schedule or in the various clauses and schedules of the text of either the Specification or the Bid, to any equipment shall imply that the equipment is complete with all accessories, apparatus and fittings as outlined in sub-clause 1.1.1 above.

### Drawings

The Contractor's obligations with regard to preparation and submission of drawings, calculations, samples, patterns, models, etc. are stated in Section IV, General Conditions of Contract and in Section VII, Appendix 7. The Contractor shall prepare and submit to the Project Manager for approval dimensioned, and clearly legible, general and detailed design drawings and other pertinent information of all the Plant and Equipment specified in the Specifications.

All dimensions marked in “SI” units on drawings are to be considered correct, although by scale may differ there from. Detailed drawings approved by the Project Manager are to be acted upon where they differ from general drawings.

Approval of drawings and calculations shall not relieve the Contractor of his obligations to supply the Plant and Equipment in accordance with the Specifications.

The Contractor is responsible for any errors that may appear in the approved documents.  He shall as soon as an error has been detected, deliver the corrected documents to the Project Manager for re-approval.

All text on drawings provided by the Contractor shall be in the English language in addition, if necessary, to that of the country of origin.

All drawings shall be dimensioned in millimetres.

The sizes of all documents and drawings shall conform to the ISO standard, i.e.:

A1	594 mm x 841 mm				A2	420 mm x 594 mm

A3	297 mm x 420 mm				A4	210 mm x 297 mm

Sizes larger than A1 shall be avoided.  All documents in size A3 and A4 shall be bound in hard covers. Plant specific “as built” drawings and schematic shall also be delivered on Hard drive in a format readable in AutoCAD latest version and in transparency copies.

The schematic diagrams, apparatus and cable lists shall have a size of A4 except for the transparency copies of schematic diagrams that shall be in A3.  Scales to be used on the drawings shall be 1:10, 1:20, 1:40, 1:50 and multiples of this series.

Documentation shall be in accordance with IEC 61082. Symbols for electrical components shall be according to IEC 60617. The Contractor shall also integrate all facilities in common item designation system following IEC 61346.

The Contractor shall during the total project time maintain a List of Documentation to be updated by him whenever needed.  The List of Documentation shall include the date of original issue of each document submitted as well as the dates of every revision. The List of Documentation shall also include a time schedule for the submittal of the documentation.

Initial drawings for construction must be replaced by as built drawings after construction and commissioning.

All drawings shall be submitted in accordance with the provisions in this Section and shall become the property of the Employer.

All construction works shall only commence upon submission of approved blueprint drawings to the employer.

### Operation and Maintenance Manuals

Before the Facilities are taken over, the Contractor shall supply five (5) sets of operation and maintenance manuals together with as built drawings of the Facilities as built. These shall be in such details as will enable the Employer to operate, maintain, adjust, and repair all parts of the Works. The manuals and drawings shall be in English.

The Facilities SHALL NOT be complete for the purpose of taking over until such manuals and drawings have been supplied to the Employer.

### Quality of Materials

All materials supplied under this Contract shall be new and of the best quality and of the class most suitable for working under the conditions specified and shall withstand the variations of temperature and atmospheric conditions arising under working conditions without distortion or deterioration and without setting up of undue stresses in any parts and without affecting the suitability of the various parts of the Works for which they were designed.

### Contractor's Quality Assurance Procedures.

The Contractor shall submit for approval a programme of quality control and inspection procedures to assure that the product during manufacture and on completion complies with the specified requirements.  The programme shall relate the quality control and inspection activities to the production cycle.  In support of the quality control and inspection programme the Contractor shall provide details of quality control and inspection procedures available for use in the execution of the Contract.  The Contractor shall retain responsibility for quality control and inspection activities made by his sub-contractors and shall indicate on the programme which items are to be sub-contracted.

### Guarantees and Particulars.

The Facilities shall comply with the technical guaranteed data stated in the Guarantee Schedules Section VII.  The Contractor shall be responsible for any discrepancies, errors and omissions in the particulars and guarantees, whether such particulars and guarantees have been approved by the Project Manager or not.

### Places of Manufacture and Sub-Contractors.

The manufacturer's identity and places of manufacture, testing and inspection before shipment for the various portions of the Contract Facilities shall be specified in the Technical Schedules and shall not be departed from without the agreement of the Project Manager.

As soon as practicable after entering into the Contract, the Contractor shall, having obtained the Project Manager's consent in accordance with the Conditions of Contract, enter into the Sub-contracts he considers necessary for the satisfactory completion of the Contract Facilities.

All Sub-contractors and Sub-suppliers of components and materials shall be subject to the approval of the Project Manager.  Information shall be given on each Sub-order sufficient to identify the material or equipment to which the sub-order relates, stating that the material is subject to inspection by the Project Manager before dispatch.

During the manufacture and assembly of the contract facilities the Contractor shall arrange for training of ZESCO engineers whenever requested

### Factory Tests.

Factory tests on equipment shall be made according to the applicable IEC Standards, or as specifically specified or, if such are lacking, according to standards approved by the Project Manager. Factory Acceptance Tests (FAT’s) shall be witnessed by the Project Manager for ZESCO (or his representative) and the Project Manager.

Routine tests shall be made on each unit of all equipment.

Type tests shall be made on one unit of each type of different equipment.  Instead of carrying out the type tests the Contractor may submit suitable certificates of tests made on equipment of the same type; however, the Employer reserves the right of accepting these certificates or to reject them partially or totally.

Measuring apparatus shall be approved by the Project Manager and if required shall be calibrated at the expense of the Contractor at an approved laboratory.

Whenever requested the Contractor shall arrange for pre-delivery test of each equipment/contract facility.

### Installation, Testing at Site, Commissioning.

The Contractor shall carry out installation, testing at site and commissioning of the Plant and Equipment specified in the Specifications.

All work, methods of work and workmanship, whether fully specified herein or not, shall be of the highest order in all respects. The generally accepted requirements and commonly recognised good practice for first-class work of the nature are to be adhered to.

The Contractor shall provide all staff, such as engineers, supervisory staff, skilled and unskilled labour necessary to carry out and complete the Facilities on schedule as specified.

The Contractor shall provide all vehicles, erection, tools and equipment necessary to carry out the Contract Works, including transport of equipment and personnel.  At the completion of the Contract, the Employer reserves the right, at his discretion, to take over vehicles, any tools, special tools, test equipment and other construction equipment used by the Contractor in connection with the Contract, at depreciated prices in Zambian Kwacha to be mutually agreed upon at that time.

A complete list of vehicles and erection equipment together with their value, shall be provided by the contractor.

Testing and/or inspection at site shall be carried out by experienced test engineers.  Functional tests shall be inherent in all test procedures.  The Contractor shall record the test results in an approved form in such a manner that the test reports can be used as the basis for future maintenance tests.  Test methods and equipment shall be noted on the test sheets.

A complete test report in 4 sets of any such tests and/or inspections shall be handed over to the Project Manager not later than one month after the Facilities being commissioned. The test engineers shall at site keep a complete record of correction made during testing and one set of corrected drawings shall be kept at site after commissioning and one set handed over to the Project Manager.

Commissioning (or pre-commissioning) will be carried out by the Contractor in the presence of the Employer's engineers and the Project Manager immediately after the issue of the Completion Certificate. The Contractor shall prior to commissioning draw up a detailed commissioning schedule for approval showing the sequence to follow step by step in all connections, including control of phase sequence and other pertinent factors. Switching of live equipment will be performed by the Employer.

### Work on Live Substations

The work will primarily be done on substations in operation. Minimisation of outage time and adaptation to operational constraints are therefore of paramount importance. All work must be planned with this in mind. The Contractor must obey to all instructions and safety rules given by the Government and the Employer and must strictly follow all instructions from the Employer’s supervisory personnel. The Contractor shall appoint his Engineer/Technician who will be authorised to receive work permits at the work sites as required by safety rules. All outages shall be discussed with the Employer and the Project Manager at least one week before the outage is required.  The Contractor will normally only be allowed to have one high voltage circuit out of operation at a time. No work must start before Employer’s site manager has authorised the work, established the required earthing and marked the safe area. All switching on live parts shall be done by the Employer.   In the rare cases where more than one circuit have to be taken out of operation the Contractor must be prepared to do the work during nights or at off-peak time. The Contractor and his personnel must respect the physical constraints as well as constraints for scheduling set by these circumstances. However, the Employer will co-operate in making the work conditions and the scheduling as efficient as possible for the Contractor and keep a responsible person with switching authority at site during all working hours (including nighttime).

If physical constraints make it necessary to replace cabinets needed for operation, the Contractor must as far as possible erect and connect the new cabinets temporarily adjacent to the one in operation. A quick disconnection and removal of the old cabinets can then be performed, and the new cabinets pulled in with most of its cables already fitted.

Location of new cabinets shall be approved by the Project Manager and a proposal for such shall be given by the Contractor one month prior to erection.

The Contractor shall be responsible for removal of old equipment and cables and for safe disposal of environmentally hazardous substances such as battery acid and transformer oil. The Contractor will also be responsible for the removal, handling, and consignment to an agreed site of components containing PCB. The Contractor may at his discretion subcontract the handling and storage of the components containing PCB to a contractor specialised in the handling of PCB waste material.

### Accommodation of Contractor's Personnel.

The Contractor shall make his own full provision for temporary accommodation to suit his requirements.

### Packing, Transportation and Storage.

The Contractor (or his subcontractors) shall provide such packing of the shipments as is required to prevent their damage or deterioration during transit to their destination as indicated in the Contract.  The packing shall be sufficient to withstand, without limitation, rough handling during transit and exposure to extreme temperatures, salt and precipitation during transit and open storage.  Packing case size and weights shall be selected by taking into consideration, where appropriate, the remoteness of the goods' destination and the absence of heavy handling facilities at all points in transit.

The following information must be clearly stenciled or printed on each packing case, crate, cask, drum, bundle or loose piece, care being taken that the number and other particulars on each package agree with those entered in the packing list accompanying the Invoice:

-	Employer's Identity

-	Supplier's Identity

-	Destination

-	Contract No.

-	Package No.

-	Item Code

-	Weight, dimensions

-	Sub-Project (Substation Identity).

The part on which the marking is done must be clear and smooth with the lettering in black on a white painted background.  In the case of wooden packing cases, crates, casks and metal drums, the marking must be upon the body of the package and will not be accepted upon a batten fastened on the case, etc.

In the case of bags, bundles and loose pieces, the shapes of which do not permit the marks to be put on the actual package, each bag, bundle, or loose piece shall have two metal labels securely fastened to it. Each label being die-stamped with the above particulars. Each label must have two holes, preferably one at each end, and must be fastened to the package by two wires no smaller than 16 SWG, each fastening being independent of the other.

Equipment belonging to different substations shall not be mixed, but kept in separate packing cases, bundles or similar.

The Contractor shall be responsible for all transportation; from works to port of shipment and onwards to port of unloading, all materials handling and transport to sites. For materials supplies only, point of destination is the Contractor’s store. The Contractor will be responsible for the recovery, documentation, and consignment to an agreed store of all redundant equipment.

Storage, maintenance and insurance of stored materials and equipment shall be the responsibility of the Contractor. The Contractor shall establish his own stores and all the equipment shall be consigned to the Contractor’s own premises. Care shall be taken to assure adequate storage to avoid damage to equipment due to rain or strong sunshine.

GENERAL TECHNICAL SPECIFICATIONS

SECTION III CONTENT

3 GENERAL TECHNICAL SPECIFICATIONS	120

3.1 General	120

3.2 Standards	120

3.3 Definitions	120

3.4 System Characteristics	121

3.5 Short Circuit Withstandability	121

3.6 Phase Relationship	122

3.7 Units	122

3.8 Drawings	122

3.9 Ambient Temperatures, Relative Humidity, Wind Pressure	122

3.10 Altitude	123

3.11 Auxiliary Power	124

3.11.1 Power Supply	124

3.11.2 Auxiliary Power Interruptions	124

3.12 Operation and Control	124

3.13 Interface and limits of supply (battery limits)	125

3.13.1.1 Control and Protection	125

3.14 Electric and Water Service During Construction	127

3.15 Materials	127

3.15.1 Electrical Equipment Materials	127

3.15.2 Standardisation of Equipment	127

3.15.3 Surface Treatment and Painting, Electrical Equipment	127

3.15.4 Insulating Oil	128

3.15.5 Sulphur hexafluoride gas (SF6) and Gas Treatment Plant	128

3.15.6 Bolts, Studs, Nuts, Screws, Washers, etc.	129

3.15.7 Nameplates and signs	130

3.15.8 Motors	130

3.15.9 Motor control gear	131

3.16 Design and Construction	132

3.16.1 General Requirements	132

3.16.2 Switchboards and Panels	133

3.16.3 Relay Testing Facilities	134

3.16.4 Wiring and Terminal Blocks	134

3.16.5 Earthing (Grounding)	136

3.17 CABLES	136

3.17.1 General	136

3.17.2 Design	137

3.17.3 Cable Laying and Routing	138

3.17.4 Laying	138

3.17.5 Diagrams and Calculations	139

3.17.6 Tests	139

3.18 SITE AND COMMISSIONING TESTS	139

3.18.1 General	139

3.18.2 Test of Wiring	139

3.18.3 Test of Relays	140

3.18.4 Test of D.C. Circuits	140

3.18.5 Test of Instruments	140

3.18.6 Tests on Conductors, Insulators and Accessories	140

3.18.7 On Load Test	141

3.18.8 Tests on the Switchyard on Site	141

3.19 Structural Steelworks	141

3.20 Civil Works	141

# GENERAL TECHNICAL SPECIFICATIONS

## General

This Chapter covers the general technical specifications of the equipment to be supplied in accordance with Section I, Scope of Works. If there is conflict between the General and the Particular Specifications, the latter shall prevail.

## Standards

Ratings, characteristics, tests, and test procedures, etc. for the electrical equipment encompassed by this specification shall comply with the provisions and requirements of the Recommendations of the International Electro-technical Commission (IEC), unless otherwise expressly stated, Particular Technical Specifications.  Where the IEC Recommendations do not fully cover all provisions and requirements for the design, construction, testing, etc. and for equipment and components which are not covered by IEC recommendations, recognised national standards may also be applied as well as the rules of CEE (International Commission for the approval of Electrical Equipment) and the standards of CENELEC (Comité Européen de Normalisation Electrotechnique).

The latest revision or edition in effect at the time of invitation to bid shall be used.

The precise Standard, complete with identification number, to which the various equipment and materials are manufactured shall be specifically stated by the Bidder.

In case of conflict or disagreement between the particulars of the Standard adopted by the Bidder and the particulars of this Contract Specification, this Specification shall prevail over the Standard.  All conflicts or disagreements mentioned above, must be clearly stated. The materials and equipment offered shall be deemed to comply in every respect with this Specification both in manufacture and in performance, and compliance thereof be insisted upon without additional cost to the Employer.

## Definitions

Whenever the following terms or words are found in the specifications and/or other documents, they shall have the following meaning:

"High Voltage Equipment" (HV):

Mostly used for equipment provided for a maximum operating voltage higher than 36 kV (generically also used for voltages down to 1000 V).

"Medium Voltage Equipment" (MV):

Equipment provided for a maximum operating voltage higher than 1000 V and up to 36 kV.

"Low Voltage Equipment" (LV):

Equipment provided for operation at 1000 V or below.

## System Characteristics

The basic characteristics of the electrical systems and equipment shall be as follows:

HV Equipment, 330 kV

- Maximum operating voltage 362kV, 3-phase, 50Hz, effectively earthed neutral.

- Rated switching impulse withstand voltage to earth 1050kV peak.

- Lightning impulse withstand voltage 1300kV peak.

HV Equipment, 132 kV

- Maximum operating voltage 145 kV, 3-phase, 50 Hz, effectively earthed neutral.

- Lightning impulse withstand voltage 650 kV peak.

- Nominal power frequency withstand voltage 275 kV.

MV Equipment, 33 kV

- Maximum operating voltage 36kV, 3-phase, 50Hz, transformer (NEC) earthed neutral.

- Lightning impulse withstand voltage 170kV peak.

- Nominal power frequency withstand voltage 70kV.

LV Equipment, 0.4 kV

- Maximum operating voltage 420V, 3-phase, 50Hz, loaded and effectively earthed neutral.

- Nominal power frequency withstand voltage 2kV.

## Short Circuit Withstand ability.

The equipment shall be designed to withstand the most severe short circuit stresses expected during service conditions. The minimum symmetrical short circuit capacity at nominal operating voltage shall be as follows:

-	330 kV system		23 000 MVA

-	132 kV system		7 000 MVA

-	66 kV	system		3,000 MVA

-	33 kV system		 	2 500	MVA

-	0.4 kV system		20 MVA

For all current carrying parts the permissible short circuit duration shall be at least one (1) second.

The dynamic or momentary short circuit current on which the equipment design shall be based shall be computed by multiplying the r.m.s. value of the symmetrical short circuit current by the factor 1.8 x .

## Phase Relationship

The phase relations and designations shall be in accordance with the existing system of the Employer.  The actual phase sequences will be made known to the Contractor at a later date, but not later than 1 month from date of commencement. The standard phase colours are Red, Yellow, Blue (RYB).

## Units

The SI-system (meter, Newton, second) shall be used throughout the works covered by this Specification.

## Drawings

The drawings attached to in this bid are of informative character and may be subject to alterations.

## Ambient Temperatures, Relative Humidity, Wind Pressure

Unless otherwise specifically stated, Particular Technical Specifications, any equipment, component and assembly shall be designed for the following service conditions:

Ambient air temperature			Outdoor	Indoor

-	Maximum			+45°C		+45°C

-	24-hour average maximum	+35°C		+35°C

-	Minimum	 		 -1°C		 -1°C

Relative humidity	 			 80%	 	 80%

Maximum wind pressure on project area

of conductors and cylindrical objects		430 N/m²

Maximum wind pressure on steel members

on 1.5 times projected area			820 N/m²

Rainfall conditions				800-1700mm/year

Maximum 160mm in 24hrs

Wherever any of these maximum or 24-hour average temperatures exceed the normal service condition temperatures of the IEC Recommendations for the relevant equipment, or of such other standard which is approved to be applied, the permissible temperature rises of the IEC Recommendations shall be reduced by the same amount as the difference between the above figures and the normal service condition temperatures.

These reduced temperature rises shall be guaranteed by the Contractor.

For cables in the ground 40oC shall be taken as design value for ambient (ground) temperature.

## Altitude

The altitudes of the plants shall be taken as 1500 metres above mean sea level.

## Auxiliary Power

### Power Supply

The power for the auxiliary service is in general supplied from the station transformers connected to the power transformer’s 11kV tertiary windings for Transmission substations or 33kV bus bar for Distribution substations.

The AC low voltage main distribution system shall have a voltage rating of 380 volts, ±10%, 50Hz. The system shall be 3-phase, 4-wire with the transformer neutral grounded (TN-S)

For lighting, small power socket outlets, domestic appliances, and other small power, 220V single phase shall be used.

The DC auxiliary supply shall be.

-	For control, protection, and alarm circuits

110V / 220V insulated will be preferred.

-	For power line communication equipment, PABXs and RTUs 48V

negative pole grounded.

      - All bulbs and any voltage sensitive relays fed by DC shall be rated 	240/125 V.

### Auxiliary Power Interruptions

The AC auxiliary power during normal operation is fed from the station transformer.  The Contractor shall ensure that the plants as a whole will function properly under the conditions which will occur due to tripping of one station transformer, which require minimum 10-hour service time for the sake of batteries.

## Operation and Control

The operations and control procedures as well as monitoring and protective devices for the plants are described in Particular Technical Specifications.

The Contractor shall take all measures and furnish all requirements necessary for effecting the intended method of operation and control.

The primary functional control shall be from the National Control Centre (NCC) in Lusaka (supervisory control) with secondary control from the control rooms at each station (remote control). The control shall include operation and indication of all circuit breakers and isolating switches for 330kV, 132kV, 33kV. Position indication at the NCC shall in addition be facilitated for the earthing switches. For on-load tap changers, both position indication and control is required at NCC and in the control room. Local control of all station switchgear at the respective switchyards shall be possible.

Interlocking devices shall be incorporated in the control circuits in the quantity needed to guarantee non-interruption and correct sequence of operation of the equipment.  Protective devices shall be supplied in accordance with the Particular Technical Specifications, and the particular needs of the equipment furnished with the aim of ensuring a safe and reliable operation of the facilities in the event of electrical and mechanical disturbances or in case of mal operation by the plant personnel.

In general, all alarms, position and status indication provided in the control room, shall be transferred to the NCC.

All equipment, instruments and devices in the substation necessary for supervisory, remote and local control as well as for protection, signalling and indication shall be included in the Bid and the Contract resulting therefrom, it being understood that the enumeration found in Scope of Works, in this respect is indicative but not limiting.

## Interface and limits of supply (battery limits)

The Contractor shall supply, erect, install and commission all equipment with foundations and support structures. The contractor shall also supply complete documentation for the Plant and Equipment. In stations where the control system is replaced, the Contractor shall supply complete revised documentation for the new and old plant. In stations where the control system is not replaced, the Contractor shall integrate the equipment in the existing documentation. This is a turnkey project.

#### Control and Protection

In stations where the control gear is totally replaced or integrated, the Contractor has the following obligations.

- Supply and erect Field Cabinets where specified in Scope of Works

- Supply and connect control equipment and control cables up to field cabinets (marshalling boxes)

- Replace control and power cables from primary equipment to field cabinets.

- Supply and connect cables for AC and DC auxiliary supply to the control system and through this to the plant.

- Supply and connect cables between the control system ( and the Main Distribution Frame if required)

- Supply and connect cables from protection to communication system (Optic fibre terminal equipment link)

- Supply complete documentation for the old and new plant including HV equipment and measuring circuits.

- Removal of superfluous equipment and cables

In stations where only the protection or specific units of the control system is replaced the Contractor is responsible for:

- Supply, erect, install and commission the control and protection units.

- Supply of cables and connection of the protection with the measuring transformers and the control system

- Integrate the equipment in the existing documentation of the plant.

- Supply and connect cables from protection to communication system (optic fibre link)

All connections shall be made and all equipment and drawings be provided by the Contractor to ensure a proper operation of the complete plants, although this should not be specifically mentioned in the Scope of Works Section.

The Employer will supply to the Contractor within one month from the date of commencement all documentation available for adaptation to the existing plant. However, as the documentation is neither complete nor updated it will be necessary for the Contractor to complement with own investigations to get a full picture of the situation.  The Employer will assist in making such investigations.

The switchgear and control-system shall constitute a complete and functioning system together with the existing power transformers.

The Contractor shall supply, lay and connect all cables between the control room cabinet and the transformer and feeder bay marshalling boxes and cabinets as well as supply all AC and DC power and control cables for motors, control, indication and alarm purpose.  The Contractor shall also provide all necessary connections to the control system from other sources like voltage and current transformers, etc.

The Contractor shall connect all HV apparatus to the grid and supply clamps. He shall supply and erect the control cables from the circuit breakers to the marshalling kiosk for the bays.

All drawings and other documentation regarding adaptation to existing plants shall be submitted to the Project Manager for approval.

## Electric and Water Service During Construction

380/220V, 3-phase/single phase, 50Hz alternating current will be made available at sites on commercial terms from the Employer. All tools and equipment supplied by the Contractor shall be suitable for this supply system. The Employer, while endeavouring at all times to maintain the supply, can accept no responsibility for the consequences that may arise from the failure or cessation of the electric supply. The contractor shall source construction supply water at their cost.

## Materials

### Electrical Equipment Materials

All materials incorporated in the equipment supplied shall be new and of first-class commercial quality, free from defects and imperfections.

Copper and aluminium used as electrical conductors shall be of the electrolytic type and comply with the respective IEC, IEEE, ASTM or DIN Standards.

### Standardisation of Equipment

The Contractor shall be responsible for the standardization of all small mechanical and electrical equipment, materials, and devices for the Works. The Contractor shall arrange and perform the necessary co-ordination work with subcontractors for the purpose of such standardization.  Such equipment, devices, fittings, etc. shall comprise, but not necessarily be restricted to, the following:

- Electrical instruments and meters

- Terminals and terminal blocks

- Primary, secondary, and auxiliary relaying devices

- Contactors, fuses, miniature breakers, and the like.

- Control devices and control switches

- Lamps, bulbs, sockets, plugs, etc.

- Lubricants

- Oil

Where electrical sockets are specified, British Standard Sockets shall be used. Single phase sockets shall be 13A for square plugs if nothing else is specified.

All indication lamps shall be of the light emitting diode type and be replaceable without use of special tools.

### Surface Treatment and Painting, Electrical Equipment

Panel boards, cubicles, cabinets, etc. in dry rooms shall have interior surfaces painted with at least one priming and one finishing coat of anti-corrosion paint. Exterior surfaces shall be adequately treated to be substantially corrosion resistant, with one priming coat, and two finishing coats.

Outdoor installations and indoor installations in wet and damp rooms shall at least have two priming coats and two finishing coats of anti-corrosion paints applied after perfect cleaning. In addition, acid resisting type paint shall be applied at all the polluted areas. Parts that cannot be readily painted shall be hot dip galvanized.

All hot dip galvanizing shall be in accordance with BS 729 or other internationally approved standards.

Steel below ground shall, in addition to galvanizing, be protected with Bitumen or a substance of similar quality.

The particulars of priming and finishing paintings shall be stated in the Bid, with specifications of paint, together with a listing of colours available, for each of the plant and equipment.

The Employer is not bound to accept the finishing colour proposed by the Bidder.  Determination of colour shall be at the option of the Employer and shall be finalized at the time of approval of drawings.

### Insulating Oil

All electrical equipment requiring insulating oil or other insulating liquids shall be furnished with the first filling including flushing, if required.

The Contractor shall endeavour to employ, as far as practicable, one type and make of insulating oil only for all the electrical equipment.

Mineral Insulating Oils shall comply with the requirements of IEC 60296:2012.

### Sulphur hexafluoride gas (SF6) and Gas Treatment Plant

The SF6 gas shall comply with the requirements of IEC 60376. In addition to the quantity of gas required to fill the equipment supplied, 20% shall be supplied as spare.

The high-pressure cylinders for shipment and storage of the SF6 gas shall comply with the applicable national regulations.

The contractor shall supply and install substation breakers with SF6 equipment:

1 set per substation of SF6 gas filling equipment

- 1 set per substation of SF6 leak detector equipment

- 3 x 45 kg SF6 gas bottle filled with SF6 gas.

The gas treatment plant(s) to be supplied shall have sufficient storage facilities for the maximum quantity of gas that could be removed when carrying out maintenance or repair work on the largest section of the switchgear.

All the necessary pipes, couplings, flexible tubes and valves for coupling to the switchgear for filling or evacuating all the gases to be used, with all necessary instructions for the storage of this equipment, shall be provided.

### Bolts, Studs, Nuts, Screws, Washers, etc.

All bolts, studs, nuts, etc., shall have a standard metric threading and conform to the relevant standards as regards shape and tolerance. They shall be marked with the manufacturer's symbol and class of strength.

All bolts, studs, nuts, washers, screws, etc., above 10 mm diameter, if not in stainless steel or other corrosion-resistant material, shall be hot-dip galvanized, except for bolts above Strength Class 8.8.  In this case, corrosion-resistant material will be required.

Bolts, etc., smaller than 10 mm diameter shall be electrolytic zinc-coated if not provided in stainless steel or other corrosion-resistant material.

Bolts, nuts, studs and screws which require frequent tightening and unbolting during inspection or maintenance procedures shall be of stainless steel.

All bolts and nuts shall be hexagonal, either normally or of the round head socket type and secured in an approved manner against becoming loose during operation. Wherever possible, bolts shall be fitted in such a manner that in the event of the nut working loose and falling off, the bolts will remain in position.

The Contractor shall supply the net quantities plus 5% of all permanent bolts, screws and other similar items and materials required for installation of the works at the site.  Any such rivets, bolts, screws, etc., which are surplus after the installation of the equipment has been completed shall become spare parts and shall be wrapped, marked and handed over to the Purchaser.

Taper pins shall have threaded stems with nuts where dismantling of the pins is likely to be required.

Bolt or stud shall project through its nut for at least 2 threads but not more than 7 mm or 4 threads, except when otherwise approved.

### Nameplates and signs

All permanent equipment of the works shall be provided with a securely fixed nameplate in English showing the maker's name, model, serial number, year of manufacture, main characteristic data of the respective equipment and further relevant information specified in the applicable standards or necessary for the proper identification of the equipment involved.

The Contractor shall supply all label plates and other labelling (of the screw-on type with engraved letters) on control boards, control desks, panels and other places where required for operational, functional and safety reasons. The labelling shall also indicate the physical designation code for the compartment.

All outdoor nameplates and signs shall be made of non-corrosive weatherproof material as trafolyte aluminium or stainless steel. Lettering shall be engraved.

Trafolyte nameplates and signs shall have white lettering on a black background. For aluminium and steel signs shall have black lettering on metallic background. For warning signs red background shall be used.

Labels shall be provided for all apparatus such as relays, switches and fuses contained in any cubicle. Labelling shall be clear, concise and adequate and shall be to approval.

Labels shall also be installed in clear and observable locations of primary equipment like switch gear, transformer, surge arrester, measuring transformers etc. These labels shall indicate names of the equipment e.g., “SF6 Circuit Breaker”, “Isolator”, “330/132kV, 160MVA Transf no.1”, “Auxiliary Transf. No.1”, “Main Busbar” etc. The phases shall be labelled, Red, Yellow, and Blue. The labels shall be located at suitable points appropriate to the equipment and phase conductor being described. The labelling of phase colours shall not be in full words but simply “R”, “Y” or “B” and painted in the corresponding colour.

### Motors

All motors shall comply with IEC 60034 and dimensions with IEC 60072.  They shall be capable of operating continuously under actual service conditions without exceeding the specified temperature rises, determined by resistance, at any frequency between 48 and 51 Hz together with any voltage between +/-5 percent of the nominal value on the transmission network and +/- 10 percent of the nominal value on the distribution network.

All motors shall be totally enclosed (IP 23 or better), and if situated in the open they shall be weatherproof and suitable for outdoor operation (IP 54). They shall be provided with a suitable means of drainage to prevent accumulation of water due to condensation and with suitable means of breathing.

Motors operating in an ambient temperature not exceeding 40°C shall have Class 'F' insulation or better, but where the ambient temperature may exceed this figure or where the motor may be appreciably affected by conducted heat, Class 'B' temperature rise shall be used.

All motors shall be suitable for direct starting at full voltage as well as 10% under-voltage.

Motors shall have sealed ball or roller bearings.

The three-line connections of A.C. motors shall be brought out to a terminal box.  The terminal arrangement shall be suitable for the reception of copper and aluminium cable. Terminal markings shall be made in a clear and permanent manner and shall comply with IEC 60034.  A permanently attached diagram or instruction sheet shall be provided giving the connections for the required direction of rotation. All terminal boxes shall be of the totally enclosed type IP 65, designed to exclude the entry of dust and moisture and sealed from the internal air circuit of the motor.  All joints shall be flanged with gaskets of neoprene or other approved material. Natural rubber insulation shall not be used.

Where single phase motors are employed, the motors shall be grouped so as to form, approximately, a balanced three phase load.

### Motor control gear

Control gear shall comply with the requirements of IEC 60947, the control gear being rated according to the duty imposed by the application. No replacement of equipment shall be necessary after short circuit (ref. IEC 60947).

Motor contactors shall comply with IEC 60947 class of intermittent duty 0-3 with type IP 52 enclosure protection and a utilisation category AC4.  The contactors, and their associated apparatus shall be capable of switching the stalled current and shall have a continuous current rating of at least 50% greater than the full load current of the motors they control.

The operating currents of overload trips fitted to motor contactors shall be substantially independent of ambient temperature conditions, including the effect of direct sunlight on the enclosure in which the contactors are installed.

Where small motors are connected in groups, the group protection shall be arranged so that it will operate satisfactorily in the event of a fault occurring on a single motor. The control and protection equipment shall be accommodated in the control cabinet or marshalling kiosk.

Each motor or group of motors shall be provided with control gear for starting and stopping by hand and automatically. Overload, earth leakage and single-phasing protection shall be provided. Facilities for padlocking the supply in off position shall be provided.

## Design and Construction

### General Requirements

The Facilities shall be designed for reliable and safe operation under all conditions. Means shall be available to simplify inspection, testing, maintenance and repair of the plants. The design shall also include all necessary provisions ensuring the safety of the operation and maintenance personnel.

The substation design should be such as to minimize the number of levels of conductors and to ensure that the consequences of a failure of one set of high-level conductors are limited to the loss of that circuit and a single busbar section. This principle shall also be applied to earth wire conductors.

All electrical equipment, apparatus and devices shall be of suitable design for satisfactory operation under the climatic conditions prevailing at the sites. The equipment shall also operate satisfactorily under normal load and voltage variations as well as during abnormal conditions to be expected during services including those due to faulty synchronizing and short circuit if these remain within the assigned ratings of the apparatus.

All electrical connections and contacts shall be of ample cross section and capacity for carrying continuously the specified currents without undue heating and shall be secured by bolts or set screws of ample size, fitted with locknuts or lock washers of approved types.

All outdoor apparatus including bushing insulators and fittings shall be designed so that water cannot collect at any point.

Cubicles, cabinets, and similar enclosed compartments containing electrical equipment shall be adequately ventilated and drained.  All major or important compartments containing electrical equipment shall be provided with internal lighting facilities and a 13 A single phase socket.

All interior surfaces of electrical apparatus, cabinets, etc. including contactors, relays, coils, etc. shall be treated in an approved manner to prevent mould growth.  Such treatment shall in no way interfere with the proper operation of the equipment either electrically or mechanically. All cabinets shall be vermin proof with screened openings.  Outdoor cabinets shall be dust and waterproof (IP 54) and provided with thermostat-controlled heaters to inhibit collection of moisture.  All cables shall be termite proof design, e.g. by brass tape or equal techniques. Openings for drainage of condense shall be provided at the lowest point in the cabinets.

Larger assemblies such as switchboards, etc. shall be designed to enable suitable transportation divisions adapted to the local conditions within the plants.

All outdoor control cabinets shall be lockable by padlocks with key system to be approved by the Employer. The key shall be marked by clear key tags of trafolyte with indications engraved.

### Switchboards and Panels

Switchboards, control, relay and metering panel boards shall be of robust construction, formed of a steel frame and covered with smooth steel plate.  The steel plate shall be properly stiffened to prevent distortion.  Whenever required, hinged steel doors with latches shall be provided; doors shall be lockable by means of approved locks.  The lock shall be of the same type throughout the plants.  Mounting of protective relays in plate doors will not be accepted. The panels shall be dust proof (IP23) with cable entrance through glands.

All termination shall be accessible without dismantling or unscrewing any components (apart from removing plug-in units). Panels shall normally be covered at their rear with hinged doors if rear access are required.

The frames of the boards shall be designed to permit firm anchoring on the floor.  The frames shall permit easy erection, and allowance shall be made for extension of the board by similar additional panels.

The Contractor's supply shall include all necessary mounting brackets, framing, foundation bolts and respective embedded metal, if required, to permit proper installation of the boards.

Unless otherwise specified or agreed upon, all instruments, apparatus and devices on panel fronts shall be provided for mounting in standard 19” rack frame or plates fitted to 19” racks.  The racks may be supplied as a hinged, swing-out, frame to allow inside access. The frame and the panels must be strengthened to allow swing out of a fully loaded frame without any support and without any temporary or permanently distortion or deformation.

Relays shall be provided with transparent cover or transparent doors. The cover or doors shall be hinged to allow resetting and adjustment.

### Relay Testing Facilities

Each protection relay shall be provided with facilities for the connection of relay testing equipment.  The facilities shall include at least 4 sets of plugs and cables for each type of relay for connecting the testing equipment and switches for disconnecting the primary circuit of the relay, short circuiting current transformer circuits and disconnecting the tripping circuit.

### Wiring and Terminal Blocks

Small wiring shall be PVC insulated with stranded copper conductor suitable for operation at voltages below 1000 V in compliance with the provisions of the applicable IEC Recommendations.  Conductors shall not be smaller than 2.5mm² for current transformer, control circuits and alarm circuits.  The selection of conductor sizes for current transformer circuits shall be supported by calculations. CT and VT terminals in marshalling boxes and control panels shall be provided with special disconnectors to ensure the safe disconnection of CTs and VTs

Wiring inside boards, desks, cubicles, etc. may, if practicable and approved by the Project Manager, be of 2.5 mm² size conductor.

For wiring within boards, the "bunch" pattern shall be adopted.  For a small number of connections, wiring may be grouped using flexible plastic bands or equivalent.  For many connections, a system using support strips or U-shaped troughs (with covers) shall be used. The latter principal arrangement shall apply for cable distribution racks.

The screens or screened pairs of multicore cables shall be earthed in a way that complies with the rules of EMC protection.  The position of the earthing connections shall be shown clearly on the diagram.

It shall be possible to work on small wiring for maintenance or test purposes without making a switchboard dead.

The wiring identification shall have numbered ferrules, sleeves or other approved means.  To avoid opening of current transformer circuits by mistake, the terminal blocks for such circuits shall be clearly marked with a danger sign.  All wires associated with the tripping circuits shall be provided with red ferrules marked "Trip".

All cables, control wiring and terminals shall be marked in a systematic manner, both on the drawings and on the cables, wires and terminals themselves. The markings shall be in accordance with a system presented and co-ordinated by the Contractor throughout the plants, but subject to approval by the Project Manager. The cable marking shall be fireproof.

All wiring shall terminate at terminal blocks. The latter shall be of the moulded type and provided with barriers to separate power from control cables. It shall be possible to replace a single terminal block without dismantling a whole row.  Where appropriate, terminal blocks shall be equipped with facilities for testing, such as short-circuiting, separating, plugging in, etc. Terminal blocks shall be located at least 300 mm from the bottom of the panel and shall be easily accessible.  They shall be clearly marked, the designations being those entered in the respective wiring diagrams.

Terminal blocks for different voltages shall not be intermixed.  The blocks shall be grouped for each voltage, and they shall be clearly marked for easy identification of the system voltage.

Terminal blocks using screws acting directly on the wire (conductor) as well as spring type terminal blocks are not acceptable.  To avoid squeezing of the wire, the screw pressure shall be applied by a pressure plate having smooth edges.

Only one conductor shall be connected to each side of a terminal block and the branch-offs shall be made by interconnecting the necessary number of neighbouring blocks by means of copper strips, unless otherwise approved by the Project Manager.

Stranded conductor ends shall be fitted with a suitable crimped thimble (bootlace ferrule type). The thimble shall be of correct type and length according to the core size. Each wire shall be separately terminated with crimped termination unless otherwise approved.

All control cables shall be multistrand wire armoured and all cores clearly labelled and multi stranded.

### Earthing (Grounding)

Each electrical device as well as equipment made of conducting material shall be provided by an earthing screw of sufficient diameter. The contractor shall be responsible for the connection of the equipment to any existing earthing mesh.

Moreover, the Contractor shall take the necessary measures and furnish the required material for the safe earthing of:

(1)	All steel structures, metal parts and overhead ground wires of the switchyard

(2)	All fences of the station, whereby for outer fences special care shall be taken to avoid injurious step and touch voltages for personnel standing outside and inside these fences.

(3)	All metal parts, even if these do not constitute a conducting part of an electric system of the plants, such as machinery, operating desks, piping, sewers, rails, metal tanks, lighting, fixtures, cable racks, etc.

(4)	All operational electric systems such as power and instrument transformers, lightning arresters etc.

All connections between equipment and the earthing network shall be exposed (not embedded) and easily accessible for checking of the transition points.  Bare conductors, as part of the earthing system, embedded directly in the concrete will not be accepted.  Similarly, bolted connection of metallic constructions, do not form an acceptable earthing connection. Steel structures shall not be part of the earthing structure.

The layout drawings, the detailed calculations for the earthing system and the relevant data which the Contractor will use as basis for his design, shall be submitted to the Project Manager for approval.  The Contractor shall also be responsible for performing all measurements and final checking of the whole of the earthing system.

## CABLES

### General

This chapter covers the technical requirements of the external cables and accessories as well as cable laying for all installations described under these Specifications.

The supply and installation of the internal cables between the various parts of equipment shall be included in the Chapter in which the relevant equipment is specified.

If, however, a considerable change in location of a switchyard should be made, the price shall be reduced or increased proportionally to the amount of reduction or increase in the distance between the switchyard and the control building.  No price adjustment shall be made for deviations of less than 25 metres.

The cables shall be delivered in full lengths, and consequently no joints are permitted.  All accessories shall be provided, such as potheads, galvanised and painted steel supports, clamps, etc.

### Design

The design, manufacture, rating and testing of all cables shall comply with the provisions and requirements of the applicable IEC recommendations, supplemented by recognised national standards if necessary. The cables shall be rated for max. 5% voltage drop by full load for transmission voltages and max. 10% voltage drop by full load for distribution voltages.

40oC maximum design ambient temperature shall be applied for all cables internally in the switchyard, between the switchyard equipment and the control building and inside the control building.

All cables shall be of termite proof design, e.g. by brass tape or equal approved techniques.

Wherever the risk of inductively transferred disturbances during abnormal (short-circuit, earth fault) conditions as well as during normal conditions exists, the cables shall be screened.

In order to have a minimum number of types of cables, all cables shall be standardized as much as possible as regards cross-sections, number of cores and marking of cores.

The phase colour identification code to be applied shall be made known to the Contractor shortly after the award of the Contract.

For the three-phase low-voltage system, four wire grounded neutral system shall be used.

The low voltage power cables (AC and DC) and all cables for control, measuring, etc., shall be PVC insulated and PVC-sheathed, screened and armoured. The conductors shall be of electrolytic copper.

Further requirements are stated in General Specification of Works, "Wiring and Terminal Blocks".

### Cable Laying and Routing

The final routing of HV and LV cables in indoor and outdoor installations shall be determined by the Contractor.  All cable routing and arrangement shall be subject to the Project Manager's approval.

For indoor installations or exposed outdoor installations cables shall be laid in covered cable trenches, plastic or steel ducts or, depending on the available space, on cable trays and racks.  Where few and small cables have to be laid they can be fixed directly to the wall or ceiling.  Cables on walls shall be protected by steel conduits against mechanical damage, at least up to 1.8m above the floor.

Low power cables, i.e. cables for control, metering, etc. shall not be run in close parallel to high power cables or earth wires, but shall be run at the greatest possible separating distance.  Additionally, cables for extra low power, i.e. mA and mV circuits and cables connected to low power solid state electronic circuits, shall be laid in separate sheet steel trays with covers.  The DC trip and A.C. voltage supplies and wiring to main protective gear shall be segregated from those for back-up protection to the greatest extent possible.

LV cables in the switchyard shall be laid in an orderly manner in covered concrete cable trenches with removable concrete covers with the exception of cables connected to equipment, which shall be laid in conduits.

The existing cable trenches including trench covers as well as conduits and cable racks shall be used. If necessary, the contractor shall dig trenches, lay and cover cables between the apparatuses and the existing cable ways. Other necessary materials and equipment for laying, fixing, terminating, etc. of the cables shall also be provided by the Contractor.

### Laying

Medium-voltage, low-voltage power cables and control and measuring cables shall be segregated from each other throughout the plant.

The cables shall be laid in an orderly manner and crossings in the same plane shall be avoided.

All cables shall be laid on cable racks where they are not running in cable ducts or trenches, or in protecting tubes.

The cable racks shall be designed to allow the laying of the cable from the side(s) without pulling through.  All racks and fixing devices shall be hot-dip galvanized.

The Contractor shall supply concrete cable trench covers reinforced with deformed steel bars.

The last section of a cable on the switchyard may be laid in a conduit or a pipe, they shall be laid in such a way that cables easily can be exchanged without digging.

### Diagrams and Calculations

The Contractor shall deliver cabling plans and diagrams showing each cable connection.

Drawings for the cable racks, fixing features, etc., shall also be provided by the Contractor.

All dimensioning calculations shall be submitted to the Project Manager for approval.

The Bidder shall in his Bid give detailed information about the different types of cables proposed.

### Tests

Factory tests and site tests shall be performed in accordance with the applicable IEC recommendation.

Type test certificates shall be submitted.

## SITE AND COMMISSIONING TESTS

### General

Tests as described below shall be used as a guideline and may be changed or varied after written agreement from the Project Manager, due to changes of design manufacturing or construction techniques.

### Test of Wiring

a.	Insulation Resistance Test at 1000 Volts A.C. for one minute shall if possible be carried out on all A.C. and D.C. protection, control, alarm and indication circuit to ensure that wiring is in satisfactory condition.  Ocular inspection shall be made on cable glands, cable jointing, fuse or circuit breaker ratings and small panel items, such as indicating lamps.

b.	Static equipment which may be damaged by the application of test voltages shall have the appropriate terminals disconnected.

c.	Inter-relay, inter-unit and cubicle wiring carried out at site is to be checked to the appropriate circuit and/or wiring diagram.  This may be done by using bells or buzzers.  D.C. supplied from the station battery may also be used.  Where it is found necessary during re-commissioning work to effect site modification to the secondary wiring, site copies of the appropriate schematic and wiring diagrams shall be suitably marked as agreed with the Project Manager before the circuit is commissioned.

d.	Loop resistance measurements are to be done and on all current transformer circuits.  Separate values are required for current transformer and lead resistance and all measurements are to be recorded on lead resistance diagrams.

### Test of Relays

a.	All relays are to be examined to ensure that they are in proper working conditions and correctly adjusted, correctly labelled and that the relay case, cover, glass and gaskets are in good order.

b.	Secondary injection shall be carried out on all A.C. relays, using voltage and current of sinusoidal wave form and rated power frequency. For circulating current protection employing high impedance voltage setting test shall be across the relay and stabilising resistance. The operation setting for the type of protection is to be established by secondary injection, where it is not possible to ascertain this value.

### Test of D.C. Circuits

Tests are to be carried out to prove the correctness of all D.C. polarities, the operating levels of D.C. relays and the correct functioning of D.C. relay schemes, selection and control switching, indications and alarm.

### Test of Instruments

Instruments and instrument transformer circuits shall be checked for polarity of direction and for calibration including any interposing transformers or transducers.  These checks shall be made on all current transformer ratios where applicable.

The burden of the connected load shall be determined to ensure that it is within the specified burden of the instrument transformer.

The error of measuring devices due to instrument transformers and wiring, for the purpose of error compensation on measuring devices, shall be tested and determined.

### Tests on Conductors, Insulators and Accessories

None required.

### On Load Test

On load tests are required, but due to the hazards inherent, they shall be carried out under the direct supervision of the Project Manager and/or the Employer.  The following tests are required:

a.	An operation and stability test shall be carried out for on-load commissioning.

b.	Test for restraint shall be carried out to prove the characteristic of protective and measuring systems with directional characteristics.

c.	On-load checks shall be made after the protective gear has been placed in service to ensure that all connections and test links have been replaced and test leads removed, as well as to confirm the integrity of the current transformer circuits.  Where necessary, voltage readings shall be taken at the terminals on each relay to ensure that loop connections between the relays are complete.  Special attention shall be paid to broken delta voltages and residual current circuits where zero voltage or current respectively may not be proof of the completeness of the circuit.

### Tests on the Switchyard on Site

All electrical equipment and installations shall be tested for correct connections of the high-voltage circuits as well as of the control and measuring circuits, installation, insulation, and earthing.

System testing is mandatory; for construction schematics, SAS and NCC SCADA functionality.

All electrical equipment and installations shall be subjected to a complete operational test to check the correct operation thereof in terms of the operational requirements specified in these Specifications.

### Earthing System tests

The contractor shall carry out substation earthing system commissioning tests in accordance with IEEE std 81-2012 and BS EN 50522-2012 at all the sites. The following shall be tested

- The substation earthing grid shall be tested by applying the Fall of Potential Method, at least in two directions using at appropriate earth resistance tester such as MEGGER DET4TCR2 earth tester.

- Earth connection resistance measurements (Equipment Bonding Tests) - To measure the resistance between an earthed/bonded equipment and the main substation earth electrode to check bonding adequacy using a four terminal Micro-ohmmeter

- Earth Conductor Joint Resistance Measurements - This measurement is used to measure the resistance across an earth joint to check its electrical integrity used for testing all types (bolted, brazed, welded) of earth conductor joints, using a four-terminal micro-ohmmeter

- Touch, Step and Transfer Voltage Measurement – This measurement is used to measure touch, step and transfer voltages for comparison with calculated values as per IEEE std 81

## Structural Steelworks

The Contractor shall include necessary supports and gantries for all new equipment. However, by approval of the Employer existing structures can be used if convenient.

## Civil Works

The Contractor shall include foundations and modifications in buildings necessary to accommodate his equipment. Existing foundations may be used if found convenient and approved by the Employer. Other civil works shall include control and guard house buildings, substation switchyard platform, cable trenches, roads, fencing, subsurface and surface drainage, water supply and sewerage disposal systems as required in the relevant clauses specified herein.

PARTICULAR TECHNICAL SPECIFICATIONS

SECTION IV CONTENT

4 PARTICULAR TECHNICAL SPECIFICATIONS	151

4.1 HIGH VOLTAGE OUTDOOR SWITCHGEAR AND SWITCHYARD EARTHING	151

4.1.1 General	151

4.1.2 Technical Requirements, General	151

4.1.2.1 Ratings and Design Criteria	151

4.1.2.2 Rated Normal Current	153

4.1.3 Circuit Breakers	154

4.1.4 Isolating Switches and Earthing Switches	156

4.1.5 Current Transformers	156

4.1.6 Voltage Transformers	158

4.1.7 Lightning Arresters	159

4.1.8 Line Traps	159

4.1.9 Conductors, Insulators, Accessories	160

4.1.9.1 Conductors	160

4.1.9.2 Insulators	161

4.1.9.3 Accessories	162

4.1.10 Switchyard Earthing	162

4.1.10.1 General	162

4.1.10.2 Technical Requirements, General	163

4.1.10.3 Earthing Electrode System Under the Control Building	164

4.1.10.4 Earthing Electrode System of the Switchyard	164

4.1.10.5 Earthing Conductors	165

4.2 MEDIUM VOLTAGE SWITCHGEAR	167

4.3 POWER CABLES AND ACCESSORIES	168

4.3.1 GENERAL	168

4.3.2 Cables	169

4.3.2.1 Conductors	169

4.3.2.2 Conductor Screening	170

4.3.2.3 Insulation	170

4.3.2.4 Core Screening	170

4.3.2.5 Identification of Cores	170

4.3.2.6 Laying-up and Fillers	170

4.3.2.7 Manufacturer’s Identification	170

4.3.2.8 Armour	170

4.3.2.9 Testing	171

4.3.2.10 Sealing and Drumming	171

4.3.2.11 Current Carrying Capacity and Design Parameters	171

4.3.3 Accessories	171

4.3.3.1 Cable Joints	171

4.3.3.2 Straight and Branch Service Joints	172

4.3.3.3 Termination	172

4.4 POWER TRANSFORMERS	173

4.4.1 GENERAL	173

4.4.1.1 Materials and Labelling	173

4.4.2 DESIGN CRITERIA	173

4.4.2.1 Service Conditions	173

4.4.2.2 Rating	174

4.4.2.3 Tapping	174

4.4.2.4 Noise	174

4.4.2.5 Radio Interference	174

4.4.2.6 Interchangeability and Paralleled Operation	174

4.4.2.7 Insulation Levels	175

4.4.2.8 Short Circuit Performance	176

4.4.2.9 Frequency	176

4.4.2.10 Flux Density	176

4.4.3 DESIGN	176

4.4.3.1 General	176

4.4.3.2 Cores	177

4.4.3.3 Windings	178

4.4.3.4 Current Transformer	179

4.4.3.5 Internal Earthing	180

4.4.3.6 Tanks	180

4.4.3.7 Gaskets	182

4.4.3.8 Bushings	182

4.4.3.9 Vibration	183

4.4.3.10 Painting and Galvanising	183

4.4.4 FITTINGS	184

4.4.4.1 Off-load Tap Changer	184

4.4.4.2 Conservator	184

4.4.4.3 Dial-type Oil Gauges	185

4.4.4.4 Silica-Gel Breathers	185

4.4.4.5 Explosion-Vents	185

4.4.4.6 Buchholz Relays	186

4.4.4.7 Temperature Indicators	186

4.4.4.8 Alarm and Trip Contacts	187

4.4.4.9 Drain, Filter and Sampling Valves	187

4.4.4.9.1 General	187

4.4.4.9.2 Drain Valves	187

4.4.4.9.3 Oil Sampling Valves	188

4.4.4.9.4 Filtration Connections	188

4.4.4.9.5 Valve Entries	188

4.4.4.10 Rating and Diagram Plates	188

4.4.4.11 Skid Under base	188

4.4.4.12 Wheels	188

4.4.5 VOLTAGE CONTROL EQUIPMENT	189

4.4.5.1 On-Load Tap Changers	189

4.4.5.1.1 General	189

4.4.5.1.2 Construction	190

4.4.5.1.3 Operation	191

4.4.5.2 Local Tap Changer Control Cubicles and Wiring	192

4.4.6 COOLING	194

4.4.6.1 Definitions	194

4.4.6.2 Declaration of Ratings	194

4.4.6.3 Radiators	194

4.4.6.4 Supplementary Cooling Plant	194

4.4.6.4.1 Natural cooling with additional Forced-Air Cooling ONAN/ONAF	194

4.4.6.4.2 Fans	195

4.4.6.4.3 Cooler Control Equipment	195

4.4.7 SPARES	196

4.4.8 OIL	196

4.4.9 INSPECTION AND TESTS	197

4.4.9.1 Inspection/Witnessing of Tests	197

4.4.9.2 Bushing Tests	197

4.4.9.3 Transformer Tests	198

4.4.9.3.1 Routine Tests	198

4.4.9.3.2 Type Tests	199

4.4.9.3.3 Site Tests	199

4.4.9.4 Test Certificates	199

4.4.10 ERECTION	200

4.4.11 DELIVERY AND TRANSPORT	200

4.4.12 EVALUATION OF LOSSES	201

4.4.12.1 Guaranteed Output and Losses, Liquidated Damages	201

4.4.12.1.1 Transformer Output	201

4.4.12.1.2 Transformer Losses	201

4.4.12.1.3 Rejection Limits	202

4.4.12.2 Evaluation of Losses	202

4.5 AUXILIARY SUPPLY	202

4.5.1 General	202

4.5.2 Switchboards and Panels	203

4.5.2.1 Circuit Breakers	204

4.5.2.2 Current Transformers	204

4.5.2.3 Instruments and Relays	205

4.5.3 DC SUPPLY	205

4.5.3.1 General	205

4.5.3.2 Batteries	207

4.5.3.3 Chargers	208

4.5.3.4 Battery Conductors and Fuses	210

4.5.3.5 48 V supply with DC/DC Converters	210

4.6 PROTECTION	210

4.6.1 General	210

4.6.2 Relay Construction and Mounting	211

4.6.3 Commissioning and Routine Testing Facilities	212

4.6.4 Relay Settings	213

4.6.5 Fault Clearing Time	213

4.6.6 Fault Recorder and Fault Locators	213

4.6.7 Programming Tools	213

4.6.8 Supervision	213

4.6.9 Training	213

4.6.10 Transmission Line Protection	213

4.6.10.1 Transmission Lines	213

4.6.11 Transformer Protection	217

4.6.11.1 330/66kV Transformers and Reactors	218

4.6.11.1.1 Main protection	218

4.6.12 Transformer Automatic Voltage Regulators (AVRs)	220

4.6.12.1 Transformers	220

4.6.12.2 Control of bay equipment	220

4.6.13 Busbar Protection	220

4.6.14 Synch Check and Synchronising Equipment	221

4.6.15 Auto Reclose System	221

4.6.16 Relay Protection Telecommunication System	221

4.6.17 Training	221

4.7 METERING	221

4.7.1 Scope	221

4.7.2 General Requirements	221

4.7.2.1 Measure Energy	222

4.7.2.2 Store Loggers (Load Profile)	223

4.7.2.3 Display Instantaneous Values with high accuracy (as with energy)	223

4.7.2.4 Act as Terminal	224

4.7.2.5 Transmit and Receive Pulse Information	224

4.7.2.6 Calculate Maximum Demand	224

4.7.2.7 Front Panel Keys	224

4.7.2.8 Configuration	224

4.7.2.9 Accuracy	224

4.7.2.10 Measuring Voltage	224

4.7.2.11 Measuring Current	224

4.7.2.12 Auxiliary Supply	224

4.7.2.13 Inputs/Outputs	224

4.7.2.14 Communication	225

4.7.2.15 Display	225

4.7.2.16 Security	225

4.7.3 Normative References	225

4.7.4 Meter Communications	226

4.7.5 Meter Case	226

4.7.6 Labels	227

4.7.7 Meter Accuracy	227

4.7.8 Temperature Monitoring	227

4.7.9 Metering System	228

4.7.9.1 AMI - Automatic Metering Infrastructure	228

4.7.9.2 AMI Features	229

4.7.9.3 AMI Network	229

4.7.9.4 Remote Metering	230

4.7.9.5 Meter Management	230

4.7.9.6 Time Synchronization	230

4.7.9.7 Communication and Data Security	231

4.7.9.8 Metrology and Quality Supply	231

4.7.9.9 System Expandability	231

4.7.10 Non-Compliance Schedule	231

4.7.11 Test Certificates Schedule	232

4.7.12 INSPECTIONS	232

4.7.12.1 Pre-Factory Acceptance Test and Factory Acceptance Tests	232

4.7.12.2 Operational Acceptance Tests	232

4.7.13 TRAINING:	232

4.7.13.1 Multifunctional Digital Energy Meter COURSES	233

4.7.13.2 Remote Metering TRAINING	233

4.7.13.3 Programmable Transducers Course	233

4.7.13.4 Temperature Gauge Course	233

4.7.14 COST OF TRAINING:	233

4.7.15 DOCUMENTATION	233

4.7.16 SPARES	233

4.8 CONTROL	234

4.8.1 General	234

4.8.1.1 Basic System Elements	234

4.8.1.2 Human Machine Interface (HMI) Server & Client computer	235

4.8.1.3 Operator Workstation (HMI) Client	235

4.8.1.4 Gateway/RTU	235

4.8.1.5 Bay Control Units	236

4.8.1.6 Automatic Voltage Regulators (AVR)	236

4.8.1.7 GPS Clock	237

4.8.1.8 Engineering Workstations	237

4.8.1.9 Control Cables	237

4.8.1.10 Colour Laserjet Printers	237

4.8.1.11 Substation Control System Architecture / Overview	237

4.8.2 Station LAN Configuration	238

4.8.2.1 Station LAN and Communication	238

4.8.2.2 LAN Cables	238

4.8.2.3 Network Switches	239

4.8.2.4 Control and Protection Panels	239

4.8.2.5 Inverters (DC to AC Power conversion)	239

4.8.2.6 Monitoring And Control Functionality	239

4.8.2.7 Inherent Safety Features	240

4.8.2.8 Event And Alarm Handling	240

4.8.3 Factory Acceptance Tests (FATs) on SAS Equipment	241

4.8.4 Factory Training on Substation Automation and SCADA Systems equipment	241

4.8.5 Substation Control System Training	241

4.8.5.1 Control System Introduction Courses	241

4.8.5.2 Control System Gateway Training	241

4.8.5.3 Control System HMI Training	242

4.8.5.4 Control System IED Training	242

4.8.6 Technical Requirements & Technical Schedules for SAS Equipment	242

4.9 NEUTRAL EARTHING	248

4.10 AUXILIARY TRANSFORMER	248

4.10.1 General	248

4.10.2 General Design	248

4.10.3 Windings	249

4.10.4 Cores	249

4.10.5 Tapping Switches	250

4.10.6 Bushings	250

4.10.7 Tanks and Conservators	250

4.10.7.1 General	250

4.10.7.2 Tanks	250

4.10.7.3 Conservators	250

4.10.8 Accessories and Fittings	250

4.10.9 Insulating Oil	250

4.10.10 Tests	250

4.10.11 Packing and Transport	250

4.10.12 Drawings and Diagrams	250

4.10.12.1 With Bid	250

4.10.12.2 With Contract	250

# PARTICULAR TECHNICAL SPECIFICATIONS

## HIGH VOLTAGE OUTDOOR SWITCHGEAR AND SWITCHYARD EARTHING

### General

This Chapter covers the technical requirements of the 330kV, 132kV and 33kV equipment to be installed at the outdoor switchyards as well as the general earthing grid and other associated equipment.

The supply shall comprise all apparatus and requisite accessories, conductors, insulators, clamps and connections, earth wires, operating cubicles, cable marshalling kiosks, fixing materials, apparatus supports and towers for the complete plants as well as earthwork and construction of control and workshop building at Kitwe, Kalulushi, Chambishi, Mufulira, Chingola and Chililabombwe substations.

The switchgear and equipment shall be clearly labelled, showing names of the apparatus, phasing, etc. The metallic labels shall clearly identify the equipment and be located at a height and at point where it can be seen by operators.

The Contractor shall supply all spares specified in Scope of Works and Supply and these shall be included in the Bid. In addition, Bidders are requested to state their recommendations at the time of Biding for extra spares bearing in mind that the switchgear shall be in continuous operation for 25 years.

Spares shall be delivered with the associated equipment and, in order that spares may be placed on order at short notice, full details including Catalogue and/or spare part numbers of all spares should be supplied with Bid.

### Technical Requirements, General

#### Ratings and Design Criteria

The ratings and design criteria for the plant and equipment shall be as follows:

| ITEM | SPECIFICATION | SYSTEM VOLTAGE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 330 kV |  | 132 kV* |  | 33 kV |  |
| 1 | System | 50 Hz, 3 phase with the neutral solidly earthed |  |  |  |  |  |
| 2 | Nominal voltage of networks *) | 330 kV |  | 132 kV |  | 33 kV |  |
| 3 | Highest system voltage as defined by IEC | 362 kV |  | 145 kV |  | 36 kV |  |
| 4 | Short circuit power not less than *) | 23 000 MVA |  | 6 500 MVA |  | 2 500 MVA |  |
| 5 | Short circuit and earth fault current, symmetrical r.m.s. value not less than | 40 kA |  | 31.5 kA |  | 31.5 kA |  |
| 8 | Thermal short-circuit current, 1 second not less than | 40 kA |  | 31.5 kA |  | 31.5 kA |  |
| 9 | Dynamic peak current not less than | 100 kA |  | 63 kA |  | 63 kA |  |
| 10 | Rated current of current carrying parts, if not otherwise specified in Scope of Works and Supply | 2 000 A |  | 2 000 A |  | 2 000 A |  |
| 11 | Minimum rated current of isolating switches and circuit breakers | 2 000 A |  | 1 200 A |  | 1 200 A |  |
| 12 | Insulation level: (at sea level, compensation for altitude is already added to these figures) |  |  |  |  |  |  |
| 12a | Switching surge withstand voltage |  |  |  |  |  |  |
|  | To earth and phase-to-phase | 1 050 kV |  |  | N/A | N/A |  |
|  | Across the isolating distance of isolating switches | 900 kV |  |  |  |  |  |
|  |  | (+205) kV |  |  |  |  |  |
| 12b | -Lightning impulse withstand voltage 1.2/50 m/s |  |  |  |  |  |  |
|  | To earth and between phases | 1300 kV |  | 650 kV |  | 170 kV |  |
|  | Across the isolating distance of isolating switches | 1300 kV |  | 750 kV |  | 170 kV |  |
|  |  | (+205) kV |  |  |  |  |  |
| 12c | -Test voltage at power frequency 1 min dry and wet |  |  |  |  |  |  |
| d | To earth and between phases | 570 kV |  | 275 kV |  | 70 kV |  |
| e | Across the isolating distance of isolating switches | 610 kV |  | 275 kV |  | 70 kV |  |
|  |  | SYSTEM VOLTAGE |  |  |  |  |  |
|  |  | 330 kV |  |  | 132 kV |  | 33 kV |
| 13 | For the design and erection of the conductors in the switchyard the following minimum distances shall be observed |  |  |  |  |  |  |
| a. | Phase to ground | 2 800 mm |  | 1 300 mm |  | 1 300 mm |  |
| b. | Phase-to-phase | 3 400 mm |  | 1 500 mm |  | 1 500 mm |  |
| c. | Busbars phase to phase | 5 000 mm |  | 3 000 mm |  | 3 000 mm |  |
| d. | Height to live parts above ground | 5 250 mm |  | 3 500 mm |  | 3 500 mm |  |
| e. | Height to live parts above ground at transformer transport routes | 12 000 mm |  | 7 5000 mm |  | 7 5000 mm |  |
| f. | Lowest part of insulators above ground | 2 500 mm |  | 2 500 mm |  | 2 500 mm |  |
| 14 | Maximum temperature rise of conductors above ambient temperature | 45oC |  | 45oC |  | 45oC |  |
| 15 | Maximum wind pressure on conductors and cylindrical objects | 430 N/m2 |  | 430 N/m2 |  | 430 N/m2 |  |
| 16 | Maximum wind pressure on flat surfaces | 820 N/m2 |  | 820 N/m2 |  | 820 N/m2 |  |
| 17 | Minimum nominal creepage distance as defined in IEC 815, Table II | 31 mm/kV |  | 31 mm/kV |  | 31 mm/kV |  |

*All 88kV equipment will be rated for 132 kV.

All components, all equipment as well as the total plant shall be suitable for operation outdoors in sub-tropical conditions.  Due consideration shall be paid to heavy rainfalls, to the temperatures and to atmospheric over voltages.

Equipment and components as well as the total plant shall withstand the thermal and mechanical stresses forced by the rated continuous currents as well as the over currents as specified above.

#### Rated Normal Current

The rated normal current of the circuit breakers and bus bars shall not be less than the following:

Three phase busbar, transformer incomers and bus section:		3150 Amps

330 kV Feeders:					2000 Amps

132 kV Feeders:					2000 Amps

33kV Feeders:	800 Amps

For transformers above 85 MVA, the individual transformer capacity shall be taken into consideration when determining the current rating of the circuit.

### Circuit Breakers

The three phase circuit breakers shall be of the outdoor, single pressure SF6 type. The breakers shall be mounted on steel structures.

The 330 kV, 132kV and 33kV circuit breakers shall be suitable and completely equipped for single phase and three phase rapid auto reclosing and a standalone common local control box.

The breakers shall be capable of handling the following operation cycle, according to the IEC recommendations:

0-t-CO-t1-CO		t = 0.3 sec		t1 = 180 sec (3 minutes)

The total breaking time (opening time plus duration of the arc) of the breakers shall be as short as possible, but in no case is it to be longer than 60 msec.

A system for monitoring continuously the gas density shall be provided.  At a certain low-density signal shall be given to indicate that refilling should take place.  At the extreme low-density the circuit breaker should be automatically blocked against operation.

Gas treatment equipment as specified in general specifications shall be furnished for each substation where Sf6 breakers are installed.

The circuit breakers shall be provided with means to prevent contact pumping while the closing circuit remains energized should the circuit breaker either fail to latch or be tripped during closing due to the operation of the protective relays.

Each individual single pole of a three-pole circuit breaker shall be provided with its own independent operating mechanism.  33 kV breakers may have one operating mechanism common to all three poles.  A spring-operated mechanism is preferred. Pneumatic operating mechanism is not accepted.

The mechanism shall be provided for electrical local and remote control.  The control voltage for closing and opening commands and for the operating mechanism motor(s), shall be stated in Scope of Works and Supply as :110V or 220V DC + 10%, 20% unearthed, from battery. (See the Scope of Works and Supply).

The opening device shall be provided with two independent trip coils, connected to separate terminal blocks in the terminal cubicle, allowing for the connection of two independent opening command circuits. The trip coils shall be capable of operating at 65% of the nominal voltage.

A local position indicator, visible with the panel door closed, shall be mounted in the front panel of the operating mechanism cubicle.

A crank, lever or other similar suitable device shall be provided to permit charging the operation mechanism by hand in the event of a failure of the auxiliary supplies or in the event of a failure of the energy storing device.

The stored energy shall for all types of operating mechanisms be sufficient to allow a complete O C O cycle.

It shall be possible to determine the available operating energy stored by the mechanism prior to operating the circuit breaker.  An alarm shall be given in the event of the stored energy falling below a minimum rated level.

If the stored operating energy is below a minimum rated level in one or more of the mechanisms, tripping, closing and auto reclosing shall be blocked in all phases.

The complete operating mechanism, including the controls, shall be built in watertight and dust proof cubicles (min. IP54).  All parts shall be easily accessible without dismantling other parts.  Openings, covered with dust filters, shall allow a good ventilation of these cubicles.  To avoid any moisture, thermostat-controlled heaters for 220 V AC shall be built in. Push buttons for operating the breaker shall be located not more than 1.7 m above ground.

A local/remote control selector switch shall be provided in the cubicle.  With the selector switch set to local control, operation from any remote source including the protective relays shall be inhibited.  The switch shall have spare contacts enough separate auxiliary contacts, with at least 5 NO and 5 NC contacts as spare, for 110V DC shall be provided for control and interlock purposes.

Motors shall be designed in accordance with valid IEC publication and shall be effectively protected by miniature circuit breakers, with alarm contacts.

All wiring shall lead to terminals.  10% of the terminals shall be spare. Position for connection of resistance measurement equipment shall be indicated or marked on the circuit breaker terminals.

### Isolating Switches and Earthing Switches

All switches shall be mounted on a steel structure preferably on the existing foundations.

The contact surfaces shall be heavily silver plated.  The contact pressure shall be ensured by means of springs.

Each three-phase isolating switch and each three-phase earthing switch shall be equipped with its own operating mechanism. The isolator mechanism shall be motor operated and shall be provided for local and remote electrical operation.  The earthing switches shall be manually operated only.  The auxiliary voltage for the operation of the closing and opening devices is given in the Scope of Works and Supply as 110 VDC, + 10%, 20% unearthed, from battery.  Operating motors shall be provided for 110 V DC operation.

In the case of a complete failure of the operating mechanism all switches shall be operable manually by means of a lever or crank or another feature.

Disconnections shall have mechanical interlocking to attached earth switches.  The interlocking shall prevent closing of earth switch when the isolator is in closed position as well as disconnect the motor and prevent closing of the isolator when the earth switch is closed.

The complete operating mechanism, including the controls, shall be built in in a watertight and dust proof cubicle (min. IP54).  All parts shall be easily accessible without dismantling other parts.  The necessary openings for a good ventilation of the cubicles shall be provided.  They shall be covered with dust filters.  Thermostat controlled heaters for 220 V AC shall be provided for each cabinet to prevent any moisture by condensation.

A local/remote control selector switch shall be mounted in the cubicle.

Enough separate auxiliary contacts, with at least 5 NO and 5 NC spares, for 110 V DC shall be provided for control and interlock purposes.

Motors shall be designed in accordance with valid IEC publication and shall be effectively protected by miniature circuit breakers, with alarm contact.

All wiring shall lead to terminals.  10% of the terminals shall be spare.

### Current Transformers

The current transformers shall be single phase, oil immersed, mounted in one insulator.  They shall be mounted on steel structures preferably on existing foundations.

Each current transformer shall be equipped with an oil level gauge to be easily visible from the ground.

The current transformers shall be supplied including oil filling.

The oil of the current transformer shall be hermetically sealed against the ambient air. The sealing method shall be described in the Bid, as well as the method of compensation for changes in the oil volume due to temperature changes.

The Bidder shall indicate what measures are provided for relieving dangerous pressure rises that may develop due to an internal electrical fault.

The primary connections shall be silver plated.

All secondary connections shall be connected to a terminal block which shall be in a dust proof and watertight terminal box and shall be clearly labelled.

An earth connection to the housing shall be provided.

The current transformers shall be designed to carry continuously a current of 120% of the rated current.

The rated current of the secondary windings shall be 1 A, unless otherwise specified in Scope of Works and Supply, the different cores shall have dual ratio and the following characteristics.

1. The core(s) for measuring (two cores):

Accuracy							class 0.1/0.2s

Instrument security factor equal to or less than		5

2. The core(s) for main protection (two cores)

Accuracy						class PX

Knee point 						as required by the protection.

3. The core(s) for Back up protection (two cores):

Accuracy								class 5 P

Accuracy limit factor equal to or greater than				20

The characteristics of the current transformers shall comply with the provisions stipulated in IEC 61869 – 1 & 2

The Contractor shall demonstrate that the current transformers selected will ensure correct functioning of the associated protective equipment.

The output of the current transformers for measuring and protection purposes shall be determined according to the technical requirements but shall not be less than 125% and not more than 160 % of the overall computed (design) burden of the connected apparatus and conductors.

Power frequency test voltage on secondary windings, 1 min.	 2 kV

Overvoltage inter-turn test, 1 min. 4.5 kV peak

### Voltage Transformers

Voltage transformers shall be of capacitive type. The single-phase voltage transformers shall be oil immersed, mounted in one insulator.  They shall be mounted on steel structures.

Each voltage transformer shall be equipped with an oil level gauge to be easily visible from ground level.

The voltage transformers shall be supplied including oil filling.

The oil of the voltage transformers shall be hermetically sealed against the ambient air. The sealing methods shall be described in the Bid, as well as the method of compensation for changes in the oil volume due to temperature changes.

The Bidder shall indicate what measures are provided for relieving dangerous pressure rises that may develop due to an internal electrical fault.

The primary connections shall be silver plated.

All secondary connections shall be connected to a terminal block which shall be in a dust proof and watertight terminal box and shall be clearly labelled. The cables from the voltage transformers shall be dimensioned in accordance with the accuracy class of the core.

An earth connection to the housing shall be provided.

The capacitive earthed voltage transformers shall be provided with the necessary features for the high frequency power line carrier coupling.  They shall be equipped with a separate connection for the HF coupling and an earthing link and be capable of supporting the associated line trap unit.  The capacitance shall be sufficient for coupling over the tuning band of the associated line trap.

The windings for measuring purposes shall be designed for accuracy according to class 1.  Rated secondary voltage shall be 110 /√3 V. One of the secondary windings shall be for open delta core with secondary voltage 110/√3.

The voltage transformers shall have two additional secondary windings for protective purposes designed for an accuracy according to class 3P.

The secondaries shall be provided with miniature circuit breakers with alarm contacts.

The characteristics of the voltage transformers shall comply with the provisions stipulated in IEC 61869 – 1 & 5

The capacities of all windings shall be determined according to the technical requirements but shall not be less than 125% of the overall computed (design) burden of the connected apparatus and conductors.

Power frequency test voltage on secondary windings, 1 min.  2 kV.

### Lightning Arresters

The lightning arresters shall be of the metal oxide gap-less type, complying with IEC 60099 -1 - 9. The lightning arresters shall have the following characteristics:

|  |  | 330kV | 132kV | 33kV |
| --- | --- | --- | --- | --- |
| 1. | Maximum continuous operating voltage (r.m.s.) | 209kV | 86kV | 22kV |
| 2. | Temporary overvoltage (TOV) | 209kV | 121kV | 36kV |
| 3. | Duration of TOV | 1 s | 2 s | 2 s |
| 4. | Rated discharge current 8/20 ms | 10kA | 10kA | 10kA |
| 5. | Max. residual voltage at 10 kA | 650 kV | 300kV | 90kV |

As all other main parts of the switchyard, they shall be mounted on steel structures.

The lightning arresters shall be fitted with a pressure relief device. Surge counters with leakage current monitoring shall be supplied for each single-phase arrester.

The earth conductor from the arrester to the counter as well as the in terminal of the counter shall be suitably insulated or screen protected against accidental touching.

### Conductors, Insulators, Accessories

#### Conductors

Unless otherwise stated in Scope of Works and Supply, the conductors shall be concentric lay stranded, flexible conductors made of round aluminium, aluminium alloy or copper wires.  The alloy shall be aluminium alloy 6201 T81 in accordance with ASTM Standard B 398 67 or aluminium alloys of similar approved composition, as known under the trade name "ALDREY".

The same type of conductor may be used for the overhead earth wires, the cross sections being at least the equivalent of 95 mm2 copper.  Other earth wires shall always be of copper.

The cross-sectional area of the conductors shall be chosen according to the electrical and mechanical requirements and shall be proposed in the Bid.  Rated currents are given in Scope of Works and Supply, for each substation.  The minimum factor of safety for busbars or other connections based on elastic limit shall be 2.5.

The number of different cross-sectional areas to be used for the current carrying conductors, shall be strictly limited.  For overhead earth wires the same cross-sectional area shall be used for all substations.

All wires making up the conductor shall be free from dirt, splints, scratches and all imperfections not consistent with the best commercial practice.

The conductor shall be tightly and uniformly stranded with no loose strands and when subjected to 50% of ultimate strength, it shall show no high wires but shall maintain a true cylindrical form.  Any Cu Al connections shall be made with special junction pieces, outdoor as well as indoor.

Supply and erection of conductors and earth wires from dead end towers to gantries will be provided for under other contracts. It is however, the Contractor's responsibility to supply and erect the clamps and connections to the intake.

For busbars tubular aluminum conductors of alloy E91E in accordance with BS 2898 may also be used.

#### Insulators

The post insulators shall be dimensioned in accordance with IEC 60383.  They shall comprise fully interchangeable units of either the pedestal or solid core cylindrical type and shall be designed so that they can be used either upright or inverted.

The string insulator units shall comply with the provisions of IEC 60120, IEC 60305 and IEC 60372.  The type of insulator and the characteristics of the discs and the number of discs per string shall be chosen according to the electrical and mechanical requirements and shall be proposed in the Bid.

Minimum factors of safety shall be:

-For complete insulators based on electromechanical

failing load test (IEC 60383)				2.5

For insulator metal fittings based on elastic limit	2.5

Each insulator shall be marked with the initials or trademark of the manufacturer and with the guaranteed electromechanical strength. All markings shall be plainly legible and durable.

The insulators shall be made of:

-	Toughened glass, or

-	Wet-process, homogenous porcelain

-	Or any other approved material like silicon rubber.

Glass insulators shall be in a uniform shade of green.  Porcelain insulators shall be glazed in a uniform shade of brown, free of such imperfections as blisters and burns.

The insulators shall be free of laminations, cavities or other flaws affecting the mechanical and electrical strength, and shall be well vitrified, tough and impervious to moisture.

The socket shall be of galvanized malleable cast iron or ductile cast iron and the pin of galvanised steel.

Ball and socket connections shall be provided with cotter pins which effectively lock the connection against accidental uncoupling without detracting from its flexibility.  The cotter pin shall be of stainless steel or bronze.

The metal parts shall be designed to transmit the mechanical stresses to the porcelain by compression and to develop maximum and uniform mechanical strength of the insulator.

Socket and pin shall be of such design that they will not yield or distort under the specified mechanical loading in such a manner as to add undue stresses to the porcelain shells.

In general, the contours of the metal and porcelain parts shall be such as to eliminate areas or points of high electrical flux concentration.

All surface of metal parts shall be smooth with no projecting points or irregularities.

All ferrous material which is not made of stainless steel shall be hot dip galvanized in accordance with BS 729.

#### Accessories

For all accessories as clamps, connections, etc., care shall be taken to fulfil all conditions required concerning current carrying capacity, mechanical strength, glow discharge characteristics, corrosion resistivity and easy mounting, etc.

All accessories shall comply with VDE Standard 0210 and 0212 and with the corresponding DIN specifications or with other similar and approved specifications and shall be tested according to the same specifications.

### Switchyard Earthing

#### General

This chapter covers technical requirements of the earth electrode systems and the earthing conductors for the connection of metallic parts, of lightning arresters and of the system neutrals, designed to protect persons and equipment and to allow for the correct service, operation, and maintenance of the installations.

The substation earthing system shall be designed principally according to ANSI/IEEE 80 - 2013 Guide to Safety in AC Substation Grounding.

The earthing system shall consist of the earth electrode system in the ground under the switchyard, and of the earthing conductors, over ground and in the buildings.

The Contractor shall design the complete earthing system.  He shall measure and verify the specific earth resistance at all places where earthing electrodes will possibly be buried, he shall make drawings of the earthing electrode grids, calculate the resulting earth electrode resistance, touch, step, mesh and Ground Potential rise and supply all information about the planned earthing electrode systems. The criteria for the touch and step potential shall be based on 70kg weight of a person.  He shall also make drawings of the earthing conductors, over ground and in the buildings and make the necessary calculations for the dimensioning of the earthing conductor systems.  All the above shall be submitted to the Engineer for approval.

For bidding purposes, the earth resistivity shall be taken as 500 ohmmeters.

#### Technical Requirements, General

The earthing system shall be constructed and installed to comply with the requirements of local regulations and of the applicable Standards such as IEEE std 80, DZS 691: 2023.

More specifically and independent of (or in addition to) the regulations and standards, the earthing system shall provide:

(1)	Adequate protection for personnel against dangerous voltages, currents and arcs

(2)	Safe touch voltages and step voltages

(3)	A low earthing impedance for the lightning arresters

(4)	A low earthing impedance for the transformer neutrals and a sufficiently low neutral conductor impedance

(5)	Limitation of the induced, or capacitively transformed, voltages on low voltage, low current and electronic cables, circuits, panels and other equipment.

(6)	That short circuit, earth fault and double earth faults currents will flow through the earthing systems and not through other conducting parts or building constructions to a hazardous extent.

The maximum resistance of the earth electrode grid in the switchyard and under the control building shall be 0.5 ohm during the dry period. In addition, the earth electrode system as well as all other earthing systems shall be designed and constructed for the operating voltages, the design short circuit capacities and the corresponding short circuit and earth fault currents which are specified in General Specification of Works, and in the other Sections of these Specifications for the respective voltage systems.

The dimensioning shall be coordinated with the relay protection scheme of the various parts of the plant.  In any case, however, the earthing conductors shall be dimensioned for carrying the earth fault current and double earth fault currents of the various parts of the plant for at least 1 (one) second without any harm to the conductors or connections.

The conductors shall be reliably protected against mechanical damage and corrosion.

Buried connection shall be made by compressed clamps or by approved welding process.  No bolted clamps may be used below surface.  Connections above earth shall be screwed and shall be easily accessible for control.  All connections shall be protected against corrosion.

The final design and construction for the achievement of the total requirements of the earthing system shall be made by the Contractor but subject to approval by the employer.

#### Substation Site Soil Resistivity Measurement

Before the Earthing is designed, the contractor shall carry out soil resistivity measurement at all substation sites using at appropriate 4 terminal earth tester based on the Werner method according to IEEE std 81. The soil analysis model shall be based on the two- layer method using appropriate earthing design software. The same results shall be used to design the substation earth grid. The measurement shall be done in the presence of ZESCO Engineers and the results of the soil resistivity shall be shared with the ZESCO Project Manager.

#### Earthing Electrode System Under the Control Building

The conductors shall be of electrolytic copper with dimensions at least 30 x 3 mm for flat bar or at least 95mm2 stranded wire. Copper weld with approximately the same conductivity shall be used.

Earth risers shall be copper stranded wire at least 95mm2.

The conductors shall be placed on the ground after the excavation is completed and just before the concreting starts. Care must be taken that the earth wire is in good contact with the soil and preferably embedded into it.

Under the building the grid of conductors shall be placed with an average distance between conductors of not more than 10 m.  At all crossings the conductors shall be interconnected by thermo welding.  The grid shall also be connected to the concrete reinforcement at several places as well as to the earthing grid of the switchyard area.  Vertical risers shall be fixed by thermo welding to the conductors.

The risers shall be placed in the concrete shuttering and led out of the shuttering at appropriate places approximately 30 cm above the floors.  Care shall be taken to protect the risers against damage during shuttering and concreting.

Connecting terminals for the screwed connections between the risers and the above floor main earthing conductors shall be placed at easily accessible places and protected against mechanical damage.

The above information describes the minimum requirements.  The final design and construction for the achievement of the total requirements of the earthing systems shall be made by the Contractor, but subject to approval by the Project Manager.

#### Earthing Electrode System of the Switchyard

The conductors shall be of electrolytic copper with dimensions at least 30 x 3 mm for the flat bar or at least 95 mm2 stranded wire. Copper weld with approximately the same conductivity may be used.

The risers shall be of at least 95 mm2 stranded copper wire or equivalent copper weld.

The conductors shall be placed forming a grid covering the whole switchyard area.  The average distance between the conductors shall not be between 3m and 15m apart or one bay with whichever is smallest.

Earth mats connected to the main earthing grid shall be installed at the position of operating cubicles/handles of isolating switches in the project substations.

(The metallic fence shall be installed within the earth grid, at least 0.5m from the substation earth grid perimeter in order to)  A conductor shall also be installed outside the fence along the entire fence perimeter at a distance and depth suitable for the potential gradation needed at least 0.5m from the fence to avoid dangerous touch voltage between the fence and the ground. Vertical earth electrodes shall be installed at all corners and at designated intervals along the fence for the same purpose.

Trenches for the earthing grid shall be excavated in the ground to reach soil of good conductivity and a layer of at least 25 cm of the same material shall be placed over the conductor.  The conductor shall at no place be less than 80 cm below the ground level.

Where advantageous for achieving low resistance to ground, vertical copper weld earthing rods may also be used, in addition to the horizontal grid.

Connecting terminals for the screwed connections between the risers and the on-ground earthing conductors shall be placed in easily accessible locations.

The overall earthing results should be within acceptable results. Where there are rocky formations, and the required depth is not achievable results should be achieved by providing increased numbers of earth rods.

Vertical earth electrodes shall be installed at all points of possible heavy current discharge such as surge arresters, transformer neutral earthing and Lightning Protection System earthing termination points for aerial/shield wires and lightning protection masts.

The above information describes the minimum requirements.  The final design and construction for the achievement of the total requirements of the earthing system shall be made by the Contractor, but subject to approval by the Project Manager.

#### Earthing Conductors

In the control building a main earthing bus shall be installed on each floor in the cable trenches.

The conductors for these main earthing buses shall be of electrolytic copper with dimensions at least 150mm² for flat bar or stranded conductor.

Branch offs to switchgear, panels and other parts which shall be earthed shall be of electrolytic copper with adequate dimensions for each item to be earthed.

Each item shall be directly connected to an earthing conductor and not through a series connection of other metallic parts.

Where rows of switchgear cubicles, boards and panels occur, each cubicle, board or panel shall be earthed individually.

The fence of the switchyard shall be earthed at distances of not more than 20 m.

Earthing conductors for low current and electronic systems shall be insulated and shall be run from the systems, panels, etc., directly to a main earthing bus close to a connection to the earthing electrode system.  These earthing conductors shall not be mixed with the earthing of the high-power systems.

Earthing switches and lightning arresters shall have a riser directly connected to the current carrying part in addition to a riser connected to the structure.

All outdoor earthing conductors shall be insulated with spacers or conduits against contact with galvanized steel structures.

All connections to equipment and earth buses should be detachable. With detachable is to be understood compression clamped cable lugs fastened to the equipment with threaded screws.

#### Switchyard Earth Grid Design Criteria

i) The earthing system of sub-station shall be designed to ensure equipment safety, personnel safety and should facilitate proper operation of protection system during earth fault in the system due to stipulated fault current for specified duration.

ii) Neutral points of different voltages, metallic enclosures and frame work associated with all current carrying structures/metal works associated with electrical system shall be connected to single earthing system unless stipulated otherwise.

iii) The following particulars shall be considered for calculation & design of earth mat:

| No. | Description | Design input for New Substation |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 1 | Substation voltages | 330/220kV | 132/33/11kV | 33/11 kV | 11kV |
| 2 | Single line -groundd Fault Current (KA) on the high voltage side |  |  |  |  |
| 3 | Site soil resistivity | To be provided by the contractor |  |  |  |
| 4 | Current diversity Factor/Split factor | 1 |  |  |  |
| 5 | Current Decrement factor | Refer to IEEE std 80 table 10 |  |  |  |
| 6 | Network X/R ratio |  |  |  |  |
| 7 | Fault duration (second) (for conductor sizing calculation of main earth grid) | 1 |  |  |  |
| 8 | Fault duration (second) (for calculation of attainable and tolerable step and touch potential) | 1 |  |  |  |
| 9 | Criteria for step and touch potential | 70kg |  |  |  |
| 10 | Crushed-stone/gravel resistivity | 2500 ohm-meter |  |  |  |
| 11 | Size of crushed stone/gravel | 30mm to 50mm (40mm average) |  |  |  |
| 12 | Thickness of the crushed stone/gravel | 0.02m |  |  |  |
| 13 | Main (ground grid) earth mat conductor size and material (minimum) | 95mm² |  |  |  |
| 14 | Riser material (above ground) for equipment, columns and Aux. structures | Copper annealed soft drawn |  |  |  |
| 15 | Depth of the earth grid conductor burial | 1m |  |  |  |
| 16 | Vertical Earth Electrode material | Copper coated Mild Steel/Copper alloy |  |  |  |

N.B: (a) Consideration of current diversity factor may be changed for achieving safe touch & step voltage within the provision IEEE 80-2013. However, design of earth mat based on non-uniform spacing method shall not be acceptable.

(b) In case of extremely high soil resistivity Bentonite Powder may be used to bring down the resistivity subject to the approval by the project manager.

(c) This design criteria shall be taken as minimum guidance. The contractor shall be expected to refer to appropriate standards for the Earthing Grid design.

iv) For the purpose of finding out actual soil resistivity, it is to be measured in dry season by the successful contractor in presence of the representative of ZESCO. On the basis of actual soil resistivity of the substation earth mat shall be designed accordingly and as per approved earth mat design and approved layout drawing, the substation earth mat shall be laid accordingly.

To get the actual soil resistivity of the entire Sub-Station area, to arrive at the designed average soil resistivity, measurement shall be done with different number of electrodes spacing, preferably in steps of 2, 5, 10, 15, 20/25 meters etc. by following Wenner’s four electrode method in line with guide line as laid down. The resistivity for these spacing shall be noted and taken as the resistivity for that particular direction. In a similar manner, resistivities for at least ten locations, covering the entire switchyard area (including control room building), are to be measured. The average resistivity thus obtained shall be used for the design of the earth grid.

a) Length of main earth mat conductors, pipe/rod earth electrode and auxiliary mat shall be considered for design purpose of Earthing system.

b) Design shall ensure that potential gradient along the surface during short circuit is limited to a value considered safe for human being. The potential gradient to be achieved shall be less than the safe touch and step voltage.

v) Supply and spreading of 200 mm (min.) Crushed stone/gravel comprising of avg 40mm (30mm to 50mm) normal size crushed stone/gravel over the entire switchyard area over 75mm average thick

## External Lightning Protection System

### Design and Construction

- The lightning protection system for the site shall comply with IEEE 998 and IEC 62305

- Substation lightning protection systems (LPS) shall protect substations (plant equipment and buildings) from harmful effects of direct lighting strikes. The designed LPS shall protect the substation from thermal, mechanical and electrical effects caused by lighting discharges

### Study

- The Contractor shall undertake a lightning protection assessment of the site unless the site-specific documentation indicates it shall not be required.

- ZESCO Limited shall make available existing technical information of the site available to the Contractor for the purposes of a lighting protection study. The information shall include:

a) Lightning Impulse Withstand Level for all equipment at all voltages;

b) Type of Phase Conductor;

c) Conductor configuration;

d) Outer Diameter of the Conductor;

e) Attachment height of the Conductor, equipment;

f) Attachment height of OHEW (for gantry applications);

g) Sag on the conductor (flexible or strung bus);

h) Sag on shield wire; and

i) Existing substation information.

- The Contractor shall bring to the attention of ZESCO any missing technical information prior to undertaking the design. Where information is missing the Contractor shall make an allowance in the submission for any back calculations or proposed values which must be approved by ZESCO.

- The lightning protection design shall consider the operation and maintenance of the system to maximise safety, minimise damage to assets and minimise outage times during the life of the asset.

- The preferred method for assessing the lightning protection coverage shall be by providing a 3D model of the substation based on rolling sphere method either in CAD or in any design software tool.

- The lightning protection system shall be developed in conjunction with the insulation coordination considerations to correctly identify the Stroke Currents to be used for a lightning strike applied directly to the equipment or the busbar in the substation.

- The study shall culminate in a design report where Strike Distance calculations, 3D model of the substation and a protection coverage plan shall be provided to ZESCO for review.

### LPS Design Requirements

- Protection of substation equipment, including buildings, shall be achieved through the provision of an effective External lightning protection system for the interception of lightning discharge and the safe dissipation to the ground.

- The lightning protection design shall maximise safety, minimise damage to assets and minimise outage times in the unplanned situation that the protection system should fail.

- The lightning protection system shall discharge currents safely without exceeding design limits for thermal, thermo-mechanical and electromechanical stresses.

- The substation including buildings, primary plant and connected infrastructure shall be protected against lightning according to IEEE 998 and IEC 62305 based on the rolling sphere method with effective shielding determined based on the calculated maximum Stroke Current and Strike Distance (IEEE 998) or Determined Protection level as per IEC 62305.

- The lightning protection shall be a combination of lightning protective air termination devices such as lightning masts and Over Head Earth Wire (OHEW) /shield wire coverage, connected to an earthing system.

- Where OHEW shall be applied, they shall be connected to poles or gantries, which shall be bonded to the primary earthing system within the substation by a minimum of two connections.

- Where Lightning masts shall be installed, they shall be installed in the yard as dictated by the lightning protection design and connected to the earth grid via a dedicated earth rod connected to the earth grid.

- Connectors shall be in accordance with IEEE 837 and BS EN/IEC 62561

- Placement of lightning masts shall not obstruct electrical clearances and maintenance access to other equipment within the substation.

### Final Report

The design report, software model and a formal as built CAD drawing showing the lightning protection system coverage plan shall be submitted to ZESCO.

  - MEDIUM VOLTAGE SWITCHGEAR

    - GENERAL DESIGN DATA

The general electrical design data for the plant and equipment shall be as follows:

| Item | Description | Unit | Nominal Voltage Level |  |
| --- | --- | --- | --- | --- |
|  |  |  | 33kV | 11kV |
|  | Nominal system voltage phase to phase | kV | 33 | 11 |
|  | Highest system voltage phase - phase | kV | 36 | 12 |
|  | System Frequency | Hz | 50 | 50 |
|  | Method of System Earthing (on 11 kV level E/C limited 500 A) |  | Resist | Resist |
|  | Impulse withstand voltage (1.2/50 sec wave) - Internal insulation - External insulation, sea level | kV peak kV peak | 170 185 | 95 95 |
|  | Power frequency withstand voltage 1 minute - Internal insulation - External insulation, sea level | kV peak kV peak | 70 80 | 28 32 |
|  | Assumed highest switching surge |  | N/A | N/A |
|  | Substation clearances for equipment not subject to impulse tests - Phase - earth - Phase - phase - Terminals across isolating distance | mm mm mm | 320 320 380 | 250 270 270 |
|  | Cable box clearances for fully insulated shrouded terminals |  |  |  |
|  | - Phase - earth | mm | 100 | 32 |
|  | - Phase - phase | mm | 125 | 45 |
|  | - Phase - earth over cable surface | mm | 250 | 125 |
|  | Transformers |  |  |  |
|  | Winding insulation |  | Full | Full |
|  | - Max flux density at any ratio or tap position | T | 1.8 | 1.8 |
|  | - Acceptable noise levels (1) | dB | 65 | 65 |
|  | Insulation Distances for Equipment, Bushings and Insulators |  |  |  |
|  | - Min surface creepage distance measured from live metal to fixing base | mm | 828 | 275 |
|  | - Min protected surface creepage distance | mm | 289 | 97 |
|  | - Min number of 254 mm dia disc insulators in tension strings |  | 3 | 2 |
|  | Surge Arresters |  |  |  |
|  | Min. rated voltage | kV | 39 | 15 |
|  | - Nominal discharge current (8/20 s) | kA | 10 | 10 |
|  | - Class Distribution Min. protective ratio |  | 1.2 | 1.2 |

    - 33KV OUTDOOR EQUIPMENT

      - 33kV Circuit Breakers

The breakers shall be capable of handling the following operation cycle, according to the IEC recommendations:

0-t-CO-t1-CO		t = 0.3 sec		t1 = 15 sec

The total breaking time (opening time plus duration of the arc) of the breakers shall be as short as possible, but in no case is it to be longer than 75 milliseconds.

A system for monitoring continuously the gas density shall be provided.  At a certain low-density signal shall be given to indicate that refilling should take place.  At the extreme low density, the circuit breaker should be automatically blocked against operation.

The circuit breakers shall be provided with means to prevent contact pumping while the closing circuit remains energised should the circuit breaker either fail to latch or be tripped during closing due to the operation of the protective relays.

Each 33kV breaker shall have one operating mechanism common to all three poles.  A spring-operated mechanism is preferred. Pneumatic operating mechanism is not accepted.

The mechanism shall be provided for electrical local and remote control.  The control voltage for closing and opening commands and for the operating mechanism motor(s), shall be 110V DC + 10% /- 20%, unearthed, from battery.

The opening device shall be provided with two independent trip coils, connected to separate terminal blocks in the terminal cubicle, allowing for the connection of two independent opening command circuits. The trip coils shall be capable of operating at 65% of the nominal voltage.

A local position indicator (circuit breaker status), visible with the panel door closed, shall be mounted in the front panel of the operating mechanism cubicle.

A crank, lever or other similar suitable device shall be provided to permit charging the operation mechanism by hand in the event of a failure of the auxiliary supplies or in the event of a failure of the energy storing device.

The complete operating mechanism, including the controls, shall be built-in water-tight and dust-proof cubicles (min. IP54).  All parts shall be easily accessible without dismantling other parts.  Openings, covered with dust filters, shall allow a good ventilation of these cubicles.  In order to avoid any moisture, thermostat-controlled heaters for 230 V AC shall be built-in. Push buttons for operating the breaker shall be located not more than 1.7 m above ground.

A local/remote control selector switch shall be provided in the cubicle.  With the selector switch set to local control, operation from any remote source including the protective relays shall be inhibited.  The switch shall have spare contacts.

A sufficient number of separate auxiliary contacts, with at least 5 NO and 5 NC contacts as spare, for 110V DC shall be provided for control and interlock purposes.

Motors shall be designed in accordance with valid IEC publication and shall be effectively protected by miniature circuit breakers, with alarm contacts.

All wiring shall lead to terminals.  10% of the terminals shall be spare.

Position for connection of resistance measurement equipment shall be indicated or marked on the circuit breaker terminals.

      - 33kV Isolating Switches and Earthing Switches

The contact surfaces shall be heavily silver-plated.  The contact pressure shall be ensured by means of springs.

Each three-phase isolating switch and each three-phase earthing switch shall be equipped with its own operating mechanism. The mechanism shall be electrically and manually operated. There shall be provision for electrical local and remote control.  The control voltage for closing and opening commands and for the operating mechanism motor(s), shall be 110V DC + 10% /- 20%, unearthed, from battery.

Disconnectors shall have mechanical interlocking attached to earth switches.  The interlocking shall prevent closing of earth switch when the disconnector is in closed position, and prevent closing of the disconnector when the earth switch is closed.

The complete operating mechanism, including the controls, shall be built-in in a water-tight and dust-proof cubicle (min. IP54).  All parts shall be easily accessible without dismantling other parts.  The necessary openings for a good ventilation of the cubicles shall be provided.  They shall be covered with dust filters.  Thermostat controlled heaters for 230 V AC shall be provided for each cabinet in order to prevent any moisture by condensation.

A sufficient number of separate auxiliary contacts, with at least 5 NO and 5 NC spares, for 110 V DC shall be provided for control and interlock purposes.

All wiring shall lead to terminals.  10% of the terminals shall be spare.

      - 33kV Current Transformers

The current transformers shall be single-phase, oil-immersed, mounted in one insulator.  They shall be mounted on steel structures. The characteristics of the current transformers shall comply with the provisions stipulated in IEC 61869 – 1 & 2.

The current transformers shall be designed to carry continuously a current of 120% of the rated current and shall be equipped with an oil level gauge easily visible from the ground.

The oil of the current transformer shall be hermetically sealed against the ambient air. The sealing method shall be described in the Bid, as well as the method of compensation for changes in the oil volume due to temperature changes.

The primary connections shall be silver-plated. All secondary connections shall be connected to a terminal block which shall be located in a dust-proof and watertight terminal box and shall be clearly labelled.

An earth connection to the housing shall be provided.

The rated current of the secondary windings shall be 1 A, unless otherwise specified. The different cores shall have the following characteristics unless otherwise specified.

Line CTs:

Core 1:	 600/1, 15VA, 5P20

Core 2:	 600/1, 15VA, Class 0.2s

Transformer CTs:

Core 1:	 600/1, 15VA, 5P20

Core 2:	 600/1, 15VA, Class 0.2s

Core 3: 600/1, 15VA, Class X

Neutral CT for SBEF: 200/1

For class X CTs, the additional requirements shall be as specified below.

Vk, the knee point voltage corresponds to the point on the magnetisation curve where a 10% increase in voltage results in a 50% increase in current.

Ie, the maximum excitation current (at a given voltage), corresponds to the current output of when a voltage is applied to the secondary terminals of the current transformer with the primary connections open-circuit.

Rct corresponds to the maximum current transformer secondary resistance corrected for a temperature of 75°C.

| Voltage Class | Type | Vk | Ie | Rct |
| --- | --- | --- | --- | --- |
| 33 kV | A | 60(Rct +10) | 30mA @ 50% Vk | 2.4 |
|  | B | 85(Rct + 2.5) | 30mA @ 50% Vk | 2.4 |
| 11kV | A | 85(Rct +2.5) | 30mA @ 50% Vk | 5 |
|  | B | 85(Rct + 2.5) | 30mA @ 50% Vk | 5 |

Class X CT characteristics

The Contractor shall demonstrate that the current transformers selected will ensure correct functioning of the associated protective equipment.

The output of the current transformers for measuring and protection purposes shall be determined according to the technical requirements, but shall not be less than 125% and not more than 160 % of the overall computed (design) burden of the connected apparatus and conductors.

      - 33kV Voltage Transformers

Voltage transformers for shall be of single-phase inductive type and mounted on steel structures.

They shall be equipped with an oil level gauge to be easily visible from ground level. The oil shall be hermetically sealed against the ambient air. The sealing methods shall be described in the Bid, as well as the method of compensation for changes in the oil volume due to temperature changes.

The primary connections shall be silver plated.

All secondary connections shall be connected to a terminal block which shall be located in a dust-proof and watertight terminal box and shall be clearly labelled. The cables from the voltage transformers shall be dimensioned in accordance with the accuracy class of the core.

An earth connection to the housing shall be provided.

The windings for measuring purposes shall be designed for an accuracy according to class 0.5.  Rated secondary voltage shall be 110 /3 V. One of the secondary windings shall be for open delta core with secondary voltage 110/3.

The voltage transformers shall have two additional secondary windings for the protective purposes designed for accuracy according to class 3P.

The secondaries shall be provided with miniature circuit breakers with alarm contacts.

The characteristics of the voltage transformers shall comply with the provisions stipulated in IEC 61869 – 1 & 5.

The capacities of all windings shall be determined according to the technical requirements but shall not be less than 125% of the overall computed (design) burden of the connected apparatus and conductors.

Power frequency test voltage on secondary windings, 1 min.  2 kV.

      - Lightning Arresters

The lightning arresters shall be of the metal oxide gap-less type, complying with IEC 60099- 1 - 9

Maximum continuous operating voltage (MCOV) refers to the maximum r.m.s value of permissible power frequency voltage across the arrester terminals.

The lightning arresters shall have the following characteristics:

33 kV	    11 kV

(1)	Maximum continuous operating voltage (r.m.s.)        30 kV       10 kV

(2)	Temporary overvoltage (TOV)			        36 kV       12 kV

(3)	Duration of TOV					        2 s           2 s

(4)	Rated discharge current 8/20ms			        10 kA       10 kA

The lightning arresters shall be fitted with a pressure relief device.	 Surge counters with leakage current monitoring shall be supplied for each single-phase arrester.

The earth conductor from the arrester to the counter as well as the in-terminal of the counter shall be suitably insulated, or screen protected against accidental touching.

    - 11 kV SWITCHBOARD

      - GENERAL

The 11kV panels shall be of the indoor air insulated type, single bus bar, totally enclosed metal-clad with floor truck mounted withdrawable vacuum circuit breakers. Cable entry shall be at the bottom.

Only switchgear of approved make from established manufacturers shall be accepted. All current carrying parts shall be capable of withstanding the specified short circuit current for three seconds.

The switchgear shall comply with the latest revisions of the IEC standards for electrical materials and equipment. It shall be compact and low profile. All LV equipment such as relays, meters, control switches, and indications shall be readily reachable without the use of a platform by a man standing on the floor.

The switchgear shall be of robust construction and shall be unaffected in part or in whole by the forces imposed by short-circuit or other currents, operation, vibration or temperature changes. It shall comply with BS 5227/IEC 60298 unless otherwise specified herein, and shall be extensible. All components and all materials used in switchgear shall conform to appropriate IEC / BS.

The switchgear shall be designed to facilitate inspection, cleaning, maintenance and repairs. The switchgear shall be of the compartmental design divided into separate compartments for the circuit breaker, the bus bars, cable circuit and the low voltage control, protection and metering equipment.

To facilitate Arc Flash protection, the cable chamber and busbar chamber shall be fitted with Arc flush sensors, suitably positioned to detect any Arc that may occur.

      - RATING

The normal continuous rating of the switchgear and bus bars in the climatic conditions obtained at sites shall be as specified in the technical schedules.

All current carrying parts of the switchgear, namely the circuit breakers, bus bars, current transformers, isolating contacts, connections, joints, etc., shall be capable of carrying the specified rated current continuously. The temperature rise in any part shall comply with the relevant standards (BS159/IEC) taking into account the site ambient temperature. BS rating alongside the site rating in each case shall be stated.

Short circuit ratings of the switchgear shall not be less than 31.5 kA for 3 sec.

      - BUS BARS

The bus bars shall be hard drawn high conductivity copper bars silicon rubber insulated. Other covering material of permanent fixage and suitable for climatic and system conditions in subtropical climate are acceptable. Subject to prior approval, the bus bar shall be site rated for 2500A.

The bus bars on the switchgear shall be arranged to permit future extensions.

      - CIRCUIT BREAKERS

The circuit breakers shall be of the vacuum type and shall have rupturing capacity of not less than 350 MVA. The circuit breakers shall conform to BS 5311 / IEC 56. Type test certificate for the circuit breakers from an internationally recognized testing authority acceptable to ZESCO shall be produced.

The circuit breaker shall be provided with 110 V DC motor charged spring closing mechanism, 110 V DC closing coil and 110 V DC shunt trip coil and shall include the following:

- Facility for manual charging of spring;

- Spring charged / discharged indicator;

- Local barrel type Trip/Neutral/Close control switch;

- Local remote control switch;

- Mechanical ON/OFF indicator;

- Red and green ON/OFF indicator lamps (5 W, 110 V DC).

      - INTERLOCK

All mechanical interlocks shall be of the preventive type and shall be arranged to prevent mal-operation of the equipment if the interlock is defeated.

Electrical interlocks shall also function so as to prevent the closing operation of the circuit breaker.

Clearly labeled mechanical interlocks shall be provided which are designed to prevent:

- A closed-circuit breaker from being withdrawn from or inserted into the isolating contacts;

- Tripping by attempted isolation;

- The closing of a circuit breaker except when correctly located in the service, earthed or isolated positions;

- A circuit breaker from being plugged into the isolating contacts if the arc chutes or circuit breaker chambers are not in position;

- A circuit breaker being closed in the service position when the secondary circuits between the fixed and moving portions are not completed.

      - CURRENT TRANSFORMERS

Current transformers shall conform to BS 3938/IEC 185 and shall be air or resin insulated, multi core. Current transformers shall be so rated and designed that they shall not sustain any damage due to an overload current of up to 120%. The CT ratios and ratings are shown in the SLD, specifications and BOQ, and are as stated in the technical schedules.

      - VOLTAGE TRANSFORMERS

The voltage transformer shall be 3 phase core type fully insulated star/star ratio 11000/3 / 110/3/ 110/3, 100 VA per phase, class 0.5 for metering and accuracy to BS 3941 / IEC 186.

The secondary winding shall be protected by either fuses or MCBs.

      - PROTECTION, CONTROL AND MONITORING

        - 11 KV TRANSFORMER INCOMERS

The 11 kV transformer incomer circuits shall be fitted with a multifunctional IED providing OCEF protection, CB control, Arc flash Protection and measurements of power system quantities (A, kV, kW, kVAr, kVA, kWh).

Additional equipment on each of the incomer shall be a multifunctional electronic energy meter set to summate and display the 30-minute thermal maximum KVA and kWh of both incomers. Energy meters and metering are specified in section 4.2.3.17.

        - FEEDER CIRCUIT

Each feeder circuit on the switchboard shall be provided with a multifunctional IED providing OCEF protection, Arc flash Protection, CB control and measurements of power system quantities. The protection characteristics shall be IDMT and include adjustment settings for both time and current. In addition, there shall also be a multifunctional energy meter on each feeder panel.

      - 11 kV CABLE COMPARTMENT

The cable compartment shall located such that access to the cable termination shall be from there rear of the panels. Cable entry shall be from the bottom. Suitable mounting arrangement shall be provided to for 11 kV, 3 x 1core XLPE single wire armoured and PVC sheathed cable, size 630 mm2 for the incomers and 1x3core 185mm2 cable for the feeders. The design shall provide sufficient space for core crossing without damage to core insulation.

All necessary termination materials and sundries for a complete termination shall be supplied. Cable compartments shall be separated from all other compartments such as CT chambers, bus bar compartments, etc.

      - BUS WIRES

The following bus wires of appropriate copper section, in no case less than 2.5mm2 PVC insulated in appropriate colour code shall be provided on the switchboard.

- DC trip circuit;

- DC close circuit;

- Remote group alarm circuit;

- Circuit breaker “closed” and “open” red and green lamp indication circuit;

- Cable Earth switch “closed” red lamp indication

- Circuit breaker panel heater circuit (230 V AC);

The bus wire shall be neatly cleated and terminated on both sides of each individual panel on terminal blocks with adequately rated terminal studs complete with all necessary provisions for interpanel connection. For connection of power and control cables to the bus wire, necessary cable glands and terminal blocks shall be provided in the incomer switchgear panel.

      - LABELS AND SECONDARY MCBs

Each panel of the switchboard shall have a circuit label approximately 30 cm x 8 cm mounted on the front of the panel in a prominent position. These labels shall be made of suitable engraving material approximately 2 mm thick, white surface with black engraving. Small blank labels of similar material shall be mounted on the rear of the panels. All other labels shall be of similar material and engraved in English.

All necessary MCBs and links shall be supplied and they shall be fitted with clearly legible label indicating the circuit and shall be grouped according to their functions to facilitate identification. MCB labels shall indicate the current ratings and code symbols shall correspond with the diagrams.

      - ISOLATION AND INTERLOCKS

The switchboard shall be provided with approved means of isolation of circuit breakers and circuit and be complete with automatic shutters to screen off all live parts. The switchgear shall be fully interlocked to prevent mal-operation. To obviate unauthorized operation, locks each with two keys of approved make shall be included for:

- Locking out each circuit breaker in the isolated or off position.

- Locking movable shutters screening live parts (lock to be coloured red).

- Locking circuit breakers control switch.

- Locking voltage transformer in the rack in position.

- Locking voltage transformer spout shutters.

All locks to differ and have individual keys.

To facilitate phasing out of any incoming circuits against the bus bars, arrangements shall be provided to enable manual opening or closing any of the related shutters independently with the circuit breaker withdrawn and for locking any of these shutters independently in the open or closed position.

      - CIRCUIT BREAKER ISOLATING EQUIPMENT

The circuit breaker isolating equipment shall be an integral part of the circuit breaker.

      - INTEGRAL EARTHING

Integral earthing shall be provided in the switchboard for circuit preferably through circuit breaker. Spring-assisted earthing switch is also acceptable. The earthing shall be complete with all necessary mechanical interlocks to prevent mal-operation.

The earthing of the bus bar shall be arranged such that earth cannot be applied till all circuit breakers of that bus including bus section are tripped and brought to test position.

      - EARTHING

The switchboard shall be provided with a copper earth bar of the sectional area not less than 50 mm x 4 mm. All metal instrument and relay cases on the panels shall be connected to the earth by copper conductors not less than 2.5 sq.mm cross section.

      - HEATERS

In view of the high humidity prevailing at the sites, each panel shall be provided with suitably rated heater for operation from 230 V AC supply and arranged for switching on when the breaker is off or isolated. This is to prevent condensation on breaker bushings, spout insulators, etc. Heaters shall be controlled by the thermostat and hygrostat. Provision to bypass this control and operate the heater manually shall be made available.

      - INSTRUMENTS AND METERING EQUIPMENT

        - GENERAL REQUIREMENTS

All metering equipment shall be as specified and shall be for the purpose of measuring instantaneous power system quantities (A, V, kW, kVA, kVAr, PF), integrated values such as kWh, kVArh, and maximum demand values in Amps, KVA or kW.

All displays shall be in terms of the primary values. The metering equipment shall comply with the relevant IEC Recommendations. Where maximum demand indicators are specified these shall be in accordance with IEC Publication 60211 for Class 1.0 meters.

Dial type, full deflection 90, 96 x 96 mm switchboard pattern, flush mounting moving iron volt meters and ammeters with maximum demand pointer shall be provided, unless otherwise indicated.

The meters shall have a temperature range of -4C to +70C.

        - SPECIAL REQUIREMENTS FOR ENERGY METERS

Energy meters shall be of the multifunctional electronic type and shall comply with the requirements of IEC Publication 521. Demand measurement shall be selectable between kW and kVA while the demand period shall be selectable between 15 to 60 minutes.  All energy meters shall be capable of being read remotely from the Lusaka District Control Center.

The energy meters shall be capable of storing demand data for load profiling. In particular they shall be able to store the monthly energy and maximum demand for all the 12 months of a year. The date and time of occurrence of maximum demand shall also be stored. It shall also be possible to download these historical monthly meter readings to a laptop. Software for the laptop shall also be supplied for communication with the meters. This shall be priced under tools and spares.

All meters shall be surface mounted on steel frame inside the panels.

The Contractor shall include a training program including training in setting, use of programming tools, fault finding and maintenance. The training shall include operators and maintenance personnel. Meters shall be supplied complete with all manuals, CDs, test certificates and programming accessories.

        - LABELS

All meters shall be clearly and permanently labelled to the approval of the Engineer. The dimensions and size of lettering shall be to the approval of the Engineer. Labels should have black lettering on a white background.

      - AUXILIARY SWITCHES

Auxiliary switches shall be provided to interrupt DC supply to trip and closing coils immediately after their operation has been completed.

All necessary auxiliary switches for control, protection and indication for supervisory control shall be provided on each circuit breaker panel plus two spare ways normally close and two spare ways normally open. The auxiliary switches shall be wired to a suitable terminal block on the panel.

      - TRIP HEALTHY INDICATION

The trip healthy indication shall be provided on each circuit breaker by the respective protection relay.

      - LOCAL / REMOTE SELECTOR SWITCH

A local/remote selector switch shall be provided on each circuit breaker panel to facilitate control of the breaker from a remote location. In remote position the control will get transferred to SCADA.

      - PENDENT SWITCH (ON/OFF)

A pendent port shall be provided on each feeder and incomer panel along with two (2) 12 meter long pendent switch for break ON/OFF operations.

      - TEST TERMINAL BLOCKS

Current transformer secondary wiring shall be connected through terminal blocks with change-over links to permit easy testing.

The terminal block shall be mounted in front of the panel and suitably insulated and provided with a detachable dust proof cover.

      - SMALL WIRING

All wiring shall be 2.5 sq.mm stranded copper conductor, 600 V tropical grade PVC insulated. All small wiring shall be suitably terminated and fitted with captive identification with circuit number. Trip circuit shall have an additional ferrule coloured red and marked "Trip".

Each circuit identification number shall be suffixed with the panel identification letter. All terminal blocks shall be provided with detachable covers. The trip circuit cables shall be coloured black. The current transformer secondary wires shall preferably be coloured with their respective phase colours.

      - SUMMARY TECHNICAL DATA

        - DESCRIPTION:

11kV, air insulated panel, single busbar, indoor metal clad vacuum Switchboard, floor mounted, withdrawable.

        - RATINGS:

BIL        	:	95kV peak

Frequency	:	50 Hz

Fault Level	:	31.5kA for 3 seconds

        - MECHANISM:

Motor charged, spring tensioned trip free mechanism with mechanical ON/OFF indicator, operation counter and spring charged /discharged Indicator.

## POWER CABLES AND ACCESSORIES

### GENERAL

All cables, accessories and materials shall be in accordance with the latest editions (including all amendments) of IEC and ISO Recommendations and National Standards approved by the Project Manager subject to variations and additions stated in this Specification.

All cables shall be suitable for operation.

(a)  on a system either direct or through resistance or reactance at one or more neutral points

(b)  under the loads specified and such sudden variations of load and voltage as may be met with under working conditions on the system and

(c)   in the climatic conditions prevailing on Site.

The design, manufacturing and testing shall comply with the below listed standards:

IEC Safety	IEC Safety Handbook containing all basic safety standards

IEC 60038	Standard Voltages

IEC 60059	Standard Current Ratings

IEC 60287	Calculation of the continuous current rating of cables

IEC 60332	Tests on electric cables under fire conditions, Part 3: Tests on

bunched Wires or cables, Category C.

IEC 60502	Extruded solid dielectric insulated power cables for rated voltages from 1 kV up to 30 kV

IEC 60811	Common test methods for insulating and sheathing materials of electric and optical fibre cables

CCITT 	G.650, G.653 and G.659

|  | Description | Unit | Nominal voltage level |
| --- | --- | --- | --- |
|  |  |  | 33 |
| 1 | Nominal system voltage phase to phase | kV | 33 |
| 2 | Highest system voltage phase - phase | kV | 36 |
| 3 | System Frequency | Hz | 50 |
| 4 | System earth | ---- | Solid |
| 5 | Impulse withstand voltage (1.2/50 sec wave) | kV ak | 200 |
| 6 | Power frequency withstand voltage 1 min. | kV | 85 |
| 7 | Assumed highest switching surge |  | 4.5 |
| 8 | Transformers |  |  |
|  | Winding insulation |  | Full |
|  | Max. flux density at any ratio or tap position | T | 1.7 |
|  | Acceptable noise levels | dB | 50-60 |
| 9 | Insulation levels for Equipment, Bushings, and Insulators | Mm | 828 |
|  | Min surface leakage distance measured from live metal to fixing base | Mm | 289 |
|  | Min protected surface leakage distance | Mm |  |
| 10 | Surge Arresters, Min rated voltage | kV | 39 |
|  | Nominal discharge current (8.20 s) | kA | 10 |
|  | Class Distribution Min. protective ratio |  | 1.2 |

The following assumed values of soil thermal resistivity, soil and air temperatures are for Bid evaluation purposes only.

Ground temperature o C	20-30

Soil thermal resistivity o C m/W	1.8

Max. ambient shade temperature o C	30-45

### Cables

### Conductors

All conductors shall be stranded copper or aluminium as specified in the Schedules.   The conductor shall be clean, uniform in size, shape and quality, smooth and free from scale, spills, splits, sharp edges and other harmful defects.

They shall be circular, shaped, stranded, bunched and multiple stranded, as required, to suit the cable specification and shall comply with the requirements of IEC Recommendation No. 228 where applicable.

Where joints are permitted in individual wires, formed into a conductor, they shall be made in the manner prescribed in the appropriate standard and the frequency shall conform to the limiting dimensions stated therein.  No joints shall be made in the conductor after it has been formed.

### Conductor Screening

Conductor screening shall be employed at rated voltages above 1.8/4.0 kV for cables insulated with XLPE and shall consist of a layer of extruded semi-conducting material having a smooth even surface in intimate contact with the cable insulation and the conductor, but easily strippable from the conductor surface.

### Insulation

Power cables shall be insulated with one of the following materials EXCEPT where the type of cable is specified in detail in the Schedules: -

Polyvinyl chloride (PVC) for 600/1000-volt cables or

Cross-linked polyethylene (XLPE) for 11/33 kV cables.

### Core Screening

Core screening shall be employed at rated voltages above 1.8/4.0 kV for cable insulated with XLPE and shall consist of a layer of semi-conducting material having a smooth even surface in intimate contact with the cable insulation and a concentric screen of copper wires and tape applied overall.  Full details of the method used for stripping the screen shall be provided with the Bid.

### Identification of Cores

The cores of all two, three and four core power cables shall be identified by numbers or colours in accordance with IEC standard or approved National Standard. All cores shall be multistrand.

### Laying-up and Fillers

The cores of all twin and multicore cables shall be laid-up together with suitable fillers, wormed circular and binding tapes applied overall.

The fillers for XLPE cables shall be non-hygroscopic. The direction of lay of the cores shall be right-hand for all twin and multicore power cables.  The term “right-hand” has the same meaning as for screw threads. All finished cables shall be circular.

### Manufacturer’s Identification

The manufacturer’s identification shall be provided throughout the length of the cables by means of a tape under the sheath printed with the manufacturer’s name.  Alternatively, the manufacturer’s identification may be embossed on the outer PVC sheath together with identification and voltage markings.

### Armour

All cables shall be AWA according to IEC60502-1.

### Testing

Notwithstanding that cables are manufactured to an approved National Standard all cables, accessories and materials shall be subjected to and withstand satisfactorily the test requirements detailed in this specification subject to any exceptions stated therein.  All materials shall withstand such routine tests as are customary in the manufacture of the cables and accessories included in the Contract.

### Sealing and Drumming

The cable shall be wound on strong non-returnable drums arranged to take a round spindle of a section adequate to support the loaded cable drum during installation and handling. 5 % of the cables of each type supplied shall be delivered on steel drums. The drum shall be lagged with strong closely fitting battens which shall be securely fixed to prevent damage to the cable.  Wooden drums shall be constructed of seasoned timber to prevent shrinkage of drums during shipment and subsequent storage on site.  Each drum shall be clearly marked in a manner which cannot be obliterated with the particulars of the cable including voltage, length, conductor size, number of cores, type of protective covering, section number, gross and net weight, together with the direction for rolling.

The ends of cables shall be suitably sealed to prevent the ingress of moisture. The end of the cable left projecting from the drum shall always be securely protected against damage by mishandling during transport or storage.

Drum lengths of cables shall not exceed the following:

11 and 33 kV, 3-core cables, maximum length 			300 m

600/1000V, 4 core cables, maximum length			300 m

600/1000V, 1-core cable, maximum length			300 m

600/1000V, ABC maximum length					1000 m

600/1000V, Concentric cables, maximum length		1000 m

### Current Carrying Capacity and Design Parameters

The maximum continuous current carrying capacity and maximum permissible continuous conductor temperature, and the factors for determining such rating and temperature shall be based on IEC Recommendation No. 287 and subsequent amendments and all conditions prevailing on the Site.

## Accessories

### Cable Joints

20% of the total cable joints shall be supplied as spares completed with joint accessories. The bid prices covering cable shall be deemed to have included these spare cables and accessories. The Bidder shall submit with his Bid drawings showing the types of joint boxes proposed for each of the cables included in the Contract.

The joints shall be watertight, free from sharp points or ridges, thoroughly clean internally and externally and designed to retain the filling medium at all times without leakage.  The sleeves shall be of sufficient diameter and length to permit colour-to-colour jointing without undue bending, handling or deformation of the cores.

### Straight and Branch Service Joints

Designs for straight and branch service joints for PVC and XLPE insulated power cables and all termination materials together with jointing instructions shall be submitted for approval by the Project Manager before factory orders are issued for manufacture.

Joints shall provide adequate mechanical and electrical security to the jointed cables when buried in pavements and roads.

The screens and armour of all cables shall be adequately bonded across each joint in an approved manner.

All resins and hardeners shall have a shelf life of at least 3 years from date of shipment to site.  They shall be compatible with the cable insulation and sheath materials.

### Termination

Detailed drawings showing the types of cable sealing ends, terminal boxes and glands and overhead line terminations shall be submitted to the Project Manager for approval.

Sealing ends and terminal boxes shall be provided with all necessary fittings, including arcing horns and external flexible connections as required. Drain plugs shall be of ample size where applicable, to permit the filling medium to be removed.

Stress cones or other approved means shall be provided for grading the voltage stress on the core insulation of screened cables.

Termination for all HV cable may be of an approved heat shrink design incorporating a suitable arrangement of stress control, and rain-sheds for outdoor use. Termination kits shall include suitable heat shrink tubing to effectively shroud, seal and insulate the exposed cable conductor and connector, and shall include a heat shrink glove to effectively seal the crutch of the cable to prevent ingress of moisture into the interstices of the cable.  Suitable arrangements shall be provided to earth the cable screen and armour.

Termination into cable boxes shall include brass compression glands and back nuts of the correct size, which shall secure the cable outer sheath and ensure effective electrical continuity between the cable armouring wires and the metal enclosures on which the cable is terminated.  At all rising termination’s the cable inner sheath shall pass through the gland to terminate not less than 6 mm above the gland.

Provision shall be made for earthing all sealing end baseplates, cable boxes, glands and armour clamps.

## POWER TRANSFORMERS

### GENERAL

### Materials and Labelling

All materials used shall be of the best quality and of the class most suitable for working under the conditions specified and shall withstand the variations of temperature and atmospheric conditions or the setting up of any undue stress in any part, and without affecting the strength and suitability of the various parts for the work which they have to perform.  No welding, filling, or plugging of defected parts will be permitted without the permission in writing of ZESCO's representative.

Cast iron shall not be used for chambers of oil or for any part of the equipment which is subject to impact and tensile stresses.  This clause is not intended to prohibit the use of suitable grades of cast iron for parts where service experience has shown it to be satisfactory.

All connections and contacts shall be of ample section and surface for carrying continuously the specified currents without undue heating.  Fixed connection shall be secured by bolts or set screws of ample size, adequately locked.  Lock nuts shall be used on stud connection carrying current.

On outdoor equipment, all bolts nuts and washers in contact with non-ferrous parts which carry current shall be of phosphor bronze.

## DESIGN CRITERIA

### Service Conditions

The transformer shall be capable of operating continuously outdoors at any tapping during the ambient conditions specified in General Specifications.

Note that the average ambient temperature in any one day is 40oC.  The maximum temperature rise of the top oil shall therefore not exceed 55oC and 60oC of the winding above the maximum ambient temperature of 45 o C.

For temperature correction due to altitude reference is made to IEC Publication 60076-2, Clause 2.3 which limits the temperature rise further, when tested at normal altitude, by 2 % for ONAN cooling and 3 % for ONAF.

### Rating

The transformer shall comply with the ratings specified in Scope of Works and Supply under the stated service conditions without exceeding the temperature rise limits specified in 5.2.1 above, over the complete tapping range.  If the voltage on the secondary (LV) side is reduced or raised by up to 5% from the rated voltage, the temperature rises of any part shall not rise by more than 5 o C (at rated power on any primary tapping).

### Tapping

All tapping shall be designed for constant kVA output, the rated voltage of each winding of the transformer on the principal tapping shall be as specified in Scope of Works and Supply and unless otherwise specified, shall correspond to the system nominal voltage.  The tapping ranges shall be as specified in Scope of Works and Supply.

### Noise

The transformer, tap-changing equipment and supplementary cooling equipment shall operate without undue noise and every care shall be taken in the design and manufacture to reduce noise to the level of that obtained in good modern practice.  The noise level of the transformer shall not exceed 78 dB when tested in accordance with IEC 60076 -10

### Radio Interference

The design of the transformer shall be such that they will not cause any objectionable interference with radio reception in the vicinity of the transformer, either by direct radiation or by transmission through the power-lines and system to which the transformer may be connected, when energising at full rated voltage and when delivering any load up to the continuous maximum rating.

### Interchangeability and Paralleled Operation

All transformers of any one type shall be identical and interchangeable with one another.  No alteration to control circuits shall be permissible for this purpose except by means of built-in terminal boards fitted with links for effecting the alteration.  All parts are to be made accurately to dimensions so that any corresponding parts will be interchangeable, and any spare parts will fit into place without need of adjustments.  Where similar equipment has previously been supplied, components shall interchange with those on previous contracts, unless otherwise approved.

The transformer shall be suitable for parallel master-follower operation with each other and with transformer of a similar rating, previously supplied, both in respect of transformer characteristics and control circuits on all relevant taps, under which conditions they shall share the load subject to the tolerances of impedance and voltage laid down in BS 171, IEC standard 60076 or equivalent standards (See also Section 4.5 of these specifications, i.e. voltage control equipment).

### Insulation Levels

When assembled complete with connections as in service, electrical clearances in air shall be adequate to withstand the required impulse withstand voltage.  The insulation level for bushings must be corrected for high altitude and particular reference is made to IEC Publication 60137, Clause 16 in this respect.  Minimum bushing BIL insulation levels at sea altitude shall be at least one voltage class (according to IEC) higher than the winding insulation levels which corresponds to 1300 kV,750 kV and 170 kV for 330kV, 220 kV,132 kV and 33kV operating voltages respectively. The Bidder shall propose in his Bid details of bushings with drawings showing air clearances and creepage distances. The creepage distance shall not be less than 31 mm/kV line voltage.  Care shall be taken to ensure that no fittings are located to interfere with the external connections to the bushing terminals.

The windings at the 330kV level may have graded insulation, the neutral points being solidly connected to earth. Windings of lower voltages shall have full insulation. The insulation levels at sea level for the various windings shall be as follows:

| Operating Voltage kV RMS | Highest System Voltage kV RMS | Impulse Test Voltage kV Peak | Power Frequency Voltage kV RMS |
| --- | --- | --- | --- |
| 33 | 36 | 170 | 70 |
| 132 | 145 | 650 | 275 |
| 220 | 245 | 1300 | 570 |
| 330 | 362 | 1425 | 610 |
| 400 | 420 | 1425 | 610 |

### Short Circuit Performance

The transformers shall be capable of withstanding, without damage, the effects of a symmetrical three-phase short circuit and a phase to earth short circuit under conditions specified in IEC 60076 or in relevant sections of other approved standards.

It can be assumed that during a short circuit, nominal voltage will be maintained on one side of the transformer with a short on the other, the external impedance being zero.  It can also be assumed that up to four transformers may be connected in parallel between HV and LV busbars.

### Frequency

The normal frequency will be 50 cycles per second.  The transformer shall, however, be suitable for continuous operation with frequency variation of plus or minus 2½ per cent from the normal, without exceeding the temperature rise limit specified in Clause 4.1 in this Section.

### Flux Density

The maximum flux density in any magnetic component under any condition of voltage and frequency specified under all the operating conditions given in this Specification shall not exceed 1.9 Tesla. The manufacturer shall provide an over fluxing characteristic for all transformers.

### DESIGN

#### General

Transformer shall be of the oil immersed type suitable for outdoor use, they shall be dried out at the manufacturers’ works and it should be possible to commission them without further dry out.

Designs shall be such that water does not collect on any of the equipment.  Particular attention shall be paid in the design of all equipment to ensure that there is no damage to working parts or insulation through the ingress of dust, insects or vermin which are prevalent for long periods in the year.

Live metal of auxiliary connections in air shall be screened to prevent accidental contact and shall be enclosed in compartments which are fitted with approved means to provide reasonable dry conditions within the compartments; in addition, where there are auxiliary connections at 380 Volts or more, "Danger" notices shall be affixed to the outside of the compartments.

When specified in Scope of Works and Supply and in addition to any range of tapping available by tap change operations, facilities for selecting several different rated voltage ratios shall be provided preferably by arranging the appropriate untapped windings in sections which may be connected in series or in parallel readily accessible changeover links shall be provided to allow selection of series or parallel connections.  The cover for the opening providing access to the links shall be labelled to show the purpose of the opening and shall be fitted with a diagram plate with material impervious to corrosion which shall be engraved to show the arrangement of links for each ratio together with link terminal numbers which shall be engraved on link board and shown on the transformer main diagram.

#### Cores

The transformer core shall be built up of laminations of the best quality non-ageing cold-rolled grain-oriented silicon sheet steel of high permeability and loss coefficient.  All joints between laminations shall be of the interleaved type and the laminations shall be clamped securely.  Bolting of the core should be avoided to reduce losses.  On no account shall butt joints be offered.  The cross-section of the core shall form an approximate circle.

The laminations shall be separated by hot-oil proof insulation, and the clamping of the frame shall be firm to ensure even pressure over the whole of the core laminations to prevent undue vibrations or noises.

The core sheets shall be insulated with high-grade oil-proof insulation, for example magnesium-silicate-phosphate.  Paper will not be accepted.

The magnetic circuit shall be designed to avoid the production of flux components at right angles to the plane of laminations, which may cause excessive local heating.

The core clamping arrangement and framework shall be efficiently insulated from the cores and withstand applying 2kV, 50 HZ during 1 minute.  The core shall be designed and built up in such a manner as to avoid accidental or slow development of short circuit paths through the iron and framework.

Each part of the core shall be electrically earthed to the transformer tank.  The internal earth connection shall be of the detachable link type and shall be in an accessible position.

The core, framework, clamping arrangements and general structure of the transformer shall be of robust design, capable of withstanding any shock to which they may be subjected during transport, installation, or service.

Suitable axial cooling ducts shall be provided to ensure free circulation of oil and efficient cooling of the core.  The ducts shall be proportioned so that the maximum temperature at any point will be within the prescribed limits of temperature rise.

Lifting lugs or other similar means shall be provided for conveniently lifting the complete assembly (with windings).

Provision shall be made for efficient arrangement of guides to prevent movement of the core and windings during transport, installation, or service.

The framework of the core shall be so designed as to prevent the presence of oil pockets, which would prevent complete emptying of the oil from the tank through the drain valve.

#### Windings

The windings shall be circular and consist of high-quality rectangular section copper, wound with age resisting paper of high dielectric strength.  The current densities in the windings shall be stated in the Bid.

The amount of insulation between turns shall be determined not merely by normal volts per turn, but also by due consideration of the line voltages and the service conditions, under heavy lightning storms.

Adequate insulation and clearances between the windings shall be provided and all insulation and clearance between live parts must be adequate for operation at 5 per cent over the highest tap voltages on all the windings.

The insulation of the end turns of each winding adjacent to the transformer terminals shall be reinforced between turns to protect the windings satisfactorily against surges and transients.  Details of the reinforcements shall be given in the Bid.

The insulation of the transformer windings and connections shall be free from insulating composition likely to soften, ooze out, shrink or collapse during service.  None of the materials used shall shrink, disintegrate, carbonise or become brittle under the action of hot oil, when the transformer is operated continuously at the maximum specified over loading.

The windings shall be so placed that they remain electrostatically balanced with their magnetic centres coincident under all conditions or operation.  To prevent excessive static voltage, static end rings shall be provided, wherever necessary, at the live end of the windings.

The windings, connections and trappings of the transformer shall be clamped in position and braced to withstand shocks or undue stresses during transport, short circuit conditions, and other transient causes.  No mechanical movement of the coils should be possible with dead short circuit on the transformers.

All windings and all fibrous and hygroscopic materials used in the construction of the transformer, shall be dried under vacuum, and impregnated with hot oil.  Full details of the drying out and vacuum treatment shall be furnished by the Bidder.

Leads from windings to terminal board and bushings shall be rigidly supported to prevent injury from vibration and short circuit forces.

Adequate provision shall be made for the circulation of oil round and between the winding so that a low temperature gradient between the conductors and the oil is assured and any danger of excessive local heating is avoided.

The finished width of any duct and clamping arrangement shall be such as not to impede the free circulation of oil through the ducts.

It is essential that the windings shall be subjected to a thorough shrinking and seasoning process, so that no further shrinking of windings occur at site.  However, clamping arrangement shall be provided for taking up any possible shrinking of coils when in service.

All similar coils shall be strictly interchangeable.

Full detailed description of the windings shall be submitted with the Bid.

When specified, stabilizing windings shall be provided. The windings shall be capable of withstanding the forces to which they are subjected under all conditions, particularly the forces due to a short circuit between terminals or between any terminal and earth with full voltage maintained on all other windings intended for connection to external sources of supply.  When stabilizing windings are to be used for purposes other than decreasing zero sequence impedance, this will be declared in the Bid documents and the windings must be designed accordingly.

Unless otherwise specified, each corner of the stabilizing winding shall be brought outside the tank for connection to auxiliary transformers or reactors and suitable bushing shall be provided for this purpose through the tank cover.

It shall be possible to earth the winding externally to the main tank by means of a flexible bolted link to be provided by the supplier between the terminal and a suitable pad on the tank cover.

The neutral points of star connected windings shall unless otherwise specified in Scope of Works and Supply be brought out to bushings located on the tank cover and connected to an earthing bus attached to the main transformer earth terminal.

Where the star point of a winding is not specified to be brought out through a neutral bushing, the connection shall, nevertheless, be available under the main tank cover plate to permit the subsequent fitting of a neutral bushing.  The subsequent installation of this bushing shall not necessitate any alteration to or repositioning of existing fittings.

#### Current Transformer

Current transformer for winding temperature measurements shall be mounted inside the transformer on the bushings, and in the connection between winding and neutral point for autotransformers.

Accuracy class 3 shall be used for temperature indication.

#### Internal Earthing

The transformer and core earthing should be brought to the top of the transformer and be accessible for test purposes. The top main core clamping structure shall be connected to the tank body by copper strap.

The bottom clamping structure shall be earthed by one or more of the following methods:

a.	by connection through vertical tie rods to the top structure.

b.	by connection to the top structure on the same side of the core as the main earth connection to the tank.

The magnetic circuit shall be earthed to the clamping structure at one point only through a removable link placed in an accessible position beneath an inspection opening in the tank cover.  The connection to the link shall be on the same side of the core as the main earth connection and be taken from the extreme edge of the top yoke.

Magnetic circuits having an insulated sectional construction shall be provided with a separate link for each individual section and the arrangement of the connections shall be to approval.

Where oil ducts or insulation parallel to the plane of the laminations divide the magnetic circuit into two or more electrically separate parts, the ducts or barriers shall be bridged in accordance with Clause 4.2 and the magnetic circuit shall not be regarded as being of sectional construction.

Where coil clamping rings are of metal, each ring shall be connected to the adjacent core clamping structure on the same side of the transformer as the main earth connection.

All earthing connections, except for those from the individual coil clamping rings, shall have a cross-sectional area of not less than 90 mm2.  Connections inserted between laminations may have the cross-sectional area reduced to 25 mm2 where in close thermal contact with the core.

#### Tanks

Tanks shall be complete with all accessories and shall be designed to allow the complete transformer in the tank and filled with oil, to be lifted by crane or jacks, transported by road, rail and water without overstraining any joints and without causing subsequent leakage of oil.  Corrugated tanks are not acceptable.

Each transformer shall be enclosed in a steel tank of welded construction, suitably stiffened by means of channel or angle sections welded to the tank, for withstanding the stresses imposed during transit to site and subsequent operation with no signs of oil leakage.  Bell type transformer tanks are not permitted.

The tanks must be so constructed as to be capable of withstanding an internal positive pressure of not less than 70 kPa without any permanent deflection of any parts.  The tank must also be capable of withstanding a vacuum of 50 mm of mercury absolute when emptied of oil.

Guides shall be provided inside the tank to facilitate the lowering into the tank of the core and coils and their raising and correct positioning.  The guides shall extend from the bottom of the tank to within 150 mm of the top of the tank.

The tank covers shall be bolted to the tank and of adequate strength and shall not be distorted when lifted.  Inspection openings suitably bolted shall be provided as necessary to give easy access to bushings, tap changer connections and earth connections.  Each inspection opening shall be of ample size for the purpose for which it is provided.  Manhole covers must be provided with lifting eyes where necessary.  The tank cover and all inspection covers shall be provided with lifting eyes.

Detachable radiators shall have lifting eyes and shall be provided with drain plugs or valves at their lowest points and vent plugs in the headers.  Isolating valves shall be provided immediately adjacent to the main tank or headers to enable the radiators to be removed without handling the oil in the transformer tank.

All oil-pipe connections shall have flanged joints provided with gaskets, preferable set-in grooves or held in position by stops to prevent over compression of the gaskets.

The base of the tank shall be so designed that it shall be possible to move the complete transformer unit in any direction without injury when using rollers, plates or rails.  A design which necessitates rails being placed in a particular position shall not be used.

Lifting lugs shall be fitted capable of lifting the transformer complete with windings and filled with oil.

Four jacking lugs shall be fitted 500 mm above ground level and four holes with a diameter of not less than 508 mm shall be provided on the jacking lugs to permit the transformer to be slewed in any direction.

The tank cover shall be fitted with pockets for a thermometer and for the bulbs of the winding temperature and oil temperature indicators specified.  Protection shall be provided when necessary for each capillary tube.  The thermometer pocket shall be fitted with a captive screwed cap to prevent ingress of water.  The pockets shall be located in the position of maximum oil temperature and it shall be possible to remove the instrument bulbs without lowering the oil in the tank.

The tank cooling equipment shall be designed to permit vacuum treatment on site.  The maximum safe permissible vacuum (millimetres of mercury) which may be applied above oil level, to the tank, cooling equipment and to the conservator, without causing permanent distortion, shall be stated in the Bid.

Two earthing terminals located at opposite side of the tank, capable of carrying for 30 seconds the full lower voltage current of the transformer, shall be provided.   Provision shall be made at positions close to each of the four bottom corners of the tank for bolting the earth terminals to the tank structure to suit local conditions.

A rating plate shall be fixed to the tank at a height of not more than 1,550 mm above ground level.  A diagram plate shall also be fixed to the tank in an easily accessible position.

#### Gaskets

Oil-resisting synthetic rubber used as a bonding medium for cork or similar material, or alternatively, where steel stops are provided to prevent over compression of the gaskets.

The Contractor shall submit details of gasket material for approval.

Spare unused sets of gaskets shall be supplied for use on site for all positions where joints must be made after transportation of the transformer.

#### Bushings

Bushings shall be fitted to the equipment as specified in Scope of Works and Supply. All terminals shall be marked to correspond with the markings on the diagram plate.

The transformer bushings shall withstand accidental arcing or flashover without seals or other vital parts becoming damaged.  Stresses due to expansion and contraction in any part of the bushing shall not lead to development of bulges, hair-line cracks or other defects.  Suitable connecting clamps shall be able to absorb shocks due to vibration of the connecting jumpers.  The bushings shall withstand internal vacuum in the transformer tank.

All the bushings of any transformer shall have a rated current of at least 120% of the rated currents of the windings to which they are connected (in order not to limit over-loads).

For every substation where one or more transformers is supplied, one spare bushing of each type used shall be included.

#### Vibration

The transformer shall be erected on anti-vibration pads or mountings when specified to be supplied by the manufacturer which shall be to the approval of the Employer's representative, the Project Manager.

#### Painting and Galvanising

Oil-filled transformer shall have their interior surfaces sandblasted and finished with two coats of anti-corrosive and oil-resistant priming paint.  Exterior surfaces shall be sand-blasted and have two rust inhibiting priming coats and one intermediate coat with paint on zinc chromate or urethane alkyd basis or equivalent: one final coat of weather and oil resistant paint.  Minimum total thickness 0.16 mm.

The radiator external surfaces shall be hot dip galvanized with a zinc deposit on average not less than 400g/m2.

Control boards, panel boards, cubicles, cabinets, etc. in dry rooms shall have interior surfaces painted with at least one priming and one finishing coat of anti-corrosion paint.  Exterior surfaces shall be adequately treated to be substantially corrosion resistant, with one prime coat and two finishing coats.

Other indoor installations in dry rooms shall be carefully cleaned, if possible, sand blasted and painted with two coats of oil resistant paint.

Outdoor installations and indoor installations in wet and damp rooms shall have at least one prime coat and two layers of paint on zinc powder basis to be applied after perfect cleaning.

The particulars of priming and finishing paintings shall be stated in the Bid, with specifications of paint, together with a listing of colours available, for each of the plant and equipment.

The Employer is not bound to accept the finishing colour proposed by the Bidder.  Determination of colour shall be at the option of the Employer and shall be finalized at the time of approval of drawings.

The exterior finish of outdoor control cabinets shall be in the same colour as that for the transformer.

Should any paint work be damaged during transit or erection, this shall be made good on site.

All interior and exterior surfaces, subject to corrosion, that cannot readily be painted shall be hot dip galvanized with an average thickness not less than 0.1 mm.  Bolts and nuts associated with galvanized parts shall be hot-dip galvanized, electro-galvanized or sherardized and shall meet the test prescribed in BS 729, i.e. four dips in Copper Sulphate solution.

### FITTINGS

The transformer shall be supplied with the fittings specified in Scope of Works and Supply.  These fittings shall comply with the following clauses:

#### Off-load Tap Changer

Transformer, if specified in Scope of Works and Supply, shall be provided with a ganged off-load tap changer operated by means of an external handle which can be pad-locked in each operating position.  This switch shall have a rotary motion of operation.  The tap changer shall be indelibly marked to indicate the tapping position corresponding to the diagram plate.

Tap changers with mercury sealing glands are not acceptable.

The tapping range shall be as specified in Scope of Works and Supply.

#### Conservator

The conservator shall be mounted on the main tank.

The conservator shall be fitted with a removable end on which shall be mounted the oil gauge.  The conservator tank shall be mounted to slope lightly downwards towards the drain valve, which shall be adjacent to the removable end.

The pipe connecting the conservator to the tank shall extend at least 50 mm into the conservator and shall be brought out from the highest point of the main tank cover.  A valve shall be provided immediately adjacent to the conservator.  All pockets and bushing turrets of the main tank shall be connected into this pipe between the transformer and the Buchholz relay.

The conservator shall be so dimensioned that it will permit all expansion over the working range of temperatures from no load with the transformer cold and at -10oC ambient air temperature to full load at 45oC ambient air temperature while the sump pipe remains covered with oil and the oil level is visible or indicated.  In any case, the volume of the conservator shall be at least 10% of the transformer oil volume.

The oil connections from the transformer tank to the conservator vessel shall be arranged at rising angle to the horizontal.  The Buchholz relay (see Clause 4.6) shall be fitted in this pipe in such a position that inspection, testing and dismantling is possible with the transformer in operation.  A step valve shall be provided between the conservator and the relay.

The conservator shall be equipped with the following fittings:

- A sump which may be formed by extending the inlet pipe inside the conservator.

- A manhole formed by bolting one endplate of the conservator.

- A drain valve with flanged plug.

- A flanged filling plug.

- An oil level gauge of the type specified in Section 4.4.3 below.

- A filter valve.

#### Dial-type Oil Gauges

Dial-type oil gauges, where specified, shall be of the magnetically operated type, in which breaking of the gauge glass will not release any oil.  The gauge shall be fitted with at least two circuit-closing, ungrounded, low-oil-level alarm contacts.

#### Silica-Gel Breathers

Each conservator shall be fitted with a silica-gel type dehydrating breather to approval.  The breather shall be provided with an oil cup or other device which prevents contact between the dehydrating agent and the air outside the transformer.  If an oil cup is provided, the oil should be visible from the outside and the lowest oil level should be marked.

The weight of the dehydrating agent shall be not less than 0,5 kg per 1500 litres of oil in the transformer and cooler.

Unless the silica-gel container is transparent the breathers shall have a window for inspection of the colour and condition of the silica-gel and oil cup or other device to prevent continuous contact of the silica-gel with the air outside the transformer.

#### Explosion-Vents

Explosion-vent pipes shall have a diaphragm of approved material fitted at the upper end only.  An equalizing non-ferrous pipe shall connect the air space of the explosion vent with the air space of the conservator, but where this pipe would be unduly long or its presence affect electrical clearances, a small silica-gel breather may be fitted at ground level and connected to the upper end of the vent pipe by means of a small-bore non-ferrous pipe.  If the explosion-vent pipe is connected to the top of the main tank, it shall either extend 50 mm into the main tank or be provided at the lower end with a gas deflector.

The explosion-vent shall be provided of sufficient size for the rapid release of any pressure which may be generated within the tank, and which might result in damage to the equipment.  The device if used shall be so placed that any discharge from it will not be deposited on any part of the transformer or its associated equipment.

The diaphragm shall be of approved design and material and shall be provided with a protective cover during transport.

The specification of the overpressure relief device shall be approved by the Project Manager. The device should not malfunction if the oil level in the conservator rises beyond the 75 % level.

#### Buchholz Relays

Buchholz relays shall be of the double-float type with separate floats for alarm and shut-down at low and high-speed gas development and shall be of approved manufacture suitable for operation in transformer oil as specified over the temperature range -10oC to 115oC.  The two contact sets shall not be exposed to oil and shall be wired to the marshalling box.

The relays must be interposed in the connecting pipe between the oil conservator and the transformer tank in such a manner that all gas from the tank must pass through the relay as it rises to the oil conservator.

Two copper pipes shall be connected to the two pet cocks on the relay and extended to position 1 m above ground level and fitted with stop cocks for sampling and testing purposes.  The stop cocks are to be labelled and easily accessible and be clear of surrounding steelwork.  The sight window of the relay shall be readily visible from ground level.

#### Temperature Indicators

The local temperature indicators shall be of the dial-type graded in oC with a manually resettable pointer to register the highest temperature reached.  The local indicators shall be mounted on the transformer tank in a suitable weatherproof steel cabinet with a lockable door.  The cabinet and gauges shall be so positioned as to allow easy access to and readability of the gauges.

Each transformer shall be provided with winding temperature indicators of the "thermal image" type compensated for changes in ambient temperature (one for each winding type: common, series, HV, LV and tertiary as appropriate).  The indicator shall have a load - temperature characteristic approximately the same as the hottest part of the windings.  The primary current transformer for operating the indicator shall be built into the main transformer tank on the bushings.  Information shall be included in the maintenance instructions in the form of either a graph or table showing the relationship between current injected into the heater coil and the corresponding temperature reading.

The indicators shall be provided with two sets of alarm/trip contacts, adjustable to close at any temperature between 45oC and 150oC such adjustment being possible without dismantling the instrument.  Where supplementary forced cooling is specified, two additional set of contacts shall be provided on the winding temperature indicators, for automatic start of the cooling fans in two stages.  The differential between "switch on" and "switch off" temperatures must also be variable in the range 10°C to 15°C.

The instrument and set points shall have an accuracy of ±1% of full-scale deflection and the indicated temperature must reflect the hot spot temperature to within 3±oC under all operating conditions.  Test links are to be provided for calibration purposes.

One temperature indicator of the capillary type for measurement of the top oil temperature shall be provided for each transformer. The capillary should be protected by steel wire armouring from the indicator to the point of entry into the thermal pocket. The capillary shall have extra protection against heavy objects, at point of entry into the thermal pocket (to prevent gauge damage during transformer maintenance by personnel stepping on them at this bend).

#### Alarm and Trip Contacts

All alarm contacts shall have ample inductive making and breaking at the specified alarm and tripping voltage.

Any auxiliary relays associated with the trip circuits shall be DC operated and suitable for the specified alarm and tripping voltage.

Alarm and trip contacts shall be provided with independent potential free contact.

#### Drain, Filter and Sampling Valves

##### General

All valves shall be attached by bolted-on flanges and shall not be screwed or welded to the tank.  Drain valves or isolating valves larger than 101.6 mm (4"B.S.P.) and of the double-flanged gate-type construction may have bodies of cast iron or cast steel.  All valves shall be opened by turning counterclockwise when facing the hand wheel.

Every valve shall be provided with an indicator to clearly show the position of the valve.

Means shall be provided for padlocking the valves in their open and closed position.

All valves shall be suitable for operation in conjunction with transformer oil as specified in IEC Publication 296 at temperatures up to 115oC.

##### Drain Valves

Drain valves shall be of suitable dimensions in relation to the volume of oil in the transformer tank and coolers.

##### Oil Sampling Valves

Oil sampling valves shall be of the screwed globe type; handle or gate valves located to permit sampling of oil from the extreme bottom of the transformer tank and the bottom of the tap changer compartment.

##### Filtration Connections

Filtration connections, which shall have flanges drilled to BS 4504 Table 6, for 50.8 mm (2") valves, or screwed 50.8 mm (2"B.S.P.) female, shall be as follows:

a.	A valve at the top and bottom of the main tank.  The drain valve of the main tank may be used for this purpose if the size is described above.

b.	The oil conservator drain valve located within easy reach of the ground, by means of a pipe extension, if necessary, shall be suitable for a filter connection.

##### Valve Entries

All valve entries shall be blanked off with gasketed bolted-on plates or plugs.

#### Rating and Diagram Plates

Rating and diagram plates shall be to IEC 60076, BS 171 or equivalent specification stamped or embossed on brass, or stainless steel.  They shall show the Employer's Order Number and shall have a blank space for the Employer's Serial Number.  The diagram plate shall show the internal connections and the voltage vector relationship of the windings in addition to a plan view of the transformer giving the correct physical relationship of the terminals and indication of winding material.

Where applicable, rating or diagram plates shall show locations, ratio, rating and accuracy class of current transformer.  Rating and diagram plates shall be approved by the Project Manager.

#### Skid Under base

Skid under base, where specified, shall be reinforced to permit moving the transformer in direction perpendicular to the base.  Hauling eyes shall be provided on the under base.

#### Wheels

Wheels, where specified, shall be plain, flanged uni-directional or bi-directional, whichever is specified in Scope of Works and Supply.

Wheels fitted to transformer shall be provided with grease nipples or cups for lubricating the wheel bearings.

Bi-directional wheels shall be designed so that it is possible to change the direction of the wheels without removing them from the transformer, and provision shall be made for locking the wheels parallel or at right angles to the major axis.  Grease nipples or cups shall be provided for lubricating the swivel bearings.  The wheel gauge will be provided by the Employer.

### VOLTAGE CONTROL EQUIPMENT

#### On-Load Tap Changers

##### General

The transformer's voltage control equipment shall be of the tap changing type for varying its effective transformation ratio whilst the transformer is on load and without producing phase displacement.  The on-load tap changing equipment shall comply with BS 4571, IEC 60214, or other approved and equivalent standards.  The tapping shall be arranged in the electrical centre of the higher winding.

The tap changing equipment shall be of the 3-phase resistor type, preferably with combined diverter and selector switches and shall be designed so that it will not be possible for the main transformer winding to be open circuited or for a portion thereof to be short circuited, except through a transition impedance. Only MR type Germany make tap changers shall be acceptable.

Generation from any type of control shall cause one tap movement only.

The equipment shall be so arranged as to ensure that when a tap change has commenced, it shall be completed independently of the operations of the control relays or switches.  Failure of the auxiliary supply during a tap change operation must not inhibit the independent completion of the tap change operation.

An auxiliary supply of 380/230 volts, 50 Hz, 3-phase 4-wire A.C. will be available for operating the tap changing equipment and all its accessories.  All equipment shall operate correctly at any voltage between the limits of 85% and 115% of nominal value.

Tap changing equipment shall be capable of carrying the same currents due to external short-circuit as the transformer windings and shall withstand the impulse and dielectric tests of the associated winding.  The tap changer connection and switches shall be capable of handling continuously currents at least 20% above the highest operating current in order not to limit overloading.

It shall not be possible for the insulating oil in those compartments which contain contacts for making or breaking current to mix with the oil in the main transformer tank or with the oil in compartments containing contacts not used for making or breaking current.  This requirement shall not apply where mercury switches are used to make and break current.

Drop-down tanks which necessitate the provision of pits in the foundations are not acceptable.

Where it is necessary to remove parts, or the whole of the on-load tap-changer for transport purpose, it shall be possible to complete erection on site with the transformer windings covered with oil.

##### Construction

The number of the tap in use shall be indicated mechanically at the transformer and electrically at the local control room panel.  A potentiometer shall be provided for the local control room panel indication.  The potentiometer switch shall be of the make-before-break type.

The tap-changing switches and mechanism shall be mounted in an easily accessible cabinet on the transformer tank and shall be supported from the main tank or its base.

The oil compartment for the tap changing switch shall be fitted with its own over-pressure device and Conservator; the conservator shall be dimensioned such that the expansion rates as specified in 8.2 can be met, together with suitable oil level indication and drain valves.

All switches forming part of the main tap-changing apparatus shall be oil immersed and readily accessible and it shall be possible to examine or repair such apparatus without lowering the oil level in the main transformer tank.

Each compartment in which the oil level is not maintained from the conservator shall be provided with an oil gauge of approved design.

Limit switches shall be provided to prevent the over-running of the mechanism and shall be connected directly in the circuit of the operating motor.  In addition, mechanical stops or other approved devices shall be provided to prevent the overrunning of the mechanism under any condition. The tap changer should be so designed that a mechanical device, through necessary relays, should trip the transformer if the tap changer is stuck in an intermediate position.

Approved means shall be provided to protect the motor and control circuits.

The whole tap-changing equipment shall be of robust design and capable of giving satisfactory service without undue maintenance under the conditions to be met in service, including frequent operation.

An externally visible mechanical recorder shall be fitted to the mechanism to indicate the number of tap-change operations completed by the equipment.  At least five digits must be provided.  No provision for resetting the counter is to be made.

##### Operation

330/132/33/11kV Transformers:

The tap changer shall be operated in the following modes:

-	Directly on the motor control cabinet in the switchyard (local control)

-	From the control room in the substation (remote control)

-	From the National Control Centre [NCC] (supervisory control).

A blocking switch shall be provided on the motor control cabinet with two positions: local/remote (supervisory).

When the switch is in local position, control can only take place from the control cabinet on the transformer and vice versa for the other position.

All the necessary equipment like relays, contactors, etc. shall be provided, wired up to terminal blocks to facilitate the functions outlined above.  A potentiometer switch of the make before break type shall be provided for remote and supervisory tap position.  The numbers shall range from 1 upwards, the lowest number representing a tapping position corresponding to the maximum number of high voltage winding turns, i.e., the highest plus-percent positions.  The lowest minus-percent position shall be represented by the highest number.

Unless specifically asked for in this document, all equipment for control and indication required in the control room shall be provided by the supplier of the control room equipment.

Facilities shall also be provided to prepare the transformer for parallel operation with one or more transformers on the master - slave principle.  An out-of-step device shall be provided and arranged to prevent further tap changing after a definite time interval when the transformer on parallel control is one tap out of step.

Alarms and Trip Signal

The following alarms shall be provided, wired up to terminal blocks in the transformer cabinet:

-	Tap changer not operating.

-	Transformer on parallel control are out of step.

-	Partial or complete failure of the voltage transformer supply to the voltage

regulating relay.  This alarm shall be inoperative when the transformer is

on non-automatic control.

-	Fan failure, alarm.

-	Gas relay transformer, alarm.

-	Gas relay transformer, trip.

-	Protective relay OLTC, trip.

-	Oil gauge low level transformer, alarm.

Oil gauge low level OLTC, alarm.

-	Pressure relief device transformer operated, trip.

-	Pressure relief device OLTC operated, trip.

-	Top oil temperature high, alarm.

-	Top oil temperature critical, trip.

-	Winding temperature high, alarm (on both sides).

-	Winding temperature critical, trip (on both sides).

-	Tap changer AC supply fail

-	Tap changer DC supply fail

-	Group 1 fans, supply fail

-	Group 2 fans, supply fail

#### Local Tap Changer Control Cubicles and Wiring

Each power transformer equipped for on-load tap changing shall be provided with a weatherproof local mechanism/control cubicle for control of the tap changer.  The cubicle shall preferably be mounted on the side of the transformer tank but for larger units, a separate free-standing marshalling kiosk would be considered.

A separate cabinet, also preferably mounted on the transformer shall be provided to facilitate connection of all wiring required for indication, control, alarm and trip signals in addition to the control of the cooling equipment.

All cubicles and cabinets shall be complete with the requisite front panels.  Bidder shall provide in their Bid a complete list of all control, alarm, protection and indication facilities and equipment included in the Bid price each item to be identified with its function.

Outdoor cubicles, cabinets and enclosed compartments shall be adequately ventilated to prevent condensation.  All contactor or relay coils and other susceptible parts shall be suitably protected against corrosion.

All control cubicles and cabinets shall be identical in respect of all secondary control circuits and equipment.  All cubicles shall be equipped with removable gland plates, and terminals to approval.

A voltmeter, suitably calibrated and indicating the secondary voltage shall be fitted on the panel of each remote-control cubicle.

All suppliers wiring shall be carried out in PVC or similar insulated wire supported clear of the panel surface and identified by ferrules at all terminations; in addition, colour identification may be used.  No ferrule number shall appear on more than one circuit and the ferrule number shall change at every break in the circuit, i.e., all switches, coils contacts, etc.  Particular attention shall be paid to ensuring that ferrule numbers conform to those on the wiring diagram.

Terminals should be arranged so that terminations of any incoming wiring provided at site under separate contract are directly visible.

Terminal boards shall be placed in accessible positions adjacent to the incoming cable entries.

Terminations shall be grouped according to their functions and labels shall be provided on the fixed portion of the terminal boards showing the functions of the groups.  All terminal boards shall have a minimum of 20% spare terminals.

All incoming and outgoing connections shall be terminated at a terminal block.  Direct termination on to auxiliary switches will not be accepted.

All indicating analogue instruments shall be flush mounting and the dials shall preferably be not less than 100 mm diameter if circular or, if rectangular have no side less than 100 mm.

Low energy heaters shall be provided in each cubicle and cabinet to prevent condensation and the internal design shall be such as to permit free circulation of air without the ingress of dust or vermin; a manual heater control switch shall be provided inside the cubicle.

Doors shall be provided with integral handles and shall have provision for padlocking.

A stay shall be provided for holding the door open without impeding access to the cubicle while work is being done in the cubicle.

An easily removable undrilled gland plate shall be supplied.

An indelible chart showing lubrication points and specifying recommended lubricants and frequency of application shall be provided in all mechanism cubicles.

One set of drawings for the tap changer control shall be placed in the tap changer local control cubicle.

### COOLING

#### Definitions

The types of cooling shall be designated by the IEC lettering symbols:

a.	Natural Air Circulation (ONAN)

By radiators directly attached to the tank.

b.	Forced Air Circulation (ONAF)

By fan cooled radiators attached directly to the tank.

#### Declaration of Ratings

The Bidder shall declare in the Schedule of Technical Guarantees the rated power available under the operating conditions ONAN or ONAF and the ratings shall be indicated on the rating plate. The rating plate shall also indicate the corresponding loss in transformer capacity in the event of loss of one cooling bank.

#### Radiators

Where detachable radiators are fitted, suitable valves, with blanking plates shall be provided at the inlet and outlet of each radiator so that it may be removed without draining oil from the tank.  Inlet and outlet valve "OPEN" and "CLOSED" positions shall be clearly marked.  The valves shall be readily accessible and easy to operate.  Lifting facilities, a drain cock and an air release vent shall be provided on each radiator.

Radiators shall be designed so that it is possible for the whole of the cooling surface to be cleaned and, if necessary, subsequently painted by brushing and spraying.  They shall also be designed so that they shall withstand dry-out vacuum without distortion or causing leakage of hot oil.

#### Supplementary Cooling Plant

Where supplementary cooling is specified for transformer the following requirements shall apply:

##### Natural cooling with additional Forced-Air Cooling ONAN/ONAF

Where mixed cooling is specified the natural (ONAN) rating shall generally not be less than 80% of the total specified forced-cooling capacity.

The forced-cooling equipment shall be designed to operate automatically from winding-temperature relay control at predetermined temperatures recommended by the Contractor.  The equipment shall be designed to start in 2 stages at preset temperatures.

Indicate setting values are as follows:

On	Off

Stage 1	65°C	50°C

Stage 2	75°C	60°C

The cooler arrangement must allow for the maintenance or failure of any one fan or radiator without losing more than 20% of the total cooling capacity.

##### Fans

All fans shall operate as a unit.  Fan blades and fan ducting shall be of aluminium alloy, stainless steel, galvanised steel, or other corrosion-resistant metal and shall be designed to keep noise and vibration to a minimum.  All fans shall be provided with galvanised wire-mesh guards.  It shall be possible to remove fan assemblies complete without dismantling other equipment.

The transformer nameplate diagram should show the corresponding reduction in transformer capacity in the event of loss of one bank of cooler fans.

##### Cooler Control Equipment

All the necessary automatic control, motor contactors, protective devices and switches for the forced-cooling equipment shall be assembled in a dust-proof, weatherproof and vermin-proof cabinet preferably mounted on the transformer.

The cooler control equipment shall include:

-	An isolating switch rated to carry and break full-load current for each

group of fan and pump motors.

-	A "Cooler Auto" - "Cooler-Manual" changeover switch.

-	Magnetic contactor for each group of fan motors.  Contactor coil leads

shall be wired to the terminal board.

-	Overload and single-phasing relays for each motor with a set of normally

closed contacts for alarm purposes.

-	Fuses, links and terminal boards to approval to make a complete

assembly.

One set of drawings for the cooling control shall be placed in the local cooler control cubicle.

### SPARES

The Contractor shall supply all spares specified in Scope of Works and Supply and these shall be included in the Bid.  In addition, Bidders are requested to state their recommendations at the time of Biding for extra spares bearing in mind that the transformer shall be in continuous uninterrupted operation for 25 years.

Spares shall be delivered with the associated equipment and, in order that spares may be placed on order at short notice, full details including Catalogue and/or spare part numbers of all spares should be supplied with Bid.

Spares shall be priced item-wise.

Spares shall be strictly interchangeable with the corresponding parts supplied with the original equipment.  Spares for identical transformers shall be strictly interchangeable and to the highest extent possible also between the different transformers.

Each spare part shall be labelled with the following:

-	The number of the Authority Order on which the part was supplied.

-	The Item No. on the Order which specified the part.

-	The serial number of the equipment for which the part may be used.

-	The part numbers.

All spares must be packed to be suitable for indefinite storage and special precautions must be taken to ensure that insulating materials included in the spares do not deteriorate during storage.

Cases in which spares are packed shall be indelibly marked with the applicable Authority order numbers.

Bidders must positively state how long they anticipate that replacement spares will be available in stock.

### OIL

The oil shall be of the uninhibited mineral type and comply to BS 148, IEC 60296 or equivalent standard. The Contractor shall demonstrate that the transformer oil shall not change its chemical composition and characteristics during continuous full load operation, in such a way that the resultant chemicals or properties accelerate or trigger insulation failure beyond what is normally and conventionally expected.

Oil shall preferably be supplied in bulk from within Zambia and dried and cleaned on site. If oil is provided in drums, these shall have a volume of approximately 200l and be full.  A separate price shall be quoted for transformer oil. The Contractor shall positively submit the names of the proposed supplier and manufacture of transformer oil for ZESCO’s approval. No transformer oil shall be accepted before suppliers and manufacturers are approved.

### INSPECTION AND TESTS

#### Inspection/Witnessing of Tests

ZESCO's representative, the Project Manager, reserves the right to inspect the transformer at any stage of manufacture or to be present at any of the tests specified.  Such inspection shall not relieve the Contractor of his responsibility for meeting all the requirements of the specification, and it shall not prevent subsequent rejection if such material or equipment is later found to be defective.

The Contractor shall in good time inform when testing will take place and shall give the Employer/Project Manager not less than several weeks’ notice in advance.  No transformer shall be tanked or dispatched from the Contractor's works without approval of ZESCO's Representative.  Based on the Contractor's manufacturing program, factory inspection will take place as required by the Employer/Project Manager.

#### Bushing Tests

Note shall be taken that the bushings shall have adequate insulation level for operating at 1500m above sea level. It is not required to perform separate bushing tests if the Contractor selects bushings which have insulation levels compensated for the altitude.  Nevertheless, the Contractor shall submit for approval test records and data for all bushings.  These records shall show the test performed on the bushings including but not necessarily restricted to the following tests:

-	Standard, one minute, 50 Hz dry withstand tests for all bushings.

-	Type test of impulse withstand voltage.

All recorded test figures shall be given with the bushings serial number.

-	For the 330 kV and 132 kV bushings including any spare bushings:

Internal pressure and terminal cap pressure.  Power factor and

capacitance measurements

-	Power factor measurement

-	Capacitance measurements between conductor and test tap and between

the tap and earth.

#### Transformer Tests

##### Routine Tests

Routine tests as far as applicable shall be carried out according the IEC standard  60076.

The following routine tests shall be applied to all transformer:

-	Resistance measurements of all windings for all tap positions.

-	Ratio tests for all tap positions and vector relationship tests.

-	Measurement of no-load losses and currents.

-	Measurements of impedance voltages (at maximum, principal and

minimum tap), short circuit impedances and load losses.  Load losses shall be measured at both rated currents when ONAN and ONAF cooling are specified.

-	Determination of efficiencies at 50%, 75%, 100% and 120% load at maximum temperature of the winding and 0.8 power factor lagging and unity power factor for all ratings (ONAN, ONAF ratings).

-	Zero sequence impedance measurement.

-	Induced voltage and separate source voltage withstand power frequency,

dielectric tests on all windings on all phases including neutral points.

-	Full wave impulse withstand tests.  The transformer shall be subjected to a complete series of tests.  Such tests shall be applied to the HV winding line terminal of each phase as well as to the neutral points.

-	Tests on on-load tap changers.

-	Routine tests on all transformer accessories such as motors, contactors

wiring, etc.

-		Partial discharge measurements (corona testing) during the power frequency dielectric tests.  The test procedures shall be as described in NEMA Publications 107, 1964 or other approved method to be agreed between the Contractor and the Project Manager.

-	Measurements of capacity between the windings and each winding and ground.

-	Oil leakage test.  The complete oil filled transformer with bushings and radiators fitted and any other attachment normally in contact with oil shall be tested at a positive pressure measured at the tank bottom of twice the column of oil in the transformer when the transformer is cold, but in any case, not less than 70 kPa.  Alternatively, the radiators may be tested separately with the same pressure.  The test period shall be not less than 12 hours.

-	Core insulation test, 2 kV, 50 Hz for one minute.

##### Type Tests

The following type tests shall be carried out on one transformer of each type:

-	Temperature rise test.  Details of the test procedure shall be agreed between Contractor and Project Manager before testing commences.

-	Noise measurements.

-	Chopped wave impulse test.  The test shall be carried out in conjunction

with the full wave test as described in IEC 60076-4.

-	Vacuum test.  The transformer tank and radiators filled with oil shall be subjected to a vacuum test to comply with Clause 4.6.  Bushings need not be fitted, and the radiators and conservator may be tested as separate units.

Tests on 330 kV transformer only

-	Switching impulse test according to method 2 in IEC 60076-4.

##### Site Tests

Testing at site by the Contractor shall be carried out to prove that the transformer in all respects complies with provisions and guarantees set forth in the Contract.

Tests shall include but not be limited to the following:

-	Dielectric oil tests.

-	Insulation dryness by an agreed method.

-	Electrical and functional control of voltage control equipment and cooling

system.

-	Core to tank insulation.

#### Test Certificates

Two copies of test certificates showing the results of all routine and type tests performed shall be supplied to the Project Manager PRIOR to the despatch of the transformer from the Contractor's works.

All test certificates shall be in English.

### ERECTION

Erection shall be carried out by the Contractor under supervision by the Project Manager or his representative.  The Contractor shall ascertain that the transformer has been erected according to the Terms of Contract before commissioning takes place.

The Contractor shall be fully responsible for the quality and timing of the works.  The Contractor shall ensure the safety of every person employed or working at the site and this shall include routine inspection of all temporary installations and portable equipment.

All heavy erection equipment like lifting cranes and other equipment to be used for erection purpose shall be provided by the Contractor.  The Contractor shall also provide all special equipment for erection and testing purpose.  Such equipment shall be listed in the Bid.

### DELIVERY AND TRANSPORT

The dimensions of the transformer shall be such that when packed for transport, they will comply with the requirements of the South African Railways, Mozambique Railways, National Railways of Zimbabwe and National Railways of Zambia with respect to systems loading and clearance gauges. Or alternatively the transport must be in accordance with the rules for road transport in the respective countries. If any special investigations, permits or arrangements are necessary for the road transport these has to be arranged for by the Contractor. Cost for such shall be included in the price.

Shipment of transformers in any position other than the upright one is not permissible.

All shafts, bearings and machined surfaces exposed for transport to the site shall be given a temporary protective coating to prevent corrosion.

If it is necessary to remove bushings or radiators for transport blanking-off plates and a spare set of gaskets shall be provided.

Where the supply of oil is included in the contract, and transport weight limitations permit, the transformer shall preferably be transported with sufficient oil to cover the core and windings.  The tank shall be sealed for transport to prevent all breathing.  The remainder of the oil to be supplied separately at the time of delivery shall be in 200l drums.

Alternatively, where the above method is not applicable or practicable, the transformer shall be transported filled with dry nitrogen under slight positive pressure.  This pressure and the temperature at the time of filling shall be communicated to the Project Manager and a pressure gauge suitably protected is to be fitted to each transformer to facilitate inspection of the gas pressure on arrival at site.  Every precaution shall be taken to ensure that the transformer arrive at site in a satisfactory condition so that after oil filling, they may be put into service without the necessity for further drying out.  Should the positive gas pressure disappear during transport and the transformer allowed to breathe, additional drying out at site if required shall be the responsibility of the Contractor.

All accessories and spares which are shipped separately must be clearly marked for identification with the transformer for which they are intended.  All pipework and valves shall have further markings showing the correct points of assembly which shall also be shown on the assembly drawing to be supplied.

Full details must be supplied on methods of drying out the windings, if found necessary, on arrival and on the method to be adopted for oil filling and oil purification on site.  Any special apparatus required for oil filling must be supplied as part of this contract.

Full details of the proposed methods of transport shall be submitted for approval.

### EVALUATION OF LOSSES

#### Guaranteed Output and Losses, Liquidated Damages

Failure to meet the guaranteed outputs and losses with be dealt with as follows:

##### Transformer Output

If the guaranteed continuous output at rated voltage of any transformer has to be reduced below the guaranteed value in order to maintain the temperature rises of any part of the transformer within the guaranteed limits, liquidated damages shall be paid at the rate of USD 4000 per kVA.

##### Transformer Losses

If the total transformer losses of any transformer, as determined by these, without any tolerances, at rated voltage, frequency and 100% rated kVA (on principal tapping) exceed the guaranteed total losses, the excess in losses shall be capitalised at the rates stated in 8.12.2 below and the resulting amount shall be paid as liquidated damages.

The payment on account of failure of one or more transformer to meet the guaranteed output and guaranteed losses shall be applied individually and shall therefore be understood to be cumulative.

##### Rejection Limits

Should any transformer fail to meet the guaranteed output by more than 5% (five per cent) or the total losses should exceed the total guaranteed losses by more that 1/5 (one fifth), and should the Contractor fail within a reasonable time to modify the transformer to increase the output and/or reduce the losses sufficiently, the Purchaser shall have the option to reject the transformer.

#### Evaluation of Losses

Transformer losses will be evaluated based on the following:

Reference to ITB 25.3(d) (i) (ii) and corresponding paragraph in Bid Data Sheet. In the Bid Evaluation, particular attention will be executed to the functional guarantees related to:

Calculated load loss (also referred to as copper losses) and no-load losses (also referred to as iron losses) shall be given in the Bid. The load loss and the no load loss shall be measured as routine tests.

For bid evaluation of the transformers, the lowest offered losses in kW will be used as a reference. The load losses for the transformers will be evaluated at the rate of USD 2000/kW (excess) per transformer and added to the bid price of the particular bidder. The excess in no load losses will correspondingly be evaluated at the rate of USD 4000/kW per transformer and added to the bid price of the particular bidder.

The losses in kW are the guaranteed values in the Technical Specifications (Technical Particulars and Guarantees section of the bid document).  These same figures per kW are to be used in the application of liquidated damages for non-compliance to guaranteed values for full load and no-load losses of the successful bidder.

Load losses will be evaluated based on the ONAN rating for transformers with combined ONAN/ONAF cooling.

## AUXILIARY SUPPLY

### General

The Contractor shall dimension the system with due consideration to the present and future load and cables shall be dimensioned for a maximum voltage drop of 5 % during full load.  The Contractor shall also select components assuring selectivity through the plant and document this selectivity through a selectivity plan.

The Contractor shall supply all spares specified in Scope of Works and Supply and these shall be included in the Bid.  In addition, Bidders are requested to state their recommendations at the time of Biding for extra spares bearing in mind that the auxiliary supply system (11kV, 33kV and 400V) is critical to the main operations and shall be in continuous uninterrupted operation for 25 years.

Spares shall be delivered with the associated equipment and, in order that spares may be placed on order at short notice, full details including Catalogue and/or spare part numbers of all spares should be supplied with Bid.

### Switchboards and Panels

The switchboards and panels shall be designed, constructed and tested in accordance with IEC 60439: Low voltage Switchgear and Control gear Assemblies.

The boards and panels shall be self-ventilated.  No ventilating fans shall be used.

Permissible temperature rise shall not be exceeded even when the free space available for future feeders is mounted with feeder equipment and loaded with rated current.

The covers (outside covers and doors, including hinges and locks) shall safely withstand the overpressure caused by short circuit currents and shall protect personnel against injury.

The main switchboards and the larger ones of the sub distributions shall be of the floor mounted prefabricated metal enclosed type, with separate compartments for each feeder, etc.  Small sub distributions may be of the wall mounted steel sheet or cast metal type.

All boards and panels shall be designed for easy access to the equipment, cable terminals, etc.  during erection, maintenance, disassembly and extensions.

In addition to the required number of outgoing circuits, one more of each rating employed (but not less than five altogether) shall be fully equipped ready for connection of future circuits.  Furthermore, each board and panel shall have at least 20% free space available for future extensions.

The main switchboard shall be designed so that additional panels can be added in the future (i.e. possibilities for extending the busbars).

Operating handles, operating switches and push buttons, signaling lamps, position indicators, instruments, etc., shall be placed on the fronts. Relays which are not incorporated on the circuit breakers shall be placed in separated compartments, metal shielded from the current carrying parts.

The busbars shall be of copper and shall have three phases and neutral.  A grounding bar of copper shall also be provided, and a grounding conductor connection shall be brought to each feeder compartment, where the feeder grounding conductor can be connected to it.

#### Circuit Breakers

In general, circuit breakers shall be used for all feeders and distribution circuits.

Miniature circuit breakers, MCB's, may be used on small circuits.

Fuses may be used in exceptional cases such as on very light loaded circuits, or in combination with small contactors and where the use of fuses is justified for the purpose of selectivity.

In the design of the distribution systems and in the selection of circuit breakers, MCB's, fuses and protection relays due attention shall be paid to the selectivity of breaker tripping at overloads and at short circuits.

Full selectivity shall be achieved, only the feeder or circuit which has an overload or short circuit shall trip.

MCB's without delay function shall be used only as the last breaker of a circuit.  Selectivity between MCB's and fuses shall be proved, with ample margin.

The circuit breakers shall be manually operated, except for the breakers in the feeders from the auxiliary transformer which shall be electrically operated.

All circuit breakers and MCB's shall have three phase overload and short circuit protection to be provided as a part of the breaker assembly or provided separately as for the transformer circuit breaker (in this case separate current transformers shall be included).  The ratings of the overload and the short circuit protections shall be selected according to the current rating of the cable or circuit to be protected, and in accordance with the requirements of the selectivity as stated above. The ratings of the overload and the short circuit protections shall cover the whole of range operations up to the maximum rating of the apparatus. The rating of settings on the overloads and circuit breakers shall not limit the operations of the equipment being protected.

Operating coils of circuit breakers, which are not continuously rated shall be suitably and economically protected from unexpected prolonged energization.

#### Current Transformers

The current transformers shall have synthetic resin insulation or equivalent dry insulation.

The cores for measuring purposes of current transformers shall have accuracy class 1 and instrument security factor less than or equal to 5.  The cores for protection shall have accuracy class 5P and accuracy limit factor greater than or equal to 20.

Power frequency test voltages, 1 minute:

Primaries			3 kV

Secondaries			2 kV

#### Instruments and Relays

The instruments shall be 96 x 96 mm square pattern with (at least) 900 pointer deflection.

Instruments shall be of the three-element type, for unbalanced three phase load and loaded neutral conductor.

The relays shall preferably be of the programmable numerical type.

The instruments and relays shall, as far as applicable, be of the same make and type as those of the other parts of the plant.

### DC SUPPLY

#### General

New DC supply systems are required for both new and existing substations.

This chapter covers the technical requirements of the batteries and battery chargers, the main DC switchboards and the sub distribution boards and panels for the DC auxiliary supply of the new plants.

110 / 220 V DC shall be used for the main circuits of the control and protection and for DC motors, unless otherwise stated in Scope of Works and Supply and when 110 V DC is already used in the existing station.

48 V DC has been foreseen as supply voltage for the communication equipment and SCADA facilities. The figure below illustrates the main principles of the DC system.

Figure -1 - DC Distribution

The 110V DC shall comprise of two independent systems i.e. double batteries and chargers allowing one system to carry all loads while the other system is out of service or when boost charging one battery.

Under normal operational conditions the two systems shall each carry 50% of the load.  Trip 1 circuits and trip 2 circuits shall be connected to separate systems. The 48 V DC system for communication shall be fed by two redundant DC/DC converters, 1500 W output, each capable of carrying the total load

All boards and panels shall be supplied with the necessary internal wiring.  Battery connections and cabling in the battery rooms shall also be included.

Miniature circuit breakers and DC distributions for control, protection, etc., and which are placed on the control, measuring and protection boards shall be included in those boards. Miniature circuit breakers shall have auxiliary contact for alarming purposes.

All instruments and protection relays on the rectifiers and on the boards and panels shall be included.

Starters, contactors and protection for motors shall be included whenever such equipment is not provided as part of the motor supply.

The Contractor shall calculate and determine the battery capacities, the power ratings of the chargers, the number of sub distribution boards, the number and size of circuits, etc., to suit the requirements of the equipment to be installed, but also considering the future extensions as indicated on the drawings.

The provisions of the clause 9.2 above, Switchboards and Panels, shall apply for the DC boards.  Reference should be made to these provisions.

The following modifications are applicable:

(1)	Circuit breakers on the main DC switchboards which are rated 50 A and higher shall be withdrawable.

(2)	The DC busbars shall have two poles.  The bars and the connection conductors to the breakers should be insulated.

The provisions of 9.2.1 Circuit Breakers, shall apply also for the DC breakers.  Reference should be made to these provisions.

The following modifications and additions are applicable:

(1)	All circuit breakers shall be manually operated.

(2)	The breakers shall be two poles, and with thermal overload and magnetic

short circuit protection in both poles.

(3)	All circuit breakers, miniature circuit breakers, switches, contactors, fuses, etc., shall be of a type specifically designated for the use on DC, and the dynamic current and the making and breaking capacities shall be ample for the short circuit power of the batteries.

(4)	Due attention shall be paid to the selectivity of breaker tripping.

(5)	All circuit breakers, miniature circuit breakers, switches and contactors

shall have an alarm contact.

(6)	On circuits protected by fuses an undervoltage relay with alarm contact shall be provided.

The provisions of 15.2.3 above, instruments and relays, shall apply wherever applicable.  Reference should be made to these provisions.

In addition, each main DC switchboard shall be provided with a voltage monitoring device with alarm contacts and signal lamps, one lamp for each type of fault.  The device shall monitor maximum and minimum voltages as well as ground faults on both poles.

#### Batteries

The number of cells shall be selected so that the voltage of the battery does not exceed 110% of the rated voltage during float charging.

The capacities of the batteries shall be selected to permit a 10-hour service without AC power with DC loads as specified below.  At the end of this period the voltage of the DC networks (measured on the busbars of the main distributions) shall be at least 90% of the rated voltage with the batteries being loaded as specified.

The 110 V batteries shall be loaded with the switchyard load. The 48 V battery shall supply the telephone exchange, the Optic fibre equipment, and the SCADA equipment. The Contractor must recalculate these loads to finalise the capacity.

Alarms shall be provided for battery faults. The batteries shall be of the lead acid type.

Each cell shall have an individual container of clear plastic (so that the acid level, the plates and the bottom of the container are clearly visible).  The container shall be completely closed and be provided with an acid spray preventing vent plug.  Each group of four containers shall stand in a plastic basin with sufficient volume for collecting all acid from one of the four cells in case of a leakage.  The polarity of the cells, and of the complete battery, shall be engraved and easily legible.

Each battery assembly shall be complete with wood bases, covered by a double coat of varnish resistant to sulphuric acid.

Bolted insulated interconnections between the cells shall be included.

In each substation where batteries are installed or replaced the following should be included:

-	one set of water distiller equipment

-	a explosion proof ventilation fan in each battery room

#### Chargers

The rated current of the battery chargers shall be selected to allow for recharging a fully discharged battery in 5 hours, in addition to simultaneously supplying the DC load.

In addition, the chargers shall comply with the following technical data and requirements:

Power supply	:			380 V AC three phase or 230 V AC single phase

Output voltage adjustable between:	110 V +/ 15% resp.  48 V +/ 15%

Output rated current:                      	at least 100A DC

Stability of the output voltage:		less than ±1% for the maximum input voltage and frequency variations, and from 1% to 95% of rated output current.

Maximum deviation of the current	:	+/- 2% of rated current.

Limitation:

Ripple of output voltage

- without the battery connected:	less than 4% peak peak of the rated output voltage.

- with battery connected:		less than 1% peak-peak of the rated output voltage.

Dry type transformers and solid state (thyristor or transistor) rectifiers shall be used throughout.

The chargers shall be completely equipped for a fully automatic and controlled charging and float charging of the batteries and shall be of a constant voltage type with current limiting device. The change of operation of the charger from boost mode to float and vice versa should be automatic.

Each of the charges for the 110 V batteries shall be rated to maintain normal charging and float-charging of both batteries.

By means of an automatic change over switch the charger shall change from normal charging and float charging to boost charging of the battery.  After the boost charging, the charger shall switch back to float charging.

Each charger shall be complete with instruments, breakers and protection, including but not limited to:

(1)	Breakers and protection on AC and DC side, with alarm contacts

(2)	One V meter for the DC voltage

(3)	One V-meter for the AC voltage

(4)	One A meter for the DC current

(5)	One lamp indicating that the charger is charging

(6)	Alarms for "high volts", "low volts", "earth fault" and "fail"

The above devices shall be placed on the front of the charger cubicle and the alarms shall also be transferred to the National Control Centre.

#### Battery Conductors and Fuses

Conductors from the batteries to the fuse boxes shall be mounted short circuit and earth fault proof.  That is, the conductors shall be single pole insulated and in addition placed on insulators, separate for each pole.  All conductors shall be placed at minimum 5cm distance from each other, even at crossings.

The conductors shall lead through insulating pipes in the wall of the battery room to closed fuse boxes made of insulating material on the wall outside the battery room. For the 110 V DC system there shall be one box per pole. The wall holes shall be tightened against gas.

Conductor insulation, insulators and pipes shall be resistant to sulphuric acid.

#### 48 V supply with DC/DC Converters

In stations with two batteries the communication equipment shall be fed from the station battery by two independent and galvanic isolated DC/DC converters as shown in Figure -1. Each converter shall be able to take the full load continuous whereas in normal operation it shall only carry 50% of the load. Each converter shall be designed for highest reliability and be equipped with parallel modules satisfying the n-1 criteria. I.e. by failure of one module the converter shall still be able to supply the rated load.

## PROTECTION

### General

For the 330kV substations, transmission lines should be equipped with three separate, independent protection systems. For substations were no changes are done in the control systems and new substations, a new first main, second main and backup protection shall be installed. The 330kV transmission lines first main protection shall be differential, and the second main shall be distance protection. The backup shall be Overcurrent/Earth fault protection.

The relays to be installed for the protection of transmission lines, transformers and other equipment shall be of numerical type. The relays shall be of robust type, insensitive to changes of temperature, vibration, etc. Input from the measuring transformers shall be based on 5/1A, 110 V AC.

In a bid to improve the reliability, rapidity, selectivity, and success of the defense scheme in Zambia power system to prevent out-of-step conditions between or separation of the ZESCO intra and interconnected grids which can lead to grid collapse in Zambia, ZESCO has implemented the. Wide Area Monitoring, Protection And Control System (WAMPACS) supplied by NR Electric Co.

As a result, the Zambian power transmission system is protected from overloaded system conditions, sudden loss of generation, tie-line tripping, under frequency, over frequency, over voltage and blackout risk.

At the same time, the real-time readiness of the WAMPACS along with the target shedding plan, as well as the strategy readiness status are all monitored through by the Master Station through sub-master via fibre optic.

It is required that the new load centres be integrated into the WAMPACS system as executing stations (Consisting of a set of 1 PCS-992M(MU) and 0 -4 PCS-992S (SU) installed per substation)

for the data acquisition required by the sub-master substation for use in the line overload and generator tripping strategies.

The contractor will be required to supply, install and commission all equipment required at the executing station including all the equipment required for communication to the sub-master station as per the WAMPACS structure.

The Contractor shall endeavour to standardise the equipment by using as few different types of racks, modules, tripping relays, switches and other devices as possible.

The relays shall comply with the requirements of IEC 60255, IEC 61850 (the international standard for substation automation systems) and such national standards as may be appropriate in the country of manufacture.

### Relay Construction and Mounting

Constructional and mounting details of the protection relays shall satisfy the following requirements:

1.	All protection relays shall be enclosed in case.

The relays shall be of the modular, plugged type. The plug mechanism shall be such that when the relays or part of the relays which are connected to the current transformer circuits are pulled out, the circuits of the current transformers are automatically shunted. If a module is pulled out, the protection functions of the module will be out of work, but this shall not affect the operation of the other protection units, control system or the grid. Pulling out modules shall not lead to trip of circuit breakers.

2.	Each protection relay, or protection scheme shall be provided with an adequate number of output contacts of suitable rating to carry out the prescribed tripping functions and as may be necessary for the initiation of automatic reclosing or automatic switching control, etc.

The output contacts shall have a rating appropriate to the maximum possible duty, due account being taken of the range of voltage variation in the DC supply source of the associated circuit.

The Contractor shall also quote the maximum breaking capability of the trip output circuit (in mA) when associated with an inductive burden having a time constant of not less than 40 ms at a rated voltage of 110V DC.

3.		All protection relays shall be designed to withstand the high voltage interference which is normally experienced in high voltage switching stations.

4.		Each relay, or relay scheme shall be provided with an adequate number of indications in front of the individual protection relays for fault detection including identification of the faulted phase and faulted zone, etc. All trip and non-trip alarm shall be indicated.

Indication should preferably be LED’s. Any alarms shall be possible to reset without opening any protection case.

5.		The design of the relay schemes shall be based on the "fail-safe" principle.

6.		All tripping relays shall be of the heavy-duty type, and with rating suitable for existing circuit breakers.

Contacts on the tripping relay shall operate 5 milliseconds from the time at which the operating coil of the relay is first energised.

7.		To achieve a high degree of security in function, the protection system of each 330kV main component (lines, power transformers, etc.) shall consist of two separated protection sets, first main and second main where applicable.

The two protection sets shall be divided into two electrically and mechanically separate parts by means of:

•	Separated DC power supply

•	Separate current and voltage transformer cores if possible

•	Separated tripping devices

•	Separated cables

8.		All protection relays shall be self-supervisory. Alarm shall be given to remote and supervisory control system in case of an internal fault in the protection system.

9.		Cable connections between protection relays and telecommunication equipment to be included:

•	From First main / Second main distance protection relays to PLC equipment

### Commissioning and Routine Testing Facilities

Each relay protection shall have test facilities of a type enabling testing of the entire relay combination when the protected part is in service. Each functional relay scheme shall be so arranged that operation and calibration checks can be carried out when the associated primary circuits are in service and form part of the operational network.

Test facilities shall be provided at the front of the boards, and it should be possible to execute all tests without having to disturb any wiring.

Test leads and plugs which are necessary to carry out secondary injection tests on each type of relay scheme should be included for each substation.

All connection wiring terminals in the protection circuits for voltage and current measurement and all trip circuits should be of shorting/separating type including testing connections for testing of complete protection circuits.

### Relay Settings

The protection setting philosophy and policy will be provided by ZESCO as well as the system parameters required. ZESCO will in general determine all setting values of the protective relays supplied. However, the Contractor shall evaluate the settings proposed and suggest alterations or additions if found appropriate. The settings shall be applied to the equipment by the Contractor, prior to making all commissioning tests. It is required that ZESCO personnel be given on-the-job training on the protection system.

### Fault Clearing Time

The 330kV protection system shall have a fault clearing time of not more than 20 ms, 132kV 30ms and 40 ms for the 33kV voltage levels.

### Fault Recorder and Fault Locators

Fault recorders and fault locators should be integrated in the line protection relays and use the same input quantities as the main protection functions.

### Programming Tools

Necessary programming hardware and software tools and licences for maintenance and simple alteration work shall be supplied by the Contractor at the time of issue of the completion certificate. The contractor shall also provide a protection relays administration Laptop.

### Supervision

Protection relays should be self – supervised with a contact for annunciation. The relays should have provision for CT and CVT supervision.

### Training

The contractor shall provide training in protection and control for six (06) protection engineers at their suitable relay research and development institutes with costs covered by the contractor. The Contractor shall include in the program, training in setting, use of programming tools, fault finding and maintenance.

### Transmission Line Protection

#### Transmission Lines

Due consideration shall be given to the existing relays at remote line ends during protection system design. The following specifications shall apply for all the protection relays:

•	Logic Software based user programmable protection functions, opto inputs and output relays

- Monitoring

- Non-volatile memory for:

- Event recording

- Disturbance recording

- Fault location

- LCD display of real time measurands

- Tripping circuit supervision

- Communication

- IEC 61850 to interface all substation IEDs

- Front port for direct PC – relay administration

- Remote (from National Control Centre) and substation centralised administration of relays

- All relay interrogation hardware and software

•	AC Current inputs

- 1A and 5A

- Continuous withstand – 4 times the nominal value.

- 10 seconds withstand - 30 times the nominal value

- 1 second withstand – 100 times the nominal value.

•	AC Voltage inputs

- 110V AC nominal phase to phase input

- Operating voltage of 0 to 200V AC

- A continuous withstand of 2 times the nominal voltage.

- A short time (1 second) withstand of at least 3 times the nominal voltage.

•	Auxiliary Voltage

- Rated for DC

- AC: 50 to 250 V AC with a software selectable nominal value

- DC: 48 to 150 V DC with a software selectable nominal value

•	Frequency Operation range

- 50Hz will be used.

- Operation range of 45 to 60Hz for the 50Hz operation with a blocking function of used protection functions when the frequency is out of range.

•	Light Emitting Diodes (LEDs)

- At least 12 programmable front panel LEDs

•	Binary Inputs

- Optically coupled.

- DC inputs range for opto inputs shall be 48 to 150V DC with a software selectable nominal value.

•	Binary outputs contacts

- Make and carry at least 30A for 3 seconds for all out put contacts.

- Carry at least 10A continuously at 300V for all output contacts.

- Break at least 1200W inductive and resistive.

- Loaded contacts to perform not less 10,000 operations.

- Unloaded contacts to perform at least 10,000 operations.

- Relay healthy and watchdog contacts to be provided.

- A minimum of 36 programmable binary output contacts to be provided.

- Sub cycle operation time for all assigned protection functions

•	Terminal connections

- At least 4mm2 for the CT and VT input circuits

- At least 2.5mm2 for DC circuits

•	Electromagnetic compatibility

- IEC 60255-22/25 Standard will apply.

•	Insulation

- IEC 60255-5 Standard will apply.

•	Mechanical test

- IEC 60255-21-1,2,3 Standard will apply.

- First main Protection

Line differential protection equipped for optic fibre link communication between the two line ends with the following functions:

•	Differential protection

- At least three CT inputs with in-zone transformer function option.

- Phase segregated differential protection tripping.

- Automatic Switch to full scheme distance protection on communication fail by software logic

- Minimum of 4 selectable settings groups

•	Impedance protection

- Full scheme distance protection

- Power swing protection

- Pole slip protection

- Switch on to fault protection.

- Broken conductor check

•	Over current and Earth fault protection

- At least three stage directional/non directional over current and earth fault elements with carrier aided operation option

- Selectable IEC/IEEE operation characteristics for all elements

- Breaker failure

- Thermal overload protection

- Stub protection

•	Power protection

- Directional under/over active and reactive power protection

- Directional Rate of change of power protection

•	Voltage protection

- At least two stage over/under voltage protection

- At least two stage residual over voltage protection

- Over excitation protection

- Loss of voltage protection

•	Frequency protection

- At least 4 stage Over/under frequency protection

- Rate of change of frequency protection

•	Secondary systems supervision

- Current transformer supervision

- Voltage transformer supervision

•	Control and Synch check

- Reasonably large mimic LCD for bay switchgear position indication and control with at least 8 open/close control commands of bay switch gear.

- Manual close and auto-reclose breaker control with split frequency, differential voltage and voltage magnitude plus live line - live bus, live line - dead bus and dead line – live bus check on synchronizing.

- Second main Protection

A fully equipped line distance protection equipped for optic fibre communication between the two line ends with functions not limited to the following:

•	Impedance protection

- Full distance protection scheme.

- Power swing protection

- Pole slip protection

- Switch on to fault protection.

- Broken conductor check

- Minimum of four selectable settings groups

•	Over current and Earth fault protection

- At least three stage directional/non directional over current and earth fault elements with carrier aided operation option

- Selectable IEC/IEEE operation characteristics for all elements

- Breaker failure

- Thermal overload protection

- Stub protection

•	Power protection

- Directional under/overactive and reactive power protection

- Directional Rate of change of power protection

•	Voltage protection

- At least two stage over/under voltage protection

- At least two stage residual over voltage protection

- Over excitation protection

- Loss of voltage protection

•	Frequency protection

- At least 4 stage Over/under frequency protection

- Rate of change of frequency protection

•	Secondary systems supervision

- Current transformer supervision

- Voltage transformer supervision

•	Control and Synch check

- Reasonably large mimic LCD for bay switchgear position indication and control with at least 8 open/close control commands of bay switch gear.

- Manual close and auto-reclose breaker control with split frequency, differential voltage, and voltage magnitude plus live line - live bus, live line - dead bus and deadline – live bus check on synch.

### Transformer Protection

The transformer protection shall include a differential protection relay equipped with stabilizing for external faults and insensitive to in-rush. This is considered main transformer protection. HV and LV restricted earth fault protection relay which may be integrated with the differential protection. Neutral point earth fault protection shall be second harmonic restrained.

The following transformer protection signals shall be integrated in the protection and alarm system using auxiliary relays:

-	Oil level signals with at least two low-oil level alarm contacts.

-	Buchholz, gas operated signals (both for the transformer and the

tap-changer). The protection will have two output contacts, one for

alarm and one for tripping.

-	Over-temperature signals for winding hot spot and top oil. Two sets of alarm/trip contact adjustable to close at any temperature between 60°C and 140°C.

- 	Pressure relief device operated alarm and trip

-	Tap changer alarms.

-	Cooling system alarms

All the transformer integral alarms shall be integrated into the Transformer differential protection relay.

#### 330/132kV Transformers

The transformer protection shall be split in two independent classes of protection relays:

##### Main protection

Main differential protection relay shall include but not limited to the following functions:

•	Differential protection

- At least three winding differential protection.

- At least three winding restricted earth fault protection

- Breaker failure

•	Over current and Earth fault protection

- At least three stage directional/non directional over current and earth fault elements on for each of the three windings

- Selectable IEC/IEEE operation characteristics for all elements

- Breaker failure

- Thermal overload protection

- Negative phase sequence protection

•	Power protection

- Directional under/overactive and reactive power protection

•	Voltage protection

- At least two stage over/under voltage protection

- At least two stage residual over voltage protection

- Over excitation protection

- Loss of voltage protection

- Neutral voltage protection

•	Frequency protection

- At least 4 stage Over/under frequency protection

- Rate of change of frequency protection

•	Secondary systems supervision

- Current transformer supervision

- Voltage transformer supervision

•	Control

- Reasonably large mimic LCD for bay switchgear position indication and control with at least 8 open/close control commands of bay switch gear.

Circulating current protection between parallel transformers has to be included in the voltage regulator.

The back-up protection relays for transformers and lines.

Feeder protection and control Intelligent Electronic Devices, which be used for transformers, reactors, transmission lines and distribution feeders back up protection, shall have functions not limited to:

•	Directional/non directional over current and earth fault

- Standard IEC and IEEE characteristics to be available.

- Three stage directional and non-directional elements must be available.

•	Broken conductor protection

- Standard IEC and IEEE characteristics to be available.

- Directional and non-directional negative phase sequence elements must be available.

•	Voltage protection

- Inverse definite minimum time, rate of voltage change with time, and definite time characteristics to be available for phase under and over voltage.

- Neutral and negative phase sequence over voltage functions to be available.

•	Over and under frequency protection

- Four stage rate of change of frequency with time and definite time characteristics to be available for under and over frequency.

•	Protection settings groups

- At least four MMI and opt input selectable setting groups.

•	Breaker failure protection

- Breaker failure function must be available.

•	Thermal phase overload protection

- This feature must be available.

•	Synchronisation check

- Phase angle, Magnitude and Frequency conditions to be available.

- Live bus-Dead line, Live bus-live line and Live line-dead bus  options to  be available on synchronization check.

- Manual closing synchronization to be available.

Each Transformer winding shall have a discrete back up protection relay.

### Transformer Automatic Voltage Regulators (AVRs)

#### Transformers

An Automatic Voltage Regulator shall be installed for each of the new transformers.

AVR control panels shall have features and functions not limited to;

- Transformer tap positions, Current, voltage and power measurands.

- Alarm annunciator for all transformer and tap changer, voltage control protection related indications and alarms.

- Circulating current/Out of step control for each transformer

- Local/remote control in tap changer control mechanism box

- Remote/supervisory control selection in control room.

- Remote operation in control room.

- Supervisory tapping and operation mode selection from NCC

- Master/Follower selection for each Transformer

- Independent/parallel selection for each transformer

- Auto/manual selection for each transformer

- Compensation possibility for Z and R-X compensation

- Blocking for over-current and low voltage.

#### Control of bay equipment

Supervisory and remote control of breakers, isolators, resetting of protection equipment and any other control functions shall be performed through one of the bay protection IEDs.

### Busbar Protection

Bus bar protection is required for all 132kV and 330kV bus bars at Substations.

The bus bar protection shall consist of zones (same number as numbers of bus bars). To pick the right measuring circuit the repeater relays for the isolator have to be used. The protection relay should have both main and check zone. Both zones have to give trip signal to make a trip.

Physically breaker failure protection should be included in the First main protection. We propose to use the bus bar protection for tripping of the circuit breakers. This system will simplify the trip circuits for the breaker failure protection system.

### Synch Check and Synchronising Equipment

All bays shall have synch check functions (auto and manual)

### Auto Reclose System

The reclosing system shall include single phase reclosing and three phase reclosing via check synch/synchronizing equipment. The auto reclose lockout shall be reset (after operating) from local control room and National Control Centre. The following criteria will need to be satisfied:

- High speed single pole automatic reclosing (HSAR) for single phase fault trips.

- Delayed automatic three phase reclose (DAR) for multiphase faults and three pole trips.

- No synchro check/synchronizing required for HSAR.

- DAR to be accompanied by synchro check or synchronizing system.

### Relay Protection Telecommunication System

The main communication link shall be optic fibre.

### Protection Management System

The Protection Management System shall comprise a terminal (IED/Computer) at each substation that shall interrogate the protection IEDs and report to a remote terminal installed at a remote location. The system shall facilitate the extraction of disturbance records from all protection relays as well as the modification of protection relay parameters. The remote connections from each site to the remote central terminal shall be adequately secured from unauthorized access.

### Training

The Contractor shall include costs for the training of four protection engineers at their facilities. The Contractor shall include training in setting, use of programming tools, fault finding and maintenance. The training shall include protection and maintenance personnel.

## METERING

### Scope

The metering requirement shall be as specified in the Scope of Works.  This specification covers the design, manufacture, supply, delivery installation, testing and performance requirements of meters.

### General Requirements

All transmission, sub-transmission, distribution network, power transformers and auxiliary transformers shall have meters installed for statistical and billing purposes. All billing points shall maintain a main/check arrangement whereas the statistical metering shall only have single metering. The main and check meters shall be identical in all respects.

The meters to be installed on transmission lines, transformers and other equipment shall be of multi-functional digital type. The meters shall be of robust type, insensitive to changes of temperature, vibration, etc. Input from the measuring transformers shall be based on /1A, 110 V AC.

The meters shall be able to read energy flowing in both directions – import and export modes. The meters shall have a temperature range of -4oC to +70oC.

The meters shall meet the following:

- Panel mounted.

- Two serial communication ports

- Optical head

- Ethernet port

- More than 1 year logging memory

- Instantaneous values with high accuracy

- Power Quality measurement

- Energy Metering – Active, Reactive and Apparent

- Easy to Configure

- Open protocol

- Load Profile Recording

- Phase failure and voltage loss recording

- All readings to be Primary Values

- In built IEC61850 along with RS232/RS485 and Ethernet ports in a single product & capability of simultaneous communication through all these port

- Remote configuration of communication ports

- Meter cover and terminal cover open detection

- Meter reading and display viewing under power outage

- Simultaneous DLMS and MODBUS over Ethernet port

- 0.2S accuracy for active and reactive measurement

The Contractor shall design and implement AMI (Advanced Meter Infrastructure) in each substation. This shall be implemented on the existing ZESCO optic fibre network using the standard Fast Ethernet interfaces.

The Contractor shall setup a Local Area Network (LAN) with redundancy at each substation in a star topology. All meters in a substation shall be accessible through the LAN by means of the local Workstation. The LAN shall then link to the SDH equipment.

#### Measure Energy

- Active energy (Wh)

Energy measurement for import and export directions

- Reactive energy (VArh)

Energy measurement for import and export directions

Reactive energy for all quadrants QI-QIV

Indication of either capacitive or inductive

- Apparent energy (Vah)

Energy measurement for import and export directions

Calculated independently for each phase, total calculated as a square root of watts and vars

| Energy | Import/Export | QI-QIV | Capacitive/Inductive |
| --- | --- | --- | --- |
| Active Reactive Apparent |  |  |  |

#### Store Loggers (Load Profile)

Should have large capacity for data-logging purposes for various programmable demand   integrations   periods such as 1, 5, 15, 30 and 60 minutes.

| Logged Value | By Phase | Total | Min/Max |
| --- | --- | --- | --- |
| Active energy import/export Reactive energy import/export Reactive energy inductive/capacitive Reactive energy QI-QIV Apparent energy import/export Phase voltage Phase to phase voltage Current Active power Reactive power Apparent power Frequency Phase angle Power factor (pf) THD voltage THD current |  |  |  |

#### Display Instantaneous Values with high accuracy (as with energy)

- Current in each phase

- Phase to phase voltage

- Phase to neutral voltages

- Power factor per phase and total

- Phase angle per phase

- Frequency

- Active power per phase and total

- Reactive power per phase and total

- Apparent power per phase and total

- THD for voltage and current

- Vector diagram

#### Act as Terminal

- Equipped with inputs which can be used to record energy from other meters.

- This feature very important for summation metering on  various feeders

#### Transmit and Receive Pulse Information

- Equipped with inputs to receive external pulses from meters.

#### Calculate Maximum Demand

- Able to calculate not less than 5 different maximum demands in different MD registers.

#### Front Panel Keys

- Front panel buttons to help user navigate useful information in the meter.

#### Configuration

- Configuration of the meter parameters should be done easily using software available in numerous languages especially English.

#### Accuracy

- Class 0.2S or better

#### Measuring Voltage

- 4 or 3  wire system		3 x 55.7 – 415V

- Range			80% - UN – 115%

- Frequency		50Hz

- Burden			17mVA/phase at 120V

- Max O/L Voltage		1.3 x UN Continuously

#### Measuring Current

- Secondary Current	/1A

- Range			0.1 - 200% of IN

- Max O/L Current		2 x IN Continuously

#### Auxiliary Supply

- Internal (self-powered)

- or External 		40-276VAC/DC

#### Inputs/Outputs

- 4 configurable I/O

- 4 Fixed I/O

#### Communication

- Optical port

Meter should be equipped with an optical port which complies with IEC 62056-21

- RS422/485 port

Used to connect many meters on the same site in a LAN.

- Ethernet port

Used to easily connect to all meters remotely to a central station.

- Baud rate	1200 - 19200 baud

#### Display

- Graphical with backlight provision

- 9 digits including 0-4 decimals (minimum), Size: 69 x 39 mm (H x W), 128x80 pixels

- Pixel size: 0.5 mm²

- Max display character size 10 x 5 mm (H x W)

#### Security

- Meter to have sealing tabs screws.

- Software security to allow calibration (highest) and read only (lowest)

### Normative References

The requirements of the following standards / specifications shall be met where applicable unless otherwise stated in this specification.

| Specification / Standard Number | Title |
| --- | --- |
| IEC 60051-7 | Direct acting indicating analogue electrical measuring instruments and their accessories |
| 60073 | Coding of indicating devices and actuators by colours and supplementary means |
| IEC 62053-21 | Electricity metering equipment. Alternating current static watt-hour meters for active energy (classes 1 & 2) |
| IEC 211 | Maximum Demand Indicators |
| IEC 297 | Environmental specifications for cabinets, racks & sub racks and Dimensions of mechanical structures of the 482.6mm (19in) series |
| IEC 62053-11 | Electricity metering equipment (a.c). Class 0.5, 1 and 2 alternating current watt hour electromechanical meters |
| IEC 62053-22 | Electricity metering equipment. Alternating current static watt-hour meters for active energy (classes 0.2S and 0.5S |
| IEC 62053-23 | Electricity metering equipment. Static metering for reactive energy class 2 & 3. |
| IEC 62052-11 | Electricity metering equipment. General requirements, tests & test conditions. |
| IEC 62053-31 | Electricity metering equipment. Pulse output for electromechanical & electronic meters (two wires only) |
| IEC 62053-61 | Electricity metering equipment. Power consumption and voltage requirements. |

### Meter Communications

The energy meters shall have the following communication interfaces:

- Fast Ethernet ,10/100Mbps, Protocol: DLMS and MODBUS TCP simultaneous client, Full duplex port (RJ-45)

- Serial Communication port RS232

- Hardware	RS232 serial port

- Port type	D-Sub, 9 pin.

- Protocol	IEC 62056-21/IEC1107 Mode C programming mode or DLMS/COSEM/MODBUS

- Serial Communication port RS485

- Protocol: Configurable DLMS/MODBUS RTU,

- Baud rate: 1200 – 57600 bps, Half duplex

- Standard IEC 62056/1107

- Optical Communication

- Protocol: DLMS, baud rate:1200 – 19200, half duplex

- Hardware	IEC 62056-21/IEC1107 optical port

- Protocol	IEC 62056-21/IEC1107 Mode C programming mode

- GPRS

- The meter shall be provided with a slot for insertion of a SIM card for GPRS communication on the 3G/4G/5G Global System for Mobile communication (GSM).

### Meter Case

Each meter shall have a dustproof case which can be sealed on site using sealing wire and seals to stop access to the terminals and meter by unauthorized persons.

The case of the meter should be non-hygroscopic and shall be of a material which will ensure reasonable safety against fire. It shall be of sufficient strength to afford the working parts adequate protection against mechanical damage.

If the entire cover is not transparent, one or more windows shall be provided for reading the outputs. A visual display of outputs shall be provided as controllable by a selection keypad. The transparent windows shall not be removable without first breaking the meter seal.

A property plate shall be permanently fixed inside the meter case in a clearly visible position engraved in English, the wording of which will be advised at the time of Contract award.

### Labels

All meters shall be clearly and permanently labelled to the approval of the Engineer. The dimensions and size of lettering shall be to the approval of the Engineer. Labels should have black lettering on a white background.

### Meter Accuracy

All integrating meters shall comply with the following limits of accuracy.

| Conditions of Test |  | Limits of Error |  |
| --- | --- | --- | --- |
| Current Expressed as a Percentage of the Marked Current | Power Factor | Grade for Tariff Meters Plus & Minus | Precision Statistical Meters Plus & Minus |
| 125% to 20% inclusive | 1.0 | 0.5% | 2.0% |
| Below 20% down to 10% inclusive | 1.0 | 1.0% | 2.0% |
| Below 10% down to 5% inclusive | 1.0 | 1.5% | 2.0% |
| 125% to 20% inclusive | 0.5 (lag) | 1.0% | 2.0% |
| Below 20% down to 10% inclusive | 0.5 (lag) | 2.0% | 2.5% |

When the meter is under the reference conditions stipulated in the appropriate IEC Publication, the percentage error shall not exceed the limits of error as set out in  the table above.

### Temperature Monitoring

There shall be installed on all power transformers temperature monitoring devices. These shall be for monitoring Winding Temperature (WTI) and Oil Temperature (OTI) of the transformers.

The temperature devices shall be equipped temperature transducers for the purpose of remote monitoring and readings.

The indications on these gauges shall be read on the temperature devices and remotely via the Metering System to the Remote Stations i.e. Kitwe and Lusaka.

### Metering System

#### AMI - Advanced Metering Infrastructure

Please Note: This infrastructure is for Bid purposes only and shall in no way limit the Employer in selecting the best possible system.

The AMI shall be deployed as follows:

- The AMI architecture shall be of main and back-up server arrangement.

- The AMI system shall have two main operation centres with workstations located as follows.

- ZESCO HQ in Lusaka; and

- ZESCO Transmission offices in Kitwe

- All  lines and transformers shall have Smart meters installed at all 330kV, 220kV, 132kV, 33kV and 11kV substations.

#### The AMI system implementation shall maintain the main and check meter arrangements at all billing points and the rest of the points shall have single meters.AMI Features

The AMI system shall read the historical billing data stored in the meters and logged load profiles data in the meters as well as live (instantaneous) accumulative and instrumentation measurements.  The following are the features of the AMI system.

- Scheduled meter readings

- Real time meter readings

- Automatic retry for reading failure.

- Alarming of reading failure

- Provision for manual entry of meter reading in case of failure of automated reading for any reason

- Monthly and daily analysis reports for low voltages, high voltages, line and sub-network loss analysis. These reports should be user customizable and configurable.

- Remote metering

- Line voltage loss detection

- Remote management and upgrades

- Archive management

- Event management

- Time synchronization

- Bi-directional meter supporting

- Fault management

- Back up management

- Statistics and reports. The readings and reports should be exportable to other computer programs such as excel.

- Data inquiry

- Interfaces supporting

- Network structure, scheme or topology indicating location of installed meters.

#### AMI Network

The Automatic Meter Infrastructure shall be implemented on the existing ZESCO optic fibre network using the standard Fast Ethernet interfaces.

The prospective bidder shall set up a Local Area Network (LAN) with redundancy at each substation in a star topology. All AMI meters in the particular substation shall be accessible through this LAN.

The AMI LAN in the relay rooms shall be linked to the SDH equipment located in the communication room using UTP cable.

The UTP cables shall be the standard CAT-6 and shall use the TIA/EIA-568-B wiring and color-coding standard.

The cables shall be laid through a flexible rodent resistant PVC pipe using existing cable trenches.

Each UTP cable on the LAN shall not exceed 100 metres in length.

The AMI servers at Kitwe and Lusaka shall communicate to the remote AMI meters using the ZTE ZXMP S385, S330, S200 and corresponding terminals on the fibre network.

All major transmission and distribution substations are linked to the ZESCO optic fibre. Thus, the AMI communication protocols between the meters and the servers shall be encapsulated on the TCP/IP media.

The physical (hardware) interface on the ZESCO SDH terminals for the Fast Ethernet connection shall be the standard RJ-45 electrical port.

Where the ZESCO optic fibre is not present, the meters shall be accessed through the GPRS connection.

#### Remote Metering

The system shall have the following remote meter reading functions and capabilities:

- The AMI system shall initiate the meter reading and collection of end of month cumulative active, apparent, reactive energy and average maximum demand reading at the beginning of each month. The readings shall be for both import and export power flows. This feature shall be scheduled by the user.

- Time Of Use (TOU) shall be fully configurable both on the meters and the AMI system and TOU registers shall be readable on the AMI system.

- Remote reading of values such as load profiles, instrumentation measurements profiles, live line measurements, meter configurations and historical meter data shall be available at the request of the user/operator.

#### Meter Management

The AMI system shall be capable of the following:

- Automatic recognition of connected meters

- Remote meter diagnostics

- Remote meter configurations and upgrade

- Flagging potential meter or communications link failures

- Grouping of meters

- Identifying instances of meter tamper of interference

- Indication of offline AMI meters

#### Time Synchronization

The AMI shall be capable of regular time synchronization of all meters from the server clock.

#### Communication and Data Security

- International standard communication protocol; IEC 62056

- The AMI system should be open and should function with any meters with the international communication standard from suppliers other than the supplier of the AMI system.

- The AMI system should mainly use the optic fibre communications available at ZESCO transmission substations. GPRS communications should be used for stations without optic fibre communications.

#### Metrology and Quality Supply

Voltage monitoring

Meter status monitoring

Measurement values shall be configurable Mega or kilo (MW/kW, MWh/kWh, MVA/kVA, MVAh/kVAh, MVAr/kVAr, MVArh/kVArh etc) depending on measurement magnitude and to two decimal places for the higher scale (Mega) and shall be primary values.

Under voltage/overvoltage threshold setting and alarms.

#### System Expandability

The system should be expandable and upgradable to accommodate future additional transmission circuits and meters.

### Non-Compliance Schedule

The bidder shall provide a list of noncompliance’s with this specification, documenting the effects that such noncompliance is likely to have on the equipment’s life, operating characteristics, and system performance. Each noncompliance shall refer to the relevant specification clause.

| Specification Clause | Non-Compliance description |
| --- | --- |

### Test Certificates Schedule

The bidder shall provide a list of the test certificates included with the bid. The list shall include type test certificate routine test report references. Each certificate listed shall as far as possible refer to the relevant specification clause.

| Specification Clause | Non-Compliance description |
| --- | --- |

### INSPECTIONS

#### Pre-Factory Acceptance Test and Factory Acceptance Tests

After configuring the whole system together with its components, the contractor shall perform pre-Factory Acceptance Tests (Pre-FAT), to ensure that the system performs according to the specification.

The contractor shall also perform FAT tests before the system is shipped to Zambia. The FAT shall be witnessed by ZESCO Meter Engineers.

#### Operational Acceptance Tests

Site Acceptance Tests (SAT) should be performed on site upon installation of the whole system. This should be done to ensure the system performs according to specification and integrates well with other components that will be re-used. The contractor shall send site commissioning engineers to ensure installation, testing and commissioning.

### TRAINING:

It is preferred that the configuration of the multifunctional digital meters will have to be done by three (03) ZESCO Meter Engineers under supervision of Contractor’s expert Engineers. These ZESCO engineers will have to be trained in detail at Contractor’s Factory premises for a period of not less than 14 days before undertaking these works to ensure transfer of skills and guarantee of adequate maintenance and troubleshooting of the multifunctional digital meter and remote metering system long after the commissioning of this project. The training should cover at least the following:

#### Multifunctional Digital Energy Meter COURSES

- Meter Programming & Configuration techniques

- Meter Communication techniques

- Meter Multi-dropping techniques

#### Remote Metering TRAINING

- Remote reading of values such as: load profiles, instrumentation measurements profiles, live line measurements, meter configurations, historical meter data.

- Remote configuration of the meters

#### Programmable Transducers Course

- Configuration of all methods of connection

- Parameter setting of outputs.

- Reading and displaying the programmed configuration

- Clear presentation of the input and output parameters

- Transmission of changed programming data to the transducer and archiving

#### Temperature Gauge Course

- Gauge hardware

- Setting and Calibration techniques

### COST OF TRAINING:

Total training fee should be for 3 Engineers for not less than 14 days (Including the two-way flights fee, per diem, accommodation, and transportation in contractor’s country)

### DOCUMENTATION

After commissioning the Substation metering system, As-Built Drawing will have to be submitted to the Project Manager in both hard copy and soft copy.

### SPARES

Adequate spares should be provided as follows:

- Spare workstation (1 each per substation).

- Tool for configuration and Programming of Energy meters (2 No.)

- Spare energy meters (2 each per substation).

- Spare multifunctional digital meters (2 each per substation).

- Programmable Transducers (4 each per substation)

## SUBSTATION AUTOMATION AND CONTROL

### General

In the new SAS, all commands, status information of switchgear and measurements shall come via Bay Control Units (BCUs) based on IEC 61850 protocol. The Protection alarms and events will be captured by Protection Intelligent Electronic Devices (IEDs) also via IEC 61850 protocol. All signals shall be available on the Station Controller (Gateway/RTU). Signals for circuits at 330kV/ 132kV, 88kV, 66kV shall be sent to the National Control Centre (NCC) and Emergency Control Centre (ECC) via two separate IEC 60870-5-104 upstream communication protocol lines of the Gateways. Signals for circuits at 33kV and 11kV shall be sent to the Distribution Regional Control Centres (RCCs) using a separate IEC104 Protocol line.

These BCUs and Protection Relays shall be supplied already fitted in the Control & Protection Relay (CRP) panels. The contractor shall supply and install complete panels fitted with new internal wiring and all the relevant IEDs and other devices required for each bay.

Editing and input of local data and parameters shall be performed locally by suitable programming tools for IEC 61850 with licenses available to ZESCO Engineers after commissioning. Preferably it should be possible to edit any such local data at a higher control level and download this information to the IEDs.

Local monitoring and control shall also be provided via Local HMI computers apart from the control board.

The Control system devices shall consist of separate redundant Human Machine Interface (HMI) Servers, redundant client workstation computers, redundant Gateways/RTUs for communication to NCC/ECC and RCC, Bay Control Units, Protection IEDs, AVRs and LAN Switches and GPS units for time synchronization. The communication protocol at substation bus level shall be IEC61850.

The communication system between the Substation Control System Gateways and the NCC and ECC Process Communication Units (PCUs) shall support IEC 60870-5-104 communication protocol. The contractor shall ensure effective communication to both NCC and ECC through implementation of two separate RTUs/Gateways that support these communication protocols (IEC 61850 downstream and IEC 60870-5-104 upstream). The contractor shall however provide a much superior option, if available, that will ensure simultaneous effective monitoring and control by both NCC/ECC and RCC masters.

#### Basic System Elements

The basic system to be delivered should comprise the following system modules:

- HMI Server computers with SCADA functions

- Operator Workstation (HMI Client) computers

- Gateway computers

- Bay Control Units

- GPS clock complete with antenna and accessories.

- Engineering & Maintenance Laptops for Control IED and SAS Configuration

- Station LAN Communication

- LAN cables

- Standard 19” Control Panels

- Industrial Network switches

- Colour LaserJet printers

- Inverters (DC to AC Power conversion)

Some of the above modules are defined below in more detail.

#### Human Machine Interface (HMI) Server & Client computer

The HMI Server shall have a database for all substation I/Os (process inputs/outputs) and have appropriate application software to facilitate data acquisition, device control and supervision functions (SCADA functions).

The HMI Server shall have appropriate database configuration software and tools such as a user-friendly graphical editor, trends, and report configuration tools.

The HMI Server computer should be configured to auto reboot and auto logon after recovery from an interruption of power supply. The HMI server computer should also be loaded with HMI Client software. It should therefore be possible to view the graphical user interface for system operations on the HMI server computer.

The HMI Server and Client computer time should be synchronized by the local GPS unit.  All servers/ workstations to have RAID hard disks and to be rack mounted.

#### Operator Workstation (HMI) Client

The Operator Workstation or HMI Client computer shall provide the Graphical User Interface (GUI) for system operations. It shall have the relevant substation single line diagram and other relevant system pictures through the HMI Client GUI software. The HMI Client shall display time stamped alarms and events with milli-second resolution and audible alarm function.

On the HMI computer, a software-controlled toggle switch should be configured to toggle between NCC/ECC control and Local HMI control. The HMI application shall default to Remote (NCC/ECC) Control after 10 minutes of inactivity while selected to Local HMI control. Operating systems to be installed on the Servers/ Workstations must be robust enough to withstand current cyber security threats. This quality must be demonstrated by the contractor.

#### Gateway/RTU

The two separate Gateways/RTUs shall facilitate communication between the Substation Control System and Remote Masters (NCC, ECC & RCC). The two Gateways shall have appropriate software and a database that will enable I/O signals to be sent to the NCC, ECC & RCC masters and vice versa. They should support communication protocols such as IEC 60870-5-104 upstream and IEC 61850 as well as legacy serial protocols downstream.

The gateways/RTUs should be configured to auto reboot and auto logon after recovery from an interruption of power supply.

The Gateways/RTUs’ time should be synchronized by the local GPS clock unit. The Firmware or Operating system to be installed on the RTU/Gateway must be robust enough to withstand current cyber security threats. This quality must be demonstrated by the contractor. All Gateways to have RAID hard disks and to be rack mounted industrial type hardware. In the case of microprocessor based RTU as station controller, it must have redundant communication cards configured in hot-standby mode to ensure continuous availability of station monitoring and control.

#### Bay Control Units

The contractor shall provide ZESCO with modern Bay Control Units (BCUs) that possess the ability to communicate using the IEC 61850 protocol as well as some legacy protocols such as Modbus serial and Modbus-TCP.

One Bay Control Unit shall be installed for each substation bay. A bay shall be defined as a circuit breaker and its associated disconnector switches. For example, in the case of a transformer, the switchgear at each voltage level shall be a bay and shall each have a BCU dedicated to it.

The Bay Control Units (BCU) shall be equipped with a processor card, communication card, digital input cards, digital output cards and analog input cards. The BCUs shall be equipped with a large format digital mimic on the front panel displaying the appropriate bay single line diagram and basic measurands. It shall be possible to reconfigure the digital mimic in case of addition of any new equipment to the bay. A BCU Local/Remote operation mode selection button shall also be provided. It should be possible to send controls to switchgear from the BCUs.

The Bay Control Units shall communicate via IEC 61850 and provide I/O status data to the HMI and Gateway computers and where appropriate, with peer IEDs. ZESCO wishes to use the latest communication protocols on the station LANs to benefit from advances in modern technology.

#### Automatic Voltage Regulators (AVR)

The contractor shall provide and install Automatic Voltage Regulators for the transformer bays. The AVRs shall be IEC 61850 compliant preferably MR Tapcon 230 Expert or REG-DA e-berle.

#### GPS Clock

The GPS Clock shall provide standard time to all the network devices. A large display format digital clock synchronized with the GPS clock shall be installed at an appropriate location in the substation control room. The BCUs, Station Servers, HMI workstations and Gateways shall be synchronized using the NTP or PTP protocol, whichever is applicable, while the Protection IEDs shall be synchronized via IRIG-B. The contractor shall ensure that all computers, BCUs and intelligent relays are time synchronized by the GPS clock.

#### Engineering Workstations

The contractor shall supply ZESCO with Control System maintenance/engineering desktop computer to be installed within the substation and three laptop computers all fully loaded with bay configuration software and appropriate drivers to facilitate configuration and maintenance of the BCUs and Protection IEDs. The workstation shall also be loaded with GPS unit configuration software. The workstation and laptops shall serve as the system configuration and documentation backup repository. The contractor shall also supply the communication cables that will be used to connect the engineering workstation and laptops to the control and protection IEDs. The system configurations shall be able to be downloaded and stored on the workstations. Additionally, the contractor shall provide one separate laptop loaded with the software for Protection IEDs administration only.

#### Control Cables

The contractor shall supply all control cables between marshalling kiosks and the control and protection panels and provide internal wiring cables for use inside the panels between the terminal blocks and the new devices. The contractor shall be required to assess as much as possible during the mandatory site visits all requirements for cabling for the successful implementation of the project.

#### Colour Laserjet Printers

The Contractor shall provide two (02) colour Laserjet Printers preferably HP model.

#### Substation Control System Architecture / Overview

The architecture of the envisaged microprocessor-based Substation Automation System (SAS) is shown below.

This architecture applies to all voltage levels (330kV,132kV,88kV, 66kV, 33kV) and is for Bid purposes only. It shall in no way limit the Employer in selecting the best possible system.

### Station LAN Configuration

#### Station LAN and Communication

The substation LAN shall have redundant process and station network, that is, Net A and Net B and all network components connecting to the LANs must have the capability to connect to both networks. In the case of ring architecture, it shall be a double, self-healing ring topology. At process level, or between IEDs and LAN Switches, Fiber optic cables are preferred. Between station level devices/equipment such as Gateways, HMIs and Engineering workstation and the station LAN, CAT5e STP/UPT cable shall be preferred. All communication cables (Fiber Optic and UTP/STP) shall all be protected by flexible conduit when passing through the cable trenches.

#### LAN Cables

The contractor shall provide sufficient and appropriate physical LAN cables with spare cables. The process and station network shall be physically redundant. The LAN cables that shall run in the cable trenches of the control building shall be armoured to provide extra protection from rodents. In the absence of armoured cable, a protective conduit shall be used to shield the cables.

#### Network Switches

The Contractor shall provide robust Industrial type of switches suitable for operation in high tension environments. All devices and panels shall be adequately electrically grounded. The Ethernet LAN Switches shall be ruggedized managed type with appropriate type and number of Fibre Optic and Electrical LAN Ports.

#### Control and Protection Panels

The contractor shall provide new standard 19” panels (800x600x2200mm) with IEDs preinstalled.

All panels supplied shall be of a design that incorporates a swing frame and clear glass visor on the front door. All cables terminated into the panels shall be adequately glanded and appropriate lugging shall be used. Where new terminal blocks are required, The Contractor shall ensure that all necessary terminal blocks are supplied and installed.

#### Inverters (DC to AC Power conversion)

The Contractor shall provide 110/220 V DC to 230 V AC inverters (min 2500W) in dual redundancy configuration to power the control system. At 330kV substations the DC system shall be operated at 220V DC. The inverters shall have a static bypass facility.

#### Monitoring And Control Functionality

The substation control system shall operate at the following levels:

- Supervisory control and monitoring from the National Control Centre (NCC) and Emergency Control Centre (ECC).

- Local HMI Workstations

- Local control at the Bay Control Units and/or the control boards

- Direct operation for maintenance and emergency on primary components (manual operation)

The selectivity of control shall be done at HMI level. As such the HMI Workstations shall be equipped with a Supervisory/Local Control selector. If the selector switch is in “Supervisory” position, then it should be possible to operate switchgear from supervisory system only. If the switch is in “Local” position, then it should be possible to operate Switchgear from the HMI only. By default, control shall be set to supervisory. However, if control is set to “Local” the system will revert control to “Supervisory” after 10 minutes of inactivity.

In addition, the bay control boards shall have “Remote/Local” control selector switches. If the selector is in “Remote” position, it shall be possible to operate switchgear from the HMI computer or the Dispatch Centre (NCC/ECC) only. If the selector is in “Local” position, then it should be possible to operate switchgear from the control board or BCU only.

In addition, the bay control boards shall have bay mimic diagram with circuit breaker Close/Open push buttons for the corresponding circuit breakers with simple status indication for CBs and isolators. The BCUs shall also have Single-line Diagrams on the display screen which shall indicate the status of the bay in real time and allow for bay level control.

#### Inherent Safety Features

The system should be made fail-safe. If a failure on the system arises, no maloperation of the control system should be possible. No fault in the SCADA system or the interfaces between the systems shall interrupt or affect the operation of the substation.

No fault in the bay control units or in the communication equipment shall interfere with the other control units or interrupt or otherwise block the remote and supervisory operation of the substation.

Software interlocks shall be implemented in such a manner that the following conditions must be met:

- When a command is selected, there should be a two-stage confirmation of the selected command prior to execution of the selected command.

- It should not be possible to execute a switchgear command on the HMI workstation while the control selector is in “Supervisory” position.

- It should not be possible to operate an isolator while the associated bay Circuit Breaker is in a closed position.

- It should not be possible to close a Circuit Breaker while the associated bay Earth Switch is in a closed position.

- It should not be possible to close the Earth Switch while the associated bay Circuit Breaker is in a closed position.

- Command operations shall only be possible in the associated bay sub-picture.

#### Event And Alarm Handling

All faults and abnormal conditions which may occur in any plant equipment shall generate an alarm and be transferred to the station and supervisory control systems (i.e., Station HMI and NCC/ECC).

Events shall include (but not be limited to) protection trips, circuit breaker, isolator and earth switch positions, selector switch remote/supervisory control “on/off”; selector switch for bay local/remote control “on/off” and selector switch auto reclose “on/off”. All events should be transferred to NCC/ECC.

For each event a Sequence of Events (SOE) record must be available on the HMI workstation with a time resolution of one millisecond (1ms).

### Factory Acceptance Tests (FATs) on SAS and Protection Equipment

FATs are mandatory for all Substation Automation, Control and Protection Systems equipment prior to shipment. No shipment release authorization shall be granted in the absence of FATs on SAS, SCADA & Protection system equipment. The arrangements for FATs shall include air tickets, local transportation, accommodation and per diem (US$365/day/person) for a duration to be proposed by the contractor and approved by the employer for six (10) ZESCO engineers. The contractor shall arrange for suitable 5-star hotel accommodation or equivalent. Prior to travelling, the contractor shall avail the FAT schedule indicating the duration of FAT to the ZESCO Project Manager.

### Factory Training on Substation Automation, SCADA and Protection Systems equipment

Factory Training is mandatory Substation Automation and Protection System equipment. The arrangements for Factory Training shall include air tickets, local transportation, accommodation and per diem (US$365/day/person) for three weeks for ten (10) ZESCO engineers. The contractor shall arrange for suitable 3 -star hotel accommodation or equivalent. A training schedule shall be availed to the project manager prior to the date of travel indicating the training period and training content by the contractor.

### Substation Control System Training

Detailed SCADA training shall be provided for six (10) ZESCO SCADA engineers at the contractor’s premises and all costs shall be borne by the contractor. Site-specific training shall also be provided by the contractor after successful commissioning of the control system.

All necessary programming tools (Engineering laptops pre-loaded with fully licensed software tools) for SCADA maintenance, simple re-programming and uploading, downloading, etc. shall be supplied by the Contractor at the time of issue of the completion certificate.

#### Control System Introduction Courses

- Substation Control System - Hardware

- Substation Control System - Introduction Data Acquisition

- Introduction in IEC61850 and IEC60870-5-104 standard structure - used protocol elements.

#### Control System Gateway Training

- Programming of Sequence of Events in Gateway

- Programming of Command Outputs in Gateway

- Programming of Measurands (Current, voltage, Power and Energy) in Gateway

- Programming of Digital inputs in Gateway

- Programming of Alarms in Gateway

- Configuration of Substation Communication protocols (IEC61850)

- Configuration of NCC and ECC protocols (IEC 60870-5-101; IEC 60870-5-104)

This same detailed training should extend to the HMI and BCUs as follows:

#### Control System HMI Training

- Station LAN configuration

- Substation Data engineering (Database)

- Programming of HMI Diagrams/Pictures

- Programming of Sequence of Events in HMI

- Programming of Command Outputs in HMI

- Programming of Measurands (Current, voltage, Power and Energy) in HMI

- Programming of Digital inputs in HMI

- Programming of Alarms in HMI

- Configuration of Substation Communication protocols (IEC61850)

- Integration of Protection signals in HMI

#### Control System IED Training

- Programming of IED Mimic Diagram

- Definition of Event and Alarm Lists in IED

- Programming of Current, Voltage, Real Power, Reactive Power, Apparent Power and Energy in IED

- Programming of Digital Inputs in IED

- Programming of Digital Outputs in IED

- Programming of Interlocking and Switching Functions in IED

- Configuration of Substation Communication protocols (IEC61850)

### Technical Requirements & Technical Schedules for SAS Equipment

Table 18-1 Bay Control Unit

|  | All Bay Control Units (BCUs) are to meet the following specifications as a minimum |  | ZESCO Criteria | Bidder’s Response |
| --- | --- | --- | --- | --- |
|  | Manufacturer |  | Specify |  |
|  | Model number |  | Specify |  |
|  | Country of origin |  | Specify |  |
|  | Minimum Functionality |  |  |  |
|  | Graphical Man-Machine Interface |  | Yes |  |
|  | Fuse Fail Supervision |  | Yes |  |
|  | Main Trip Circuit Supervision (Dual State) |  | Yes |  |
|  | Backup Trip Circuit Supervision (Dual State) |  | Yes |  |
|  | Circuit Breaker Fail Protection |  |  |  |
|  | Voltage and Current Measuring Functions |  | Yes |  |
|  | 3 Phase Power Measuring Functions |  | Yes |  |
|  | Circuit Breaker Wear Monitor |  | Yes |  |
|  | Synchro Check function |  | Yes |  |
|  | Electrically operated devices’ control |  | Yes - SCADA & Local selection via relay pushbuttons / switch |  |
|  | Rated Frequency (fn) | Hz | 50 |  |
|  | Local / Remote Control Selection |  | Yes - SCADA & Local selection via relay pushbuttons / switch |  |
|  | Binary opto-input Channels |  | >96 |  |
|  | Binary Output Channels |  | >24 |  |
|  | Binary Input Voltage Range | V dc | 60-220 |  |
|  | Rated Auxiliary Supply Voltage | V dc | 60-220 |  |
|  | Rated Auxiliary Supply Voltage Operation Range | % | 80 - 120 |  |
|  | Internal hardware and Software Supervision |  | Internal Alarm variable programmable to a fail-safe Output Contact |  |
|  | Internal Relay Fail watchdog potential free contact |  | Yes |  |
|  | Output Contact Rated Voltage | V dc | >=300 |  |
|  | Output Contact Continuous Current Rating | A | >=10 |  |
|  | Data Communication on dual Ethernet port to Substation LAN – IEC61850 (including send /receive GOOSE) and legacy protocols such as MODBUS, IEC-103, DNP.3, etc |  | Yes |  |
|  | Number of Switch Control Logical Nodes (CSWI) |  | >=7 |  |
|  | Time Sychronization capable (SNTP/PTP) |  | Yes |  |
|  | Large format Local HMI Display with integrated control functionality |  | Yes |  |
|  | Front-mounted LEDs for alarm or status annunciation |  | Yes |  |
|  | Full Local and Remote Control and Interlocking |  | Yes |  |
|  | Local Data Communication port |  | Yes (front) |  |
|  | Attach Data Sheet, Technical Specifications and Type Test certificates |  | Yes |  |
|  | All supplied Master Trip / Lock-out Relays are to meet the following specifications at a minimum |  |  | ----- |
|  | Manufacturer |  | Specify |  |
|  | Type or designation |  | Specify |  |
|  | Country of origin |  | Specify |  |
|  | Technical Details |  |  |  |
|  | Mechanically Latched |  | Yes |  |
|  | Flagged Indication |  | Yes |  |
|  | Reset |  | Electrical and Manual |  |
|  | Maximum Operation time | ms | 25 |  |
|  | Rated Supply Voltage | Vdc | 60-220 |  |
|  | Rated Supply Voltage Operation Range | % | 80 - 120 |  |
|  | Output Contact Rated Voltage | V | 400 |  |
|  | Attach Data Sheet, Technical Specifications and Type Test certificates | V AC/DC | Yes |  |

Table 18-2 Station Servers

|  | SCADA HMI Server/Client |  | ZESCO Criteria | Bidder’s Response |
| --- | --- | --- | --- | --- |
|  | Manufacturer |  | Specify |  |
|  | Model Number |  | Specify |  |
|  | Country of Origin |  | Specify |  |
|  | Redundancy |  | 1 + 1 |  |
|  |  |  | (On hot standby) |  |
|  | Communication Protocol |  | IEC 61850 |  |
|  | HMI Interface with Substation LAN redundancy |  | specify |  |
|  | HMI Memory (capacity and redundancy) |  | specify |  |
|  | HMI Additional Hardware |  | specify |  |
|  | HMI Mounting |  | specify |  |
|  | Display Screen Type |  | specify |  |
|  | Display Screen Size |  | >= 27-inches |  |

Table 18-3 Gateway

|  | Gateway |  | ZESCO Criteria | Bidder’s Response |
| --- | --- | --- | --- | --- |
|  | Manufacturer |  | Specify |  |
|  | Model Number |  | Specify |  |
|  | Country of Origin |  | Specify |  |
|  | Redundancy |  | 1+1 |  |
|  | Upstream Communication Ports (number of) |  | 4 ports |  |
|  | Upstream Communication Ports (communication protocol support) |  | IEC 60870-5-104 |  |
|  | Downstream Communication Ports (number of) |  | Specify |  |
|  | Downstream Communication Ports (communication protocol support) |  | IEC 61850 |  |

Table 18-4 Remote Terminal Unit

|  | Remote Terminal Unit |  | ZESCO Criteria | Bidder’s Response |
| --- | --- | --- | --- | --- |
|  | Manufacturer |  | Specify |  |
|  | Model Number |  | Specify |  |
|  | Country of Origin |  | Specify |  |
|  | Technical Specifications |  |  |  |
|  | Analogue Inputs (voltage range and number of) |  | specify |  |
|  | Digital Inputs (voltage range and number of) |  |  |  |
|  | Digital Outputs (voltage range and number of) |  |  |  |
|  | Fibre ports (number of) |  |  |  |
|  | Upstream Communication Ports (number of) |  | >3 ports |  |
|  | Upstream Communication Ports (communication protocol support) |  | IEC 60870-5-101 IEC 60870-5-104 |  |
|  | Time Synchronization Support |  | SNTP/PTP Server |  |
|  |  |  | SNTP/PTP Client |  |
|  | Downstream Communication Ports (number of) |  | specify |  |
|  | Downstream Communication Ports (communication protocol support) |  | IEC 61850 |  |
|  |  |  | DNP 3.0 |  |
|  |  |  | SPA-Bus |  |
|  |  |  | Modbus |  |
|  |  |  | IEC 60870-5-101 |  |
|  |  |  | IEC 60870-5-103 |  |
|  |  |  | IEC 60870-5-104 |  |

Table 18-5 Engineering Workstation

|  | Engineering Workstation PC |  | ZESCO Criteria | Bidder’s Response |
| --- | --- | --- | --- | --- |
|  | Manufacturer |  | Specify |  |
|  | Model Number |  | Specify |  |
|  | Country of Origin |  | Specify |  |
|  | Technical Specifications |  |  |  |
|  | Processor |  | Specify specify |  |
|  | RAM |  |  |  |
|  | ROM |  |  |  |
|  | ROM Redundancy |  |  |  |
|  | Monitors Type and Size |  |  |  |
|  | Keyboard |  |  |  |

Table 18-6 Station LAN

|  | Station Bus Local Area Network |  | ZESCO Criteria | Bidder’s response |
| --- | --- | --- | --- | --- |
|  | Communication cabling and equipment required to interface Workstation equipment to Substation LAN |  | specify |  |
|  | Communication cabling and equipment required to interface Substation LAN to IEDs |  | Fibre |  |
|  | Communication cabling and equipment required to establish Substation LAN Backbone |  | Fibre |  |
|  | Substation LAN Backbone Topography |  | specify |  |
|  | Substation LAN Backbone redundancy |  | specify |  |
|  | Substation LAN to IED interface redundancy |  | specify |  |
|  | Server/Gateway/RTU to IED and inter-IED communication protocol |  | IEC 61850 |  |
|  | GPS Time Server (Clock) Manufacturer and Model Number |  | Specify |  |
|  | GPS Time Server Country of Origin |  | Specify |  |
|  | GPS Time Server Protocol |  | SNTP/PTP |  |
|  | GPS Time Server Protocol Accuracy | ms | 10 |  |
|  | Ethernet Switches |  |  |  |
|  | Manufacturer |  | Specify |  |
|  | Model Number |  | Specify |  |
|  | Country of Origin |  | Specify |  |
|  | Ethernet Switches (number of) |  | Specify |  |
|  | Rated Auxiliary Supply Voltage | V DC | 60-220 |  |
|  | Rated Auxiliary Supply Voltage Operation Range |  | 80% - 120% |  |
|  | Maximum Power Consumption |  | Specify |  |
|  | Protocol Support |  | IEC 61850 |  |
|  |  |  | GOOSE |  |
|  |  |  | MMS |  |
|  |  |  | IEEE 802.1q |  |
|  |  |  | IEEE 802.1d |  |
|  |  |  | SNTP |  |

Table 18-7 Office IT LAN

|  | Office IT Local Area Network |  | ZESCO Criteria | Bidder’s response |
| --- | --- | --- | --- | --- |
|  | Communication cabling and equipment required to interface Workstation equipment to Substation LAN |  | 1000BASE-T SFP-based ports: RJ-45 connectors, 4-pair Cat 6E UTP cabling |  |
|  | Communication cabling and equipment required to interface Office LAN to Computers |  | Specify |  |
|  | Communication cabling and equipment required to establish Office LAN Backbone |  | Fibre |  |
|  | Office LAN Backbone Topography |  | specify |  |
|  | Office LAN Backbone redundancy |  | SFP Module |  |
|  | Office LAN to Computer interface redundancy |  | 24 PoE+ ports |  |
|  | Ethernet Switches |  |  |  |
|  | Manufacturer |  | CISCO |  |
|  | Model Number |  | C9300 – 24P |  |
|  | Country of Origin |  | Specify |  |
|  | Ethernet Switches (number of) |  | 24 Ports POE |  |
|  | Rated Auxiliary Supply Voltage | VAC | 230 |  |
|  | Rated Auxiliary Supply Voltage Operation Range |  | 80% - 120% |  |
|  | Maximum Power Consumption |  | Specify |  |
|  | Protocol Support |  | IEC 61850 |  |
|  |  |  | GOOSE |  |
|  |  |  | MMS |  |
|  |  |  | IEEE 802.1q |  |
|  |  |  | IEEE 802.1d |  |
|  |  |  | SNTP |  |

## NEUTRAL EARTHING

The neutral earthing configuration shall be as follows.

330kV – Solid grounding

132 or 66kV – Solid grounding

33kV resistance grounding

11kV resistance grounding.

## AUXILIARY TRANSFORMER

### General

This specification covers the manufacture, testing, supply and delivery of auxiliary or distribution type transformers and spares.

### General Design

  - transformers shall be of the mineral oil immersed core type suitable for outdoor use with ONAN cooling.

  - Transformers shall be designed to deliver full rated power continuously on any tapping within the specified tapping range under the following conditions:

- With the voltage of the untapped winding at normal, without the need to down rate the transformer at the extreme tap positions and without exceeding IEC temperature limits.

- With voltage applied up to 10% in excess of the rated tapping voltages and with injurious overheating.

  - Transformers shall be connected in accordance with IEC 60076, BS 171 or equivalent: three phase transformers to Vector Group reference Dyn11 or Yzn.

  - All LV neutrals shall be brought out of the tank to a readily accessible terminal and shall not be earthed inside the tank, unless otherwise specified in the enquiry.

  - Transformers on a particular contract with similar voltage ratios and connections shall be suitable for parallel operations on all relevant taps under with conditions they should share the load in proportion to their ratings subject to the tolerances on impedance laid down in IEC 60076 or BS 171.

  - If it is required to parallel any transformer with existing transformer, then full details of the existing transformer will be provided when contracts are placed.

  - Low impedance transformers are preferred, a maximum of 5% being envisaged on any size with no plus tolerance.

  - When requested in the enquiry, sealed designs shall be offered, and the following details shall apply:

- Unless otherwise approved, sealing shall be affected by means of a welded cover design employing a tank flange not less than 50 mm in width and a cover-plate 12 mm smaller all round to provide the required welding lip.

- Any holes or plugs used to facilitate vacuum/pressure testing, leak testing or oil filling of the transformers shall finally be sealed by welding.

- The expansion space above the oil level shall not be less than 25 per cent of the volume of the oil at 20°C and shall be nitrogen filled.  The transformers shall be sealed at atmospheric pressure.

- An oil level gauge shall be provided.

- Pressure valves, pressure/vacuum gauges, non-return valves and drain valves shall not be fitted.

- Earth stud required at both HV and LV ends of transformers.

### Windings

- Where tappings are specified in the enquiry they shall be provided in the HV windings, preferably in the centre of the windings, to permit variation of the number of HV turns without significant variation in the kVA rating.  The variations shall be effected by means of a manually operated tapping switch to be provided in accordance with Clause 13.5.

- All windings and termination shall be fully insulated and those for service above 1000 volts shall be designed for impulse voltage tests.

Designs shall be such that electrical stresses are as uniform as possible throughout the windings under impulse conditions.

- Windings shall be vacuum impregnated and insulating materials shall not be liable to soften, shrink, become brittle, carbonise, deteriorate, or collapse in any way during service.

### Cores

- The magnetic circuit shall be earthed to the core clamping structure, at one point only, and the core assembly to the tank.  Where transformers are not sealed, readily accessible removable bolted links shall be employed for the earthing connections.

- The general construction of the cores, framework and the clamping arrangements shall be robust and such that they will be capable of withstanding completely any stresses with may occur due to handling, transport or service.  All cores and yokes shall be terminated and clamped by means of a suitable framework.  Suitable means shall be provided for lifting the cores from the tanks.

- It shall not be possible for the core to move relative to the tank during handling or transport.

- Particular attention shall be paid to maintaining low core loss consistent with sound design.

### Tapping Switches

- Transformers shall be provided with approved off-circuit type tap changing equipment.

A fully insulated off-circuit, externally manually operated ganged tapping switch shall be supplied, capable of withstanding the specified impulse voltage when connected to be transformer windings.

- Clearly visible tap position indication shall be provided. The tapping switch shall be operated by means of an external handle which can be positively located and locked in each operating position.

The switch shall be mechanically robust and provided with a device between the handle and the switch to permit operation without strain in the event of imperfect alignment between switch and handle; the switch operating shaft shall be fully insulated as between tank and switch and shall be provided with a suitable oil and vacuum tight gland where it passes through the tank.

- The use of wood shall be avoided wherever possible, and all the supports and terminal boards shall be completely unaffected by hot oil and non-moisture absorbent.

- High grade insulating materials shall be used in the construction of tapping switches which shall be designed with special attention to the elimination of points where tracking is likely to occur.

- Tapping switches shall be mounted on supports made of suitable high strength insulating material and shall be provided with self-aligning spring-loaded wiping contacts capable of maintaining good electrical contact without the need for periodic maintenance.

All clearances between tapping switch contacts and leads shall be indicated on drawings submitted at the time of bidding and such clearances shall be sufficient to prevent tracing or flashovers in the event of carbon or sludge deposits forming on leakage paths.

- HV taps: Minus 7.5%: Minus 5%: Minus 2.5%: 0%: Plus 2.5%: Plus 5%: Plus 7.5%.

### Bushings

- All line terminals and neutral connections where specified, shall be brought out to porcelain outdoor type terminal bushings. The bushings shall be as specified in the following unless otherwise agreed in writing.

The following are the preferred current ratings of bushings:

| Nominal Working Voltage | Current Rating Amps |
| --- | --- |
| Below 1 000 | 110 |
|  | 250 |
|  | 500 |
|  | 850 |
|  | 1600 |
| 11 000 | 220 |
|  | 350 or 550 |
| 33 000 | 350 |

- Arcing horns shall be fitted on all transformer bushings above 660 volts.

### Tanks and Conservators

#### General

- Drain valves may be either screwed or flanged whilst conservator isolating valves shall be flanged.  Drain valves shall be complete with captive plugs which shall be either of non-ferrous metal or galvanised.

- All internal surfaces or tanks and conservators shall be shot blasted and cleaned, and a coat of protecting compound, unaffected by hot oil, shall be applied.

- All external surfaces and parts made of steel are to be thoroughly shot blasted and cleaned, after which two coats of priming paint, preferably of zinc chromate, one intermediate coat and one coat of finishing paint are to be applied.  The colour shall be approved by the Project Manager.

- Transformers on which the paints are found to flake off or deteriorate within the guaranteed period shall be suitably cleaned and repainted free of charge by the supplier.

#### Tanks

- Each transformer shall be housed in a tank of welded steel plate construction suitably stiffened where necessary but with a flat base. Wheels or rollers are not required.

- Each tank shall be provided with the accessories, the lifting lugs called for shall be suitable for lifting the transformers bodily by means of a hoist or crane when it is completely assembled and ready for service.

- All transformers up to and including 330 kVA rating shall be provided with four fixing lugs on the base drilled with 15 mm holes for bolting to a platform.  The fixing holes shall project beyond the ends of the tank and be placed to provide the most practical stable arrangement.

#### Conservators

- Where conservators are called for, they shall be of dimensions such that oil expansion may occur over the working range temperature from no load with the transformer cold at minus 1°C ambient air temperature to full load at plus 40°C ambient air temperature while the sump pipe remains covered and the oil level is visible or indicated.

- The required fittings shall be provided on all transformer conservators.

- Drain plugs shall preferably incorporate approved sampling facilities, and shall be mounted at the lowest part of the conservator tank and so designed that the sampling device can be readily cleared in the event of its being blocked by an accumulation of sludge etc., without the necessity of having to dismantle the device completely.

- Oil level gauges on conservator tanks shall be of the refracting plate glass or other approved type, marked with the level at 20°C at no-load and capable of indicating the level of oil over the specified working range.

- Where dehydrating breathers are specified, they shall be of the Silica Gel type which give indication of moisture absorption by change in colour of the charge.

- An inspection window shall be provided and mounted in a position convenient for inspection.  The breather is to incorporate an oil seal to prevent contact with the external air when breathing is not taking place.  The breather to be fitted on the LV end of the transformers.

- Where only a vent pipe without a breaker and incorporating a filling hole is specified, it shall preferably be fitted with a cap and provided with very fine mesh non corrodible anti-vermin gauze.

### Accessories and Fittings

- All transformers shall be provided with accessories and fittings unless otherwise specified in the enquiry.

- Rating and diagram plates shall be of engraved steel, brass or other approved incorrigible material.

- Where a thermometer pocket is provided, it shall be of a thin-walled metal mounted in the tank cover.

- The pocket shall project 25 mm outside of the tank and shall be threaded along the whole projecting portion, a screwed cap shall be provided to cover the pocket when not in use.

- When required lightning arresters equipped with galvanised brackets suitable for bolting to a vertical surface shall be mounted directly on to the transformer tank.  The mounting surface shall be such that the centre lines of the arresters are parallel with the centre lines of the associated bushings, and at the same spacing as the bushings.

### Insulating Oil

The transformers shall be filled with low viscosity mineral insulating oil which complies in every respect with the provision of BS 148 or IEC 60296.

### Tests

The following tests shall be carried out:

- Routing covering test certificates shall be submitted, immediately after completion of tests in the factory, for every transformer.

- As a type test, a temperature rise test on each different rating of transformer.

- As a special test, an impulse voltage withstand test including chopped waves on each different rating of transformer.

Note:	If tests to b) and c) above have been carried out satisfactory on designs identical in all essential details, tests b) and c) may be waived on the production of acceptable covering test certificates.

### Packing and Transport

Transformers shall be transported to their destination with their tanks full of oil up to the service level.

Bushings and any accessories or fittings likely to be damaged shall be protected adequately against damage in transit.

### Drawings and Diagrams

#### With Bid

The following drawings shall be supplied with any Bid unless identical drawings have been previously supplied, in which case a statement in the Bid of the applicable drawing subjects, numbers and revisions will suffice together with details of the referencs under which previous supply was made:

- General arrangement drawings of each rating of transformers offered showing:

- Minimum clearance (phase to phase and earth to earth) on HV and LV bushings including clearance HV to LV.

- Positions and identification in a separate legend of all fittings with type numbers.

- Size and position of all fixing holes.

- Total weights with and without oil and core lifting height and weight.

- Detail dimensioned drawings of tapping switch illustrating type of material, clearances, between tapping points and to earth and method of operation.

- Detailed dimensioned drawing of bushings, silica gel or plain oil seal type breather and conservator.

Note:	Where sealed transformers are offered, a cross arrangement drawing shall be submitted with the Bid showing, in particular, details of the tank construction and internal tank finish and the dept of the expansion space above the oil.

#### With Contract

- Latest issues of the drawings listed shall be supplied under the contract; if no modifications are applicable to the drawings supplied with the Bid, this shall be confirmed in writing under the contract and further drawings need not be supplied

PARTICULAR TECHNICAL SPECIFICATIONS, TELECOMMUNICATIONS

SECTION V CONTENT

5 PARTICULAR TECHNICAL SPECIFICATIONS, TELECOMMUNICATIONS	257

5.1 Description	257

5.1.1 General	257

5.1.2 Optical Fibre Equipment	257

5.2 General Telecommunication Requirements	259

5.2.1 Bid Documentation	260

5.2.2 Documents to be provided after Award of Contract and minimum 30 days before shipment.	260

5.3 Particular Requirements for the Optical Line Terminal Equipment and Access Multiplexers at new and existing Project areas Substations.	261

5.3.1 General	261

5.3.2 Fibre Optical Terminal Equipment/Multiplexer Units	261

5.3.3 Delivery	261

5.3.4 Functional Requirements:	262

5.3.5 Design Tests, Factory Assembly and Factory Acceptance Tests (FAT)	263

5.3.5.1 Installation	264

5.3.5.2 Field Acceptance Tests	264

5.3.5.3 Data and Documentation Requirements	264

# PARTICULAR TECHNICAL SPECIFICATIONS, TELECOMMUNICATIONS

## Description

### General

This chapter describes the existing transmission system telecommunication equipment and describes and specifies all new telecommunication equipment to be supplied.

ZESCO operates a vast private telecommunications network. Additionally, ZESCO has a commercial license to lease excess capacity on the network. ZESCO’s existing telecommunication systems consists of an optical fibre network, microwave radio network, VHF mobile and fixed radio systems and Power Line Carrier (PLC) equipment. In addition, ZESCO leases some dedicated lines from ZAMTEL where the ZESCO network is not available.

The PLC equipment and associated equipment are installed in the respective substations and mainly on the 66kV to 330kV lines.

The optical network is based on SDH and DWDM transmission technologies and covers all the 330 and 220 kV power networks from Kaoma in the Western province to Lumwana in the Northwest through Mongu, Sesheke, Livingstone, Lusaka and the Copperbelt. There is also a link from Lusaka to Kafue Gorge and Kariba North, the two big power stations. From Kabwe Step Down substation through Serenje, the fibre network extends farther to Luapula, Northern, Muchinga and Eastern provinces. The DWDM OTN network forms the main communication backbone while the SDH and PCM form the Edge and access networks. The optical fibre cables used are mainly based on Optical Ground Wire (OPGW) but All Dielectric Self Supporting (ADSS) fibres are also used on 33kV, 11kV and 400V distribution lines.

The fixed radio network based on microwave covers the area from Kariba in the South to Luano in the north on the Copperbelt. The microwave radios are also used in the access links from the optical fibre network. Additionally, ZESCO also operates a country-wide mobile radio network based on VHF and HF that is used purely for internal operations.

### Optical Fibre Equipment

Under the Optical Fibre Projects of 2006, 2011 and completed in 2013 in phases one, two and three respectively, a high-capacity optical network was implemented on the 330 and 220 kV power networks covering all the ten provinces of Zambia.

The optical fibres cables used are mainly based on Optical Pilot Ground Wire (OPGW) but All Dielectric Self Supporting (ADSS) fibres are also used on 11 and 33 kV distribution lines.

The optical transmission equipment is based on SDH and DWDM OTN technologies and was supplied by ZTE Corporation of China. The equipment type is called ZXMP S385 and ZXMP M920 for SDH and DWDM respectively. The network has multiservice transport capabilities. The installed backbone OTN transmission capacity is 400 Gbps with 40 channel DWDM terminal and add-and-insert optical multiplexers.

The telecommunications infrastructure has been an integral part of ZESCO systems since the company was established. The purpose of having a telecommunication infrastructure in a power company is to ensure that the provision of electricity from the point of generation to the point of supply to the customers is done efficiently, reliably, and safely. This is done by offering telecommunications services and network facilities for voice, control, protection, and various information systems as follows:

- Operations and Business voice communication

- Supervisory Control and Data Acquisition (SCADA)

- Tele-protection (High Voltage Line differential, permissive and direct protection)

- Tele-metering (measurands)

- Access Control and remote surveillance of key installations (CCTV).

- Video conferencing system (VCS) for remote interactive meetings.

- Vehicle tracking system (VTS).

- Enhanced corporate connectivity for information systems like Business Information Systems (BIS), email, internet etc.

Tasked with the responsibility of offering the services listed above, ZESCO has implemented the following telecommunication networks:

- Telephone network

- High voltage Power Line carrier network

- Mobile Radio Network

- Fixed Radio Network

- Video Conferencing Network.

- Access Control and CCTV Network

- Optical Fibre Network

Due to the extensive telecommunications network with excess capacity especially on the optical fibre network, ZESCO management made a corporate decision to diversify into the provisioning of commercial telecommunication services to the ICT industry. The commercial activities started on a small scale on the microwave radio network in 2003. When the optical fibre network was implemented in 2007, full scale telecommunications business operations commenced with the acquisition of a telecommunications licence from the communications authority (ZICTA) in the wholesale category of Carrier of Carriers.

## General Telecommunication Requirements

This specification covers the technical and associated requirements for the telecommunication equipment including all various equipment and devices. Functional details as well as technical standard levels are stated in this section. However, it is not ZESCO’s intent to specify all detailed requirements, which will be parts of manufacturer's product excellence. The Bidder shall furnish equipment meeting the requirements of this specification and the industry standards.

The bidder shall bear full responsibility for the designed and manufactured of the systems and all equipment in accordance with all codes, standards and applicable government regulations to perform under the conditions and standards specified herein.

All materials and parts which are not specifically mentioned herein but are necessary for the proper purchase, erection, and safe operation of the equipment shall be identified by the Bidder and furnished at no increase in cost to ZESCO.

No departure shall be made from this specification and standards unless waived or modified in writing by ZESCO. The Contractor shall obtain from its subcontractors a statement of compliance with this specification without exception and/or if there are any exception or deviation these shall be described in detail and included in the Bidder’s proposal.  Bidders shall add a statement that no other exceptions are taken to this specification.

The construction of the different parts of the supply must be as standard as possible in order to reduce to a minimum the spare parts and to make the maintenance and replacement operation easy. All equipment proposed shall comply with but not limited to the IEC, ITU-T and ITU-R standards, including all addenda, in effect at time of purchase order unless otherwise stated. In addition to the codes and standards, the Contractor shall comply with applicable national and local laws, codes, regulations, statutes and ordinances.

It is the intent of this specification to allow the supply of equipment according to the standard listed. If the Bidder, due to any reason, deviates from the standards, he shall describe the equivalence and/or differences of such standards with his bid.  In any event, the Bidder shall list all those standards he proposes to use in the supply of the specified equipment.

The construction of the different parts of the supply must be as standard as possible in order to reduce to a minimum the spare parts and to make the maintenance and replacement operation easy.

Further reference is made to the figures.

### Bid Documentation

The following documentation shall be furnished together with the bid as a minimum:

- Relevant specifications stated in the General Technical Specifications

- Filled-in-technical data of Section Technical Schedules.

- Preliminary general assembly drawings indicating approximate overall dimensions, cable entrance, weights, nameplates, location of accessories, plans and section views, mounting and other details and clearances needed for operation and maintenance.

- Brochures and Catalogues

- Typical installation instructions

- Reference lists

- A statement that for all equipment where type tests have been requested, these have been performed successfully and with it a summary of type test reports.

- A list of recommended spare parts with specification of availability and location of permanently stocked by supplier.

- Proposed time schedule to meet delivery date.

- List of codes and particular abbreviations used.

### Documents to be provided after Award of Contract and minimum 30 days before shipment.

- Relevant specifications stated in the General Technical Specifications

- Complete shipping and assembly drawings showing the Contractor’s identification, plans, elevation and section view, mounting dimensions and details, weights and cable entrance openings.

- Shipping details including its weights, sizes and shipping containers.

- Certified test reports

- Bill of material and parts list of identifying sketch showing components

- Final arrangement drawings showing the layout and information for design of foundation details, overall dimensions of all equipment with details of external cable entry height and clearance, including weights and showing all necessary details as listed below:

- Updated systems drawings

- All cabinet floor mounting details.

- Detailed material list

- Detailed functional diagram

- General assembly and erection/installation drawings and procedures

- Test reports

- List of drawings and schedule of submittal

## Particular Requirements for the Optical Line Terminal Equipment and Access Multiplexers at new and existing Project areas Substations.

### General

At substations, the connection to terminal towers from the substation gantry for one of the aerial earths of transmission lines shall be the composite earth wire called Optical Pilot Ground Wire (OPGW). From the OPGW termination boxes on the substation gantries, there shall be optical approach cable linking the Optical Distribution Frame and the OPGW. The scope of supply of this contract shall include the fibre optical terminal equipment. This will carry data, voice, SCADA and protection signalling communications. There shall be in-out looping of optical fibre with respective terminal equipment for OPGW at all transmission voltage levels.

### Fibre Optical Terminal Equipment/Multiplexer Units

The optical terminal equipment shall have redundant communication features with automatic protection switching using 2-fibre pairs The Bidder shall endeavour to supply multiplexers similar (brown field projects) or of superior versions to the ones already installed on the ZESCO network through other projects. The bidder shall also provide three (3) separate access multiplexers based on Pulse Code Modulation (PCM) for provisioning of user services like telephony, SCADA and low speed data units. The bidder shall also supply PCM multiplexers of make and type as the ones already installed on the ZESCO network. Two types of PCM multiplexers are in use in our network. These are the FOX series from ABB and the ZXMP P230 from ZTE.

### Delivery

      - Optical Transport Network (OTN) equipment with the following characteristics/requirements

- Not less than 4000G of transmission capacity in all configurable directions.

- The equipment must be able to transmits for distances of over 300km without any signal degradation.

- The equipment must have cross connection capabilities.

- Must be open for integration and monitoring on the already operational ZTE Network Management System (NMS)

- The equipment must be linked to the already operational ZXONE9700 equipment at the substation

- Service interface modules:

        - 2 x 155M – 2.5G Modules/Cards

        - 2 x 10G Modules/Cards

        - 3 x 100G Modules/Cards

      - Packet Transport Network (PTN) equipment with the following characteristics/requirements:

- Transmission rate of 10G to 100G

- Supply voltage of -48VDC

- Supported interfaces/rates of 2Mbps, 100Mbps, 155Mbps, GE, 10G and 100G

- Line and Service Interface modules

- 3 x 100G

- 2 x 12 ports 10G module

- 4 x 16 ports GE module

- 1 x 4 port STM-1

- 1 x 63 TDM E1 processing module

      - Synchronous Digital Hierarchy (SDH) multiplexer with STM-64 optical transmission capacity each and the following interfaces:

- Optical Transmission Modules:

- 2 x 2 ports STM-64

- 4 x 4 ports STM-16

- Service Interfaces:

- 63 x E1 ports

- 2 x 8 ports STM-1

- 8 x 100 Base TX ports (Fast Ethernet - Electrical)

- 8 x 100 Base FX ports (Fast Ethernet – Optical)

- 2 x Gigabit Ethernet ports x 4 control modules

- Engineer’s Order Wire

      - DC Power System (Charger and Batteries) with the following characteristics/requirements:

- Three phase AC input

- Modular charger type

- Single phase input voltage range between 140V – 280V

- Input Current range between 6A – 600A

- Output DC voltage range between 42V – 58V

- Output high-off voltage range between 58V – 62V

- Lithium battery type

- Battery rating of 48VDC, 100Ahr

- Able to handle 16 x 48VDC, 100Ahr Lithium batteries

- Must be open for integration and monitoring on the already operational ZTE Power Management System (PMS)

      - Private Automatic Branch Exchange (PABX)

The contractor shall supply, test, install, commission, and integrate an ALCATEL PABX modern exchange which will be used for internal calls and also for external calls to the public switched telephone network.

Therefore, the exchange shall have interconnections to the Public switched telephone network and interlinked to the ZESCO PABX system network. To link to ZESCO PABX network, the system to be supplied shall be compatible and be able to work seamlessly with the head office PCX (Alcatel OmniPCX enterprise 4400) using H.323, SIP, SS7, ABC-F signaling protocol and IXP 3000 (Harris) in the telephone network using Q-SIG protocol.  VoIP connections will be necessary for the extension of telephony services to offices that are in a different locality from where the exchange will be placed.

The supplier shall be wholly responsible for the engineering, design, installation and commissioning of the whole telephone system.

      - PCM access multiplexers for telephony, SCADA and low speed data each unit shall have the following interfaces:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

      - Local craft terminal (Personnel/Laptop) Computers with minimum management system features as;

(1) Windows 10 operating software, (2) RAM of not less than 16.0GB (3) 64-bit operating system (4) Core i7 processor @ 2.30G (5) 1TB or better (6) Touch screen.  based on Windows. This will be pre-installed with management software for the OTN, PTN SDH, PABX and PCM access multiplexers and shall be in English.

      - Network Test Equipment

- Optical fibre splicing machine

- Optical Time Domain Reflectometer

- Optical power meter

- Optical light source

- Optical visual fault locator

      - Free standing and split type air conditioning units in telecoms rooms

      - FOX615 multiplexer for tele-protection with the following characteristics/requirements:

- Two (02) CESM1 cards

- Two (02) SAMO2 (With SFPs STM-16)

- Two (2) SAMO1 (STM-1 and STM-4)

- LEDS1

- LESU1 (1)

- LEXI1 (3)

- LEDE1

- 1 x 4 Port OPIC (With Multi Mode SFP’s)

- 1 x 4 Port OPIC (With Single Mode SFP’s)

- TEPI

- FAMO

- ETOP (optic single mode 8 SFPs and 4 electrical SFPs)

PCM access multiplexers for telephony, SCADA and low speed data each unit shall have the following interfaces:

- 8 ports for 2 wire subscriber lines

- 4 ports for RS-232 (or V24/ V28) data channels

- 4 ports for 64 kbps G.703 co-directional channels.

- 4 ports for 2 Mbps G.703 (E1) channels.

- 2 Ethernet ports

- IP-PABX switchboards at all substations.

- Local craft terminal (Personnel Computer) with management system based on Windows XP Professional or higher. This will be pre-installed with management software for both the SDH and PCM access multiplexers and shall be in English.

### Functional Requirements:

- SDH based optical line equipment:

- Fibre Type: Standard Single mode fibre (G.652.D)

- Operating Wavelength:	1310 and 1550 nm

- Transmitter Module: Laser

- Optical Transmission Procedure: According to ITU-T Rec G.957

- The frame structure of STM-16 and STM-1 including the payload and Section Over Head bytes shall be as per ITU-T Rec.G.707.

- The transmission equipment shall be flexible enough to operate in the following configurations:

  - Terminal Multiplexer (TM);

  - Add / Drop multiplexer (ADM).

- In TM and ADM configuration, it shall support the following types of payloads:

- STM-4;

- STM-1 (optical and electrical);

- E3;

- E1;

• Ethernet at 100 Base Tx and 100 Base FX;

- The optical line equipment shall have 1+1 protection for all optical interfaces.

- The equipment shall have Engineers Order Wire (EOW) using the E1 and E2 bytes with telephone handsets.

- Network Element management system with the following:

- Based in English Language.

- Faults Management.

- Configuration capabilities.

- Performance Monitoring.

- Security management.

- PCM Access Multiplexer

- The PCM equipment will be connected to the SDH equipment through E1 interfaces.

- The PCM multiplexer shall support the following interfaces:

- E1.

- 64 kbps (G.703).

- V.24/V.28 (RS 232);

- 2 wire Telephony Subscriber Interfaces.

- 2/4 wire 600 Ohm Voice Frequency Telegraph Interfaces.

- Ethernet interface.

- Complete 48V DC Charger and battery Power supply per substation

### Design Tests, Factory Assembly and Factory Acceptance Tests (FAT)

The optical fibre terminal equipment shall be completely assembled and adjusted at the factory and given the manufacturer’s routine FAT and also other tests required. All parts shall be properly marked for ease of assembly in the field. All routine and/or FAT’s required shall be witnessed by ZESCO. No equipment shall be shipped until released for shipment by ZESCO.

Test equipment, test methods, measurements and computations shall be in accordance with the latest applicable requirements of appropriate standards except in cases where otherwise set forth and shall be subject to the approval of The Project Manager.  The Contractor shall make the preparation for tests and provide the apparatus and personnel and shall notify ZESCO about the date of tests at least 30 days in advance.

The design tests shall conform to applicable IEC, ITU or IEEE standards. However, performance of actual design tests may be omitted, if previous design test records for an identical unit duly witnessed and certified by a third party can be furnished. The Bidder shall submit with his Bid, certified copies of the results of type tests on each type of equipment to be supplied meeting the requirements of applicable IEC standards to show the adequacy of its design.

For the FAT, the test protocol shall be proposed by the Contractor and submitted to The Project Manager for approval at least 30 days before the date of test. As a minimum the tests noted below shall be performed during the FAT:

For the SDH Optical Mux Equipment:

- Complete test of the functional operation of the equipment

- Construction, Appearance and Mechanical Inspections

ZESCO will finalise the report of FAT performed within 15 days after the FAT. The Contractor and ZESCO shall sign the FAT report as part of the Contract.

If any equipment fails to pass any test, it shall be reported in the test report. All equipment with any defect shall be repaired, with defective parts replaced, and the equipment shall then be re-tested without any additional cost to ZESCO and without extension of time.

If part of equipment or function defects is considerable, according to the Project Managers point of view, the FAT will not be approved.  In this case the FAT shall be repeated without any additional cost to ZESCO and without influence of the delivery schedule.

The Contractor shall bear his part of all FAT costs.

-TRAINING

Training for 5 telecomms engineers for a period of not less than 15 working days for  EACH  TELECOMMS EQUIPMENT,i.e OTN,PTN,FOX and DC SYSTEM at perdium of $365/day /person

#### Installation

The complete installation work is the Contractor’s responsibility. However, as part of on-the-job training and technology transfer, the Contractor shall hand over major parts of the installation work to ZESCO under the Contractor’s supervision. The Contractor shall provide the services of a competent field supervisor to ZESCO’s staff during installation and commissioning where required.

#### Field Acceptance Tests

Field acceptance test shall be part of the commissioning. The Contractor shall provide instructions and propose acceptance test criteria for field testing prior to commissioning the optical line terminal equipment.

#### Data and Documentation Requirements

Contractor furnished data and information shall be the guaranteed performance data, predicted performance, interface requirements and construction features of all furnished equipment. The accuracy of such information and its compatibility with overall performance requirements specified are the sole responsibility of the Contractor.  All information submitted would become part of contract data for successful Bidder.

TECHINCAL SCHEDULES

SECTION VI CONTENT

6 TECHINCAL SCHEDULES	269

6.1 PREAMBLE	269

6.2 SUMMARY SCHEDULE OF EQUIPMENT MANUFACTURERS	270

6.3 330kV SWITCHGEAR AND EQUIPMENT TECHNICAL GUARANTEES	272

6.3.1 GTP: 330kV CIRCUIT BREAKERS	272

6.3.2 GTP: 330KV DISCONNECTORS	277

6.3.3 GTP: 330KV OIL FILLED POST MOUNTED CURRENT TRANSFORMERS	279

6.3.4 GTP: 330KV CAPACITIVE VOLTAGE TRANSFORMERS	281

6.3.5 GTP: 330KV SURGE ARRESTORS	283

6.3.6 SCHEDULE OF INFORMATIVE DATA ON HARDWARE, FITTINGS AND ACCESSORIES	285

6.4 132kV SWITCHGEAR EQUIPMENT TECHNICAL GUARANTEES	289

6.4.1 132kV SF6 CIRCUIT BREAKER	289

6.4.2 132KV DISCONNECTOR	294

6.4.3 132KV OIL FILLED POST MOUNTED CURRENT TRANSFORMERS	296

6.4.4 132KV CAPACITIVE VOLTAGE TRANSFORMERS	298

6.4.5 132kV SWITCHGEAR AND EQUIPMENT SCHEDULE OF INFORMATIVE DATA	300

6.4.6 132 kV SWITCHGEAR SCHEDULE 2b INFORMATIVE DATA	301

6.4.7 33KV CIRCUIT BREAKERS	302

6.4.8 33KV DISCONNECTOR	306

6.4.9 33KV CURRENT TRANSFORMERS	310

6.4.10 33KV CAPACITIVE VOLTAGE TRANSFORMERS	311

6.4.11 33KV SURGE ARRESTERS	312

6.4.12 11KV INCOMER CIRCUIT BREAKER TECHNICAL SCHEDULE	314

6.4.13 11KV OUTGOING CIRCUIT BREAKER TECHNICAL SCHEDULE	316

6.4.14 11KV SURGE ARRESTERS	318

6.4.15 LOW VOLTAGE A.C. SWITCHBOARDS SCHEDULE 4a TECHNICAL GUARANTEES	321

6.4.16 SCHEDULE 3a TECHNICAL GUARANTEES	322

6.4.17 LOW VOLTAGE A.C. SWITCHBOARDS SCHEDULE 4b INFORMATIVE DATA	323

6.5 SPECIFICATION FOR SUBSTATION DC BATTERY BANK	324

6.5.1 GENERAL DESCRIPTION	324

6.5.2 STANDARDS	324

6.5.3 DESIGN	324

6.5.4 ZESCO MINIMUM TECHNICAL REQUIREMENTS FOR DC BATTERY BANK	325

6.5.4.1 SPECIFICATION FOR 110V DC, 50A BATTERY CHARGER	326

6.5.4.2 DC SUPPLY SCHEDULE 5a TECHNICAL GUARANTEES (additional)	328

6.5.4.3 SCHEDULE 5a TECHNICAL GUARANTEES	328

6.5.4.4 DC SUPPLY SCHEDULE 5b INFORMATIVE DATA	330

6.5.4.5 SCHEDULE 5b INFORMATIVE DATA	331

6.5.5 METERING TECHNICAL GUARANTEES	332

6.5.5.1 Meter Specifications	332

6.5.5.2 Panel Specifications	336

6.5.5.3 Meter enclosure	338

6.5.5.4 Metering Workstation	339

6.6 POWER CABLES, CONTROL CABLES, CABLE RACKS SCHEDULE	340

6.6.1 TECHNICAL GUARANTEES Sheet 1 of 1	340

6.6.2 8b INFORMATIVE DATA Sheet 1 of 2	341

6.6.3 8b INFORMATIVE DATA Sheet 2 of 2	342

6.7 EARTHING SYSTEM	343

6.7.1 SCHEDULE 9a TECHNICAL GUARANTEES Sheet 1 of 1	343

6.7.2 SCHEDULE VI-V-9 b INFORMATIVE DATA Sheet 1 of 1	344

6.8 HV POWER TRANSFORMERS SCHEDULES TECHNICAL GUARANTEES	345

6.8.1 250MVA 330/132/11kV TRANSFORMERS TECHNICAL GUARANTEES	345

6.8.2 63MVA 132/88/33KV TRANSFORMERS	361

6.8.3 90MVA 132/33/11KV TRANSFORMERS	365

6.8.4 63MVA 132/33/11KV TRANSFORMERS	369

6.8.5 31.5MVA 33/11KV TRANSFORMERS	373

6.9 TECHNICAL SPECIFCATION FOR AUXILIARY TRANSFORMERS	375

6.9.1 Preamble	375

6.9.2 100KVA, 33/0.4 STATION AUXILIARY TRANSFORMER	375

6.9.3 33KV XLPE CABLE TECHNICAL SCHEDULE	377

6.9.4 100KVA, 11/0.4 STATION AUXILIARY TRANSFORMER	378

6.9.5 11KV XLPE CABLE TECHNICAL SCHEDULE	380

6.10 TECHNICAL SCHEDULE FOR CONTROL PANELS	381

6.11 TECHNICAL SCHEDULE FOR ELECTRONIC MULTIFUNCTIONAL ENERGY AND DEMAND METERS	382

6.12 TECHNICAL SCHEDULE FOR METERING AND PROTECTION	383

6.12.1 Control and Supply Circuits	383

6.13 PROTECTION TECHNICAL SCHEDULES	384

6.13.1 LINE DISTANCE PROTECTION RELAYS SCHEDULE 13a – INFORMATIVE DATA	384

6.13.2 SCHEDULE 13b - INFORMATIVE DATA BACK UP PROTECTION RELAYS	389

6.13.3 TRANSFORMER DIFFERENTIAL PROTECTION RELAYS SCHEDULE 13c - INFORMATIVE DATA	398

6.14 TELECOMMUNICATION EQUIPMENT TECHNICAL SCHEDULES	403

6.14.1 FIBRE OPTIC TERMINAL EQUIPMENT SDH MULTIPLEXER	403

6.14.2 SPECIFICATIONS FOR PABX SYSTEM	406

6.14.3 PABX TECHNICAL SCHEDULE	407

6.14.4 SCHEDULE FOR OPTIC FIBRE CABLE	441

6.14.4.1 Approach Cable Attributes:	441

6.14.4.2 OPGW Cable Characteristics	442

6.14.4.2.1 Cable Structure	442

6.14.4.2.2 OPGW Cable Mechanical/Electrical characteristics	443

6.14.4.2.3 OPGW/Approach cables Optical Characteristics	444

6.14.4.2.4 NORMATIVE REFERENCE	445

6.14.4.2.4.1 Optical Characteristics	445

6.14.4.2.4.2 Mechanical Characteristics of the Fibre Cores	445

6.14.4.2.4.3 Mechanical Characteristics of the Cable	445

6.14.4.2.4.4 Color Coding	445

# TECHINCAL SCHEDULES

## PREAMBLE

    - The Technical Schedules shall be filled in and completed by the Bidder and submitted with the Bid.

    - All documentation necessary to evaluate whether the equipment offered is in accordance with this Specification shall be submitted with the Bid.

    - All data entered in the Schedules of Technical Guarantees are guaranteed values by the Bidder and cannot be departed from whatsoever.

    - All data entered in the Schedules of Informative Data are also guaranteed values by the Bidder.  These data may only be altered following the Project Manager's written consent.

    - All standard accessories, including those not indicated in this specification, shall be furnished.  The detailed work to be performed by ZESCO or by the Contractor shall be as below stated.

## SUMMARY SCHEDULE OF EQUIPMENT MANUFACTURERS

| Item Description | Manufacturer | Country of Manufacture | Place of Inspection |
| --- | --- | --- | --- |
| OUTDOOR EQUIPMENT |  |  |  |
| 125/160 MVA (ONAF/ONAN) 330/132/11kV transformer |  |  |  |
| 31.5/40MVA (ONAF/ONAN) 132/33kV transformer |  |  |  |
| 31.5/40 MVA (ONAF/ONAN) 132/11kV transformer |  |  |  |
| 25/31.5 MVA (ONAF/ONAN) 33/11kV transformer |  |  |  |
| 10/12.5 MVA (ONAF/ONAN) 33/11kV transformer |  |  |  |
| 100kVA, 11/0.4kV auxiliary transformers |  |  |  |
| 100kVA, 33/0.4kV auxiliary transformers |  |  |  |
| 330kV circuit breakers |  |  |  |
| 330kV disconnectors |  |  |  |
| 330kV current transformers |  |  |  |
| 330kV capacitor voltage transformers |  |  |  |
| 330kV surge arrestors |  |  |  |
| 132kV circuit breakers |  |  |  |
| 132kV disconnectors |  |  |  |
| 132kV current transformers |  |  |  |
| 132kV capacitor voltage transformers |  |  |  |
| 132kV surge arrestors |  |  |  |
| 33kV Circuit breakers |  |  |  |
| 33kV current transformers |  |  |  |
| 33kV voltage transformers |  |  |  |
| 33kV disconnectors |  |  |  |
| 33kV surge arrestors |  |  |  |
| 11kV Switchgear panels |  |  |  |
| 11kV and 33kV Transformer earthing resistor banks. |  |  |  |
| Protection relay equipment and panels |  |  |  |
| Substation control/automation system |  |  |  |
| Telecommunication terminal equipment and panels |  |  |  |
| OPGW approach cable |  |  |  |
| 110V DC system + DBs |  |  |  |
| LTAC DBs |  |  |  |
| Insulator, hardware fittings and connectors |  |  |  |
| Multicore control cables |  |  |  |
| 11kV surge arresters |  |  |  |
| 400V Pole Fuse cartridge |  |  |  |

## 330kV SWITCHGEAR AND EQUIPMENT TECHNICAL GUARANTEES

### GTP: 330kV CIRCUIT BREAKERS

| S/NO. | PARAMETER DESCRIPTION FOR 330KV CIRCUIT BREAKER | UNIT | TECHNICAL GUARANTEE DATA |  |
| --- | --- | --- | --- | --- |
|  |  |  | SCHEDULE A: MIN. REQUIREMENTS | SCHEDULE B: BIDDER GUARANTEE |
|  |  |  | 330kV SF6 outdoor circuit Breaker; 3 phases |  |
| 1. | Scope: Design, manufacture, testing, supply & installation. |  | Yes |  |
| 2. Design & Construction |  |  |  |  |
| 2.1 | Type designation |  | Bidder to Indicate |  |
| 2.2 | Reference Standard |  | IEC 62271-100 IEC 62271-1 |  |
| 2.3 | No. of poles/circuit breaker |  | 3 |  |
| 2.3.1 | No. of interrupters/pole |  | 2 |  |
| 2.4 | Type of control mechanism |  | Motor operated spring |  |
| 2.4.1 | Mechanical class |  | M2 |  |
| 2.5 | Protection level of electrical cubicle |  | IP54 |  |
| 2.6 | Protection level of operating mechanism |  | IP55 |  |
| 2.7 | Type of insulator |  | Porcelain or silicone rubber |  |
| 2.8 | Insulating gas |  | SF6 |  |
| 2.9 | Rated absolute pressure at 20oC |  | Bidder to indicate |  |
| 2.10 | Relative leakage rate | %/yr | ˂0,5% |  |
| 2.11 | Circuit breaker class |  | Outdoor |  |
| 2.12 | Support structures supplied |  | Yes |  |
| 3. Service Conditions |  |  |  |  |
| 3.1 | Altitude of installation (a.s.l.) | m | 1500 |  |
| 3.2 | Operating ambient temperature | oC | -1 to +48 |  |
| 3.3 | Relative humidity (max) | % | 90 |  |
| 3.4 | Pollution levels | mm/kV | 31 |  |
| 4. Rated Characteristics |  |  |  |  |
| 4.1 | Rated voltage | kV | 330 |  |
| 4.2 | Maximum service voltage | kV | 362 |  |
| 4.3 | Rated frequency | Hz | 50 |  |
| 4.4 | Rated continuous current | A | 3150 |  |
| 4.5 | Rated peak withstand current | kApk | 125 |  |
| 4.6 | Rated short time withstand current | kA | 50 |  |
| 4.7 | Rated duration of short circuit | s | 3 |  |
| 4.8 | One min. power frequency withstand voltage: |  |  |  |
|  | phase to earth | kV | 450 |  |
|  | Across open contacts | kV | 520 |  |
| 4.9 | Rated lightning impulse withstand voltage: |  |  |  |
|  | phase to earth | kVpk | 1175 |  |
|  | across open contacts | kVpk | 1175(+205) |  |
| 4.10 | Rated switching impulse withstand voltage: |  |  |  |
|  | phase to earth | kVpk | 950 |  |
|  | across open contacts | kVpk | 800(+295) |  |
| 5. Breaking and Making Characteristics |  |  |  |  |
| 5.1 | Rated short circuit breaking current | kA | 50 |  |
| 5.2 | First pole to clear factor |  | 1.3 |  |
| 5.3 | DC component (% of AC component) | % | 43 |  |
| 5.4 | Peak value of rated short circuit making current | kApk | 125 |  |
| 5.5 | Rated breaking current for short line faults |  | As per IEC Standard |  |
| 5.6 | Rated out of phase breaking current | Id (kA) | 12.5 |  |
| 5.7 | Rated overvoltage factor for unloaded transformers |  | ˂2.5 |  |
| 5.8 | Rated line charging breaking current | A | 255 |  |
| 5.9 | Rated cable charging breaking current |  | 355 |  |
| 6. Operating Times |  |  |  |  |
| 6.1 | Rated opening time – from opening coil energizing to separation of main contacts | ms | ≤25 |  |
| 6.2 | Rated breaking time – from opening coil energizing to arc extinction | ms | ≤45 |  |
| 6.3 | Rated closing time – from closing coil energizing to main contact making | ms | ≤104 |  |
| 6.4 | Rated operating sequence |  | O-0.3s-CO-180s-CO |  |
| 6.5 | Rated operating sequence without motor supply |  | O-CO |  |
| 7. Low Voltage Specification |  |  |  |  |
| 7.1 | Motor voltage | V | 110/220 DC |  |
| 7.2 | Circuit motor protection |  | MCB |  |
| 7.3 | Motor voltage min. range | % | 85 |  |
| 7.4 | Motor voltage max. range | % | 110 |  |
| 7.5 | Opening voltage min. range | % | 65 |  |
| 7.6 | Opening voltage max. range | % | 110 |  |
| 7.7 | Closing voltage min. range | % | 75 |  |
| 7.8 | Closing voltage max. range | % | 110 |  |
| 7.9 | Lighting and heating circuit voltage | V | 220, AC |  |
| 7.10 | Local electrical control with two push button |  | Yes |  |
| 7.11 | Anti-pumping relay |  | Yes |  |
| 7.12 | Local/remote selector switch |  | Yes |  |
| 7.13 | Number of trip coils |  | 2 |  |
| 7.14 | Provision for trip coil supervision |  | Yes |  |
| 7.15 | Pole discrepancy feature |  | Yes |  |
| 7.16 | Signaling contacts for spring position/status |  | Yes, 1NO |  |
|  | Signaling contacts for SF6 gas low, block etc |  | Yes |  |
| 7.17 | Number of available auxiliary NO contacts |  | 8 |  |
| 7.18 | Number of available NC auxiliary contacts |  | 8 |  |
| 7.19 | Position indicator – O/I |  | Yes |  |
| 7.20 | Indicator for spring status |  | Yes |  |
| 7.21 | Gas for first filling plus 20% |  | Yes |  |
| 7.22 | SF6 filling equipment supplied |  | Yes |  |
| 7.23 | SF6 gas leakage detector supplied |  | Yes |  |
| 8. Documents and Drawings with Bid |  |  |  |  |
| 8.1 | Circuit breaker outline drawing |  | Yes |  |
| 8.2 | Foundation detail drawings |  | Yes |  |
| 8.3 | Quality assurance certification |  | Yes |  |
| 8.4 | Typical low voltage elementary diagram included in Bid |  | Yes |  |
| 9. Test Reports with Bid |  |  |  |  |
| 9.1 | Dielectric test |  | Yes |  |
| 9.2 | Temperature rise test |  | Yes |  |
| 9.3 | Short time withstand current test |  | Yes |  |
| 9.4 | Mechanical endurance test |  | Class M2 – 10,000 operations |  |
| 9.5 | Capacitive current breaking test |  | Yes |  |
| 9.6 | Operating times test |  | Yes |  |
| 9.7 | Main contact resistance test |  | Yes |  |

### GTP: 330KV DISCONNECTORS

| S/No. | PARAMETER DESCRIPTION FOR 330KV DISCONNECTOR C/W EARTH SWITCH | UNIT | TECHNICAL GUARANTEE DATA |  |
| --- | --- | --- | --- | --- |
|  |  |  | SCHEDULE A: MIN. REQUIREMENTS | SCHEDULE B: BIDDER GUARANTEE |
| 1 | Rated Voltage | kV | 330 |  |
| 2 | Maximum service voltage | kV | 362 |  |
| 3 | Number of poles |  | 3 |  |
| 4 | Rated frequency | Hz | 50 |  |
| 5 | Rated normal current | A | 3150 |  |
| 6 | Rated short time current for isolator and earth switch | kA | 40 |  |
| 7 | Rated peak withstand current for isolator and earth switch | kApk | 100 |  |
| 8 | Maximum temperature rise of current carrying parts at rated current. - Isolating Switch - Earth Switch | Deg |  |  |
| 9 | One minute power frequency withstand voltage |  |  |  |
|  | To earth and between poles | kVrms | 450 |  |
|  | Across isolating distance | kVrms | 520 |  |
| 10 | Lightning impulse withstand voltage |  |  |  |
|  | To earth and between poles | kVrms | 1175 |  |
|  | Across isolating distance | kVrms | 1175(+205) |  |
| 11 | Switching impulse withstand voltage |  |  |  |
|  | To earth and between poles | kVrms | 950 |  |
|  | Across isolating distance | kVrms | 800(+295) |  |
| 12 | Creepage distance for column | mm/kV | 31 |  |
| 13 | Ambient temperature range | oC | -1 to +48 |  |
| 14 | Relative humidity (max) | % | 90 |  |
| 15 | Altitude above sea level | m | 1500 |  |
| 16 | Operating mechanism type |  | Motor operated, control voltage 110/220V DC |  |
| 17 | Earthing switch operating mechanism |  | Independent manual drive, mechanically interlocked with main blades |  |
| 18 | Type of break |  | Centre rotating horizontal double break |  |
| 19 | Material(s) of contacts |  |  |  |
| 20 | Opening Time | Sec |  |  |
| 21 | Closing Time | Sec |  |  |
| 22 | Bending moment at base of support insulator | kN |  |  |
| 23 | Applicable standard |  | IEC 62271-102 |  |
| 24 | Support structures supplied |  | Yes |  |
| 25 | Isolator outline drawing |  | To be provided with Bid |  |
| 26 | Foundation detail drawings |  | To be provided with Bid |  |
| 27 | Quality assurance certification |  | To be provided with Bid |  |
| 28 | Type tests |  | Bidder to provide previous test certificates/results |  |

### GTP: 330KV OIL FILLED POST MOUNTED CURRENT TRANSFORMERS

| S/N | ITEM DESCRIPTION | UNIT | GUARANTEE VALUE |  |
| --- | --- | --- | --- | --- |
|  | 330KV CT’s |  | ZESCO MIN. REQUIREMENTS | BIDDER TO FILL IN |
| 1 | Type designation |  | Bidder to Indicate |  |
| 2 | Applicable standard |  | IEC 61869 -1 & 2 |  |
| 3 | Nominal Rated voltage | kV | 330 |  |
| 4 | Highest System voltage | kV | 362 |  |
| 5 | Rated frequency | Hz | 50 |  |
| 6 | Power frequency withstand voltage (1 min.) | kVrms | 520 |  |
| 7 | Lightning impulse withstand voltage | kVpk | 1175 |  |
| 8 | Rated continuous current | A | 600-1200/2400 |  |
| 9 | Rated short circuit withstand current (3s) | kA | 40 |  |
| 10 | Short time dynamic rating | kA pk | 100 |  |
| 11 | Ratio, Burden, Class and ALF for Secondary Cores |  |  |  |
| 12 | Current density - In primary winding - In secondary winding | A/mm2 | 0.9 1.3 |  |
| 13 | Core type |  | Ring |  |
| 14 | Core material |  | Oriented steel & nickel |  |
| 15 | 330kV oil filled type: Core 1 Core 2 Core 3 Core 4 Core 5 Core 6 |  |  |  |
|  |  |  | 1200/2400/1, 20VA, 5P20 |  |
|  |  |  | 1200/2400/1, 20VA, 5P20 |  |
|  |  |  | 1200/2400/1, 15VA, 0.2s |  |
|  |  |  | 1200/2400/1, 20VA, PX V≥250Vk, Im≤8mA |  |
|  |  |  | 1200/2400/1, 20VA, PX V≥250Vk, Im≤8mA |  |
|  |  |  | 1200/2400/1, 20VA, PX V≥250Vk, Im≤8mA |  |
| 16 | Temperature rise for continuous full load operation: - In windings - In oil | Deg. | 60 55 |  |
| 17 | Thermal current rating factor |  | 1.2 |  |
| 18 | Permitted static load (primary terminals) | kN | 4000 |  |
| 19 | Permitted dynamic load (primary terminals) | kN | 5600 |  |
| 20 | Creepage distance | kV/mm | 31 |  |
| 21 | Operating Temperature Range | oC | -1 to +48 |  |
| 22 | Altitude of Operation | m | 1500 |  |
| 23 | Humidity (max) | % | 90 |  |
| 24 | Current transformer outline and dimension drawing required |  | Yes |  |
| 25 | Foundation detail drawing required |  | Yes |  |
| 26 | Quality assurance certification required |  | Yes |  |
| 27 | Type tests required |  | Yes |  |

### GTP: 330KV CAPACITIVE VOLTAGE TRANSFORMERS

| S/N | ITEM DESCRIPTION | UNIT | GUARANTEE VALUE |  |
| --- | --- | --- | --- | --- |
|  | 330KV CVT |  | SCHEDULE A: MIN. REQUIREMENTS | SCHEDULE B: BIDDER GUARANTEE |
| 1 | Type Designation |  | Bidder to indicate |  |
| 2 | Applicable Standard |  | IEC 61869- 1 & 5 |  |
| 3 | Rated Primary Voltage | kV | 330 |  |
| 4 | Highest System Voltage | kV | 362 |  |
| 5 | Rated Frequency | Hz | 50 |  |
| 6 | Power Frequency Withstand Voltage (one min.) | kVrms | 520 |  |
| 7 | Lightning Impulse Withstand Voltage, 1.2/50µs | kVpk | 1175 |  |
| 8 | Power Frequency Withstand Voltage Test on Secondary | kVrms | 3 |  |
| 9 | Power Frequency Withstand Voltage Test on HF Terminal | kVrms | 4 |  |
| 10 | Method of transformation |  | Capacitive |  |
| 11 | Capacitance | F | 4500 +10%, -5% |  |
| 12 | Number of Secondary Windings |  | 2 |  |
| 13 | Range of Frequency for Accuracy - Winding I - Winding II |  | 99% - 101% 96% - 102% |  |
| 14 | Rated Voltage Factor |  | 1.2 continuous, 1.5 for 30 sec. |  |
| 15 | Ratio - Winding I - Winding II | V V | 330000/√3: 110/√3 330000/√3: 110/√3 |  |
| 16 | Accuracy and Burden - Winding I - Winding II |  | 0.2s, 100VA 3P, 100VA |  |
| 17 | Damping circuit of reactor provided |  | Yes |  |
| 18 | Creepage Distance | KV/mm | 31 |  |
| 19 | Temperature Range | ℃ | -1 to 48 |  |
| 20 | Altitude of Operation | m | 1500 |  |
| 21 | Humidity (max) | % | 90 |  |
| 22 | Type of Secondary Terminal Blocks |  | Clip on Stud Type |  |
| 23 | Type of Primary Terminal |  | Aluminium – Bar Type |  |
| 24 | CVT outline and dimension drawing provided |  | Yes |  |
| 25 | Support structures provided |  | Yes |  |
| 26 | Foundation detail drawing required |  | Yes |  |
| 27 | Quality assurance certification required |  | Yes |  |
| 28 | Type tests to be provided |  | Yes |  |

### GTP: 330KV SURGE ARRESTORS

| DESCRIPTION |  | UNIT | GUARANTEED VALUES |  |
| --- | --- | --- | --- | --- |
| 330KV SURGE ARRESTERS |  |  | ZESCO MIN. REQUIREMENTS | BIDDER TO FILL IN |
| Type of Surge Arrestor |  |  | Zinc Oxide, gapless Station Class |  |
| Applicable Standard |  |  | IEC 60099-1 - 9 |  |
| System Parameters | Nominal System Voltage | kV | 330 |  |
|  | Maximum System Voltage | kV | 362 |  |
|  | Number of Phases |  | 3 |  |
|  | Type of Earthing |  | Solid |  |
|  | Rated Frequency | Hz | 50 |  |
| Surge Arrestor Characteristics |  |  |  |  |
|  | Nominal Discharge Current | kA | 10 |  |
|  | Arrester rated voltage | kVrms | 258 |  |
|  | Max. Continuous Operating Voltage | kV | 209 |  |
|  | Temporal overvoltage capability, 10s | kVrms | 283 |  |
|  | Line Discharge Class |  | 3 |  |
|  | Max. Residual Voltage with 8/20µs current wave | kVpk | 587 |  |
|  | High Current Discharge Withstand Strength, 4/10µs | kApk | 100 |  |
|  | Construction type |  | Single or two columns |  |
| Accessories | Surge counter with leakage current measurement |  | Yes, must be provided |  |
| Insulation Withstand Voltages |  |  |  |  |
|  | Power Frequency Withstand Voltage | kV | 520 |  |
|  | Lightning Impulse Withstand Voltage | kV | 1175 |  |
|  | Switching Impulse Withstand Voltage | kV | 950 |  |
| Mechanical Strength and Service Conditions |  |  |  |  |
|  | Specified Continuous Load | Nm | 1600 |  |
|  | Creepage Distance | mm/kV | 31 |  |
|  | Type of Housing and Insulating Material |  | Silicone Rubber |  |
|  | Altitude | m | 1500 |  |
|  | Operating Temperature Range | oC | -1 to +48 |  |
|  | Humidity (max) | % | Up to 90% |  |
|  | Type Tests |  | Supplier to Provide Previous Test Certificates/Results |  |
|  | Drawings |  | Supplier to Provide Dimensional Drawings & Mounting Arrangements |  |
|  | Quality Assurance |  | Supplier to Provide Quality Assurance Certificate with Bid |  |

### SCHEDULE OF INFORMATIVE DATA ON HARDWARE, FITTINGS AND ACCESSORIES

| 330 kV SWITCHGEAR AND ACCESSORIES |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | 330 kV |  |
| 1B.1 | Disc Insulators |  |  |  |
|  | - Reference standard |  |  |  |
|  | - Type reference |  |  |  |
|  | - Insulating material |  |  |  |
|  | - Material of socket |  |  |  |
|  | - Material of pin ball |  |  |  |
|  | - Material of cotter pin |  |  |  |
|  | - Number of units per suspension |  |  |  |
|  | - Number of units per tension string |  |  |  |
|  | - Net weight per unit | kg |  |  |
|  | - Weight of suspension string with fittings | kg |  |  |
|  | - Weight of tension string with fittings | kg |  |  |
|  | - Negative 50% impulse flash-over voltage of suspension string | kV |  |  |
|  | - Positive 50% impulse flash-over voltage of suspension string | kV |  |  |
|  | - Negative 50% impulse flash-over voltage of tension string | kV |  |  |
|  | - Positive 50% impulse flash-over voltage of tension string | kV |  |  |
| 1B.2 | Conductors |  |  |  |
|  | - Reference standard |  |  |  |
|  | a. Line bay |  |  |  |
|  | - Type |  |  |  |
|  | - Material |  |  |  |
|  | - Weight | kg/m |  |  |
|  | - Weight of the heaviest reels including conductors | kg |  |  |
|  | - Size of the biggest reel |  |  |  |
|  | - Diameter | mm |  |  |
|  | - Width | mm |  |  |

| 330 kV SWITCHGEAR AND ACCESSORIES |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | 330 kV |  |
|  | b. Transformer bay |  |  |  |
|  | - Type |  |  |  |
|  | - Material |  |  |  |
|  | - Weight | kg/m |  |  |
|  | - Weight of the heaviest reels including conductors | kg |  |  |
|  | - Size of the biggest reel |  |  |  |
|  | - Diameter | mm |  |  |
|  | - Width | mm |  |  |
|  | c. Busbars |  |  |  |
|  | - Type |  |  |  |
|  | - Material |  |  |  |
|  | - Weight | kg/m |  |  |
|  | - Weight of the heaviest reels including conductors | kg |  |  |
|  | - Size of the biggest reel |  |  |  |
|  | - Diameter | mm |  |  |
|  | - Width | mm |  |  |
| b.9 | Overhead Wires (to be the same for all substations) |  |  |  |
|  | - Reference standard |  |  |  |
|  | - Type |  |  |  |
|  | - Material |  |  |  |
|  | - Weight | kg/m |  |  |
|  | - Weight of the heaviest reels including conductors | kg |  |  |
|  | - Size of the biggest reel |  |  |  |
|  | - Diameter | mm |  |  |
|  | - Width | mm |  |  |
| b.10 | Accessories |  |  |  |
|  | - Reference standards |  |  |  |
|  | - Type of accessories |  |  |  |
|  | - |  |  |  |
|  | - Material of accessories used |  |  |  |

## 132kV SWITCHGEAR EQUIPMENT TECHNICAL GUARANTEES

### 132kV SF6 CIRCUIT BREAKER

| S/NO. | PARAMETER DESCRIPTION FOR 132kV CIRCUIT BREAKER | UNIT | TECHNICAL GUARANTEE DATA |  |
| --- | --- | --- | --- | --- |
|  |  |  | SCHEDULE A MIN. REQUIREMENTS | SCHEDULE B BIDDER GUARANTEE |
|  |  |  | 132kV SF6 outdoor circuit Breaker – Ganged Type |  |
| 1 | Scope: Design, manufacture, testing, supply & installation. |  | Yes |  |
| 2 Design & Construction |  |  |  |  |
| 2.1 | Type designation |  | Bidder to Indicate |  |
| 2.2 | Reference Standard |  | IEC 62271-100 IEC 62271-1 |  |
| 2.3 | No. of poles/circuit breaker |  | 3 |  |
| 2.4 | Type of control mechanism |  | Motor operated spring |  |
| 2.4.1 | Mechanical class |  | M2 |  |
| 2.5 | Protection level of electrical cubicle |  | IP54 |  |
| 2.6 | Protection level of operating mechanism |  | IP55 |  |
| 2.7 | Type of insulator |  | silicone rubber |  |
| 2.8 | Insulating gas |  | SF6 |  |
| 2.9 | Rated absolute pressure at 20oC |  | Bidder to indicate |  |
| 2.10 | Relative leakage rate | %/yr | ˂0,5% |  |
| 2.11 | Circuit breaker class |  | Outdoor |  |
| 2.12 | Support structures supplied |  | Yes |  |
| 3 Service Conditions |  |  |  |  |
| 3.1 | Altitude of installation (a.s.l.) | m | 1500 |  |
| 3.2 | Operating ambient temperature | oC | -1 to +48 |  |
| 3.3 | Relative humidity (max) | % | 90 |  |
| 3.4 | Pollution levels | mm/kV | 31 |  |
| 4 Rated Characteristics |  |  |  |  |
| 4.1 | Rated voltage | kV | 132 |  |
| 4.2 | Maximum service voltage | kV | 145 |  |
| 4.3 | Rated frequency | Hz | 50 |  |
| 4.4 | Rated continuous current | A | 3150 |  |
| 4.5 | Rated peak withstand current | kApk | 100 |  |
| 4.6 | Rated short time withstand current | kA | 40 |  |
| 4.7 | Rated duration of short circuit | s | 3 |  |
| 4.8 | One min. power frequency withstand voltage: |  |  |  |
|  | phase to earth | kV | 275 |  |
|  | Across open contacts | kV | 275 |  |
| 4.9 | Rated lightning impulse withstand voltage: |  |  |  |
|  | phase to earth | kVpk | 650 |  |
|  | across open contacts | kVpk | 650 |  |
| 4.10 | Rated switching impulse withstand voltage: |  |  |  |
|  | phase to earth | kVpk | n/a |  |
|  | across open contacts | kVpk | n/a |  |
| 5. Breaking and Making Characteristics |  |  |  |  |
| 5.1 | Rated short circuit breaking current | kA | 40 |  |
| 5.2 | First pole to clear factor |  | 1.5 |  |
| 5.3 | DC component (% of AC component) | % | 45 |  |
| 5.4 | Peak value of rated short circuit making current | kApk | 100 |  |
| 5.5 | Rated breaking current for short line faults |  | As per IEC Standard |  |
| 5.6 | Rated out of phase breaking current | Id (kA) | 10 |  |
| 5.7 | Rated overvoltage factor for unloaded transformers |  | ˂2.5 |  |
| 5.8 | Rated line charging breaking current | A | 50 |  |
| 5.9 | Rated cable charging breaking current |  | 160 |  |
| 6. Operating Times |  |  |  |  |
| 6.1 | Rated opening time – from opening coil energizing to separation of main contacts | ms | ≤28 |  |
| 6.2 | Rated breaking time – from opening coil energizing to arc extinction | ms | ≤50 |  |
| 6.3 | Rated closing time – from closing coil energizing to main contact making | ms | ≤70 |  |
| 6.4 | Rated operating sequence |  | O-0.3s-CO-180s-CO |  |
| 6.5 | Rated operating sequence without motor supply |  | O-CO |  |
| 7 Low Voltage Specification |  |  |  |  |
| 7.1 | Motor voltage | V | 110/220 DC |  |
| 7.2 | Circuit motor protection |  | MCB |  |
| 7.3 | Motor voltage min. range | % | 85 |  |
| 7.4 | Motor voltage max. range | % | 110 |  |
| 7.5 | Opening voltage min. range | % | 65 |  |
| 7.6 | Opening voltage max. range | % | 110 |  |
| 7.7 | Closing voltage min. range | % | 75 |  |
| 7.8 | Closing voltage max. range | % | 110 |  |
| 7.9 | Lighting and heating circuit voltage | V | 220, AC |  |
| 7.10 | Local electrical control with two push buttons |  | Yes |  |
| 7.11 | Anti-pumping relay |  | Yes |  |
| 7.12 | Local/remote selector switch |  | Yes |  |
| 7.13 | Number of trip coils |  | 2 |  |
| 7.14 | Provision for trip coil supervision |  | Yes |  |
| 7.15 | Pole discrepancy feature |  | n/a |  |
| 7.16 | Signaling contacts for spring position/status |  | Yes, 1NO |  |
|  | Signaling contacts for SF6 gas low, block etc |  | Yes |  |
| 7.17 | Number of available auxiliary NO contacts |  | 8 |  |
| 7.18 | Number of available NC auxiliary contacts |  | 8 |  |
| 7.19 | Position indicator – O/I |  | Yes |  |
| 7.20 | Indicator for spring status |  | Yes |  |
| 7.21 | Gas for first filling plus 30% |  | Yes |  |
| 7.22 | SF6 filling equipment supplied |  | Yes |  |
| 7.23 | SF6 gas leakage detector supplied |  | Yes |  |
| 8 Documents and Drawings with Bid |  |  |  |  |
| 8.1 | Circuit breaker outline drawing |  | Yes |  |
| 8.2 | Foundation detail drawings |  | Yes |  |
| 8.3 | Quality assurance certification |  | Yes |  |
| 8.4 | Typical low voltage elementary diagram included in Bid |  | Yes |  |
| 9 Test Reports with Bid |  |  |  |  |
| 9.1 | Dielectric test |  | Yes |  |
| 9.2 | Temperature rise test |  | Yes |  |
| 9.3 | Short time withstand current test |  | Yes |  |
| 9.4 | Mechanical endurance test |  | Class M2 – 10,000 operations |  |
| 9.5 | Capacitive current breaking test |  | Yes |  |
| 9.6 | Operating times test |  | Yes |  |
| 9.7 | Main contact resistance test |  | Yes |  |

### 132KV DISCONNECTOR

| S/No. | PARAMETER DESCRIPTION FOR 132KV DISCONNECTOR C/W EARTH SWITCH | UNIT | TECHNICAL GUARANTEE DATA |  |
| --- | --- | --- | --- | --- |
|  |  |  | SCHEDULE A: MIN. REQUIREMENTS | SCHEDULE B: BIDDER GUARANTEE |
| 1 | Rated Voltage | kV | 132 |  |
| 2 | Maximum service voltage | kV | 145 |  |
| 3 | Number of poles |  | 3 |  |
| 4 | Rated frequency | Hz | 50 |  |
| 5 | Rated normal current | A | 3150 |  |
| 6 | Rated short time current for isolator and earth switch | kA | 40 |  |
| 7 | Rated peak withstand current for isolator and earth switch | kApk | 100 |  |
| 8 | Maximum temperature rise of current carrying parts at rated current. Isolating Switch Earth Switch | Deg |  |  |
| 9 | One minute power frequency withstand voltage |  |  |  |
|  | To earth and between poles | kVrms | 275 |  |
|  | Across isolating distance | kVrms | 275 |  |
| 10 | Lightning impulse withstand voltage |  |  |  |
|  | To earth and between poles | kVrms | 650 |  |
|  | Across isolating distance | kVrms | 650 |  |
| 11 | Switching impulse withstand voltage |  |  |  |
|  | To earth and between poles | kVrms | n/a |  |
|  | Across isolating distance | kVrms | n/a |  |
| 12 | Creepage distance for column | mm/kV | 31 |  |
| 13 | Ambient temperature range | oC | -1 to +48 |  |
| 14 | Relative humidity (max) | % | 90 |  |
| 15 | Altitude above sea level | m | 1500 |  |
| 16 | Operating mechanism type |  | Motor operated, control voltage 110/220V DC |  |
| 17 | Earthing switch operating mechanism |  | Independent manual drive, mechanically interlocked with main blades |  |
| 18 | Type of break |  | Center rotating horizontal double break |  |
| 19 | Material(s) of contacts |  |  |  |
| 20 | Opening Time | Sec |  |  |
| 21 | Closing Time | Sec |  |  |
| 22 | Bending moment at base of support insulator | kN |  |  |
| 23 | Applicable standard |  | IEC 62271-102 |  |
| 24 | Support structures supplied |  | Yes |  |
| 25 | Isolator outline drawing |  | To be provided with Bid |  |
| 26 | Foundation detail drawings |  | To be provided with Bid |  |
| 27 | Quality assurance certification |  | To be provided with Bid |  |
| 28 | Type tests |  | Bidder to provide previous test certificates/results |  |

### 132KV OIL FILLED POST MOUNTED CURRENT TRANSFORMERS

| S/N | ITEM DESCRIPTION | UNIT | GUARANTEE VALUE |  |
| --- | --- | --- | --- | --- |
|  | 132KV CT’s |  | ZESCO MIN. REQUIREMENTS | BIDDER TO FILL IN |
| 1 | Type designation |  | Bidder to Indicate |  |
| 2 | Applicable standard |  | IEC 61869-1 &2 |  |
| 3 | Nominal Rated voltage | kV | 132 |  |
| 4 | Highest System voltage | kV | 145 |  |
| 5 | Rated frequency | Hz | 50 |  |
| 6 | Power frequency withstand voltage (1 min.) | kVrms | 275 |  |
| 7 | Lightning impulse withstand voltage | kVpk | 650 |  |
| 8 | Rated continuous current | A | 300-600 |  |
| 9 | Rated short circuit withstand current (3s) | kA | 40 |  |
| 10 | Short time dynamic rating | kApk | 100 |  |
| 11 | Ratio, Burden, Class and ALF for Secondary Cores |  |  |  |
| 12 | Current density - In primary winding - In secondary winding | A/mm2 | 0.8 1.2 |  |
| 13 | Core type |  | Ring |  |
| 14 | Core material |  | Oriented steel & nickel |  |
| 15 | 330kV oil filled type: Core 1 Core 2 Core 3 Core 4 Core 5 Core 6 |  |  |  |
|  |  |  | 300/600/1, 20VA, 5P20 |  |
|  |  |  | 300/600/1, 20VA, 5P20 |  |
|  |  |  | 300/600/1, 15VA, 0.2s |  |
|  |  |  | 300/600//1, 20VA, PX V≥250Vk, Im≤8mA |  |
|  |  |  | 300/600//1, 20VA, PX V≥250Vk, Im≤8mA |  |
|  |  |  | 300/600//1, 20VA, PX V≥250Vk, Im≤8mA |  |
| 16 | Temperature rise for continuous full load operation In windings In oil | Deg. | 60 55 |  |
| 17 | Thermal current rating factor |  | 1.2 |  |
| 18 | Permitted static load (primary terminals) | kN | 3000 |  |
| 19 | Permitted dynamic load (primary terminals) | kN | 4000 |  |
| 20 | Creepage distance | kV/mm | 31 |  |
| 21 | Operating Temperature Range | oC | -1 to +48 |  |
| 22 | Altitude of Operation | m | 1500 |  |
| 23 | Humidity (max) | % | 90 |  |
| 24 | Current transformer outline and dimension drawing required |  | Yes |  |
| 25 | Foundation detail drawing required |  | Yes |  |
| 26 | Quality assurance certification required |  | Yes |  |
| 27 | Type tests required |  | Yes |  |

### 132KV CAPACITIVE VOLTAGE TRANSFORMERS

| S/N | ITEM DESCRIPTION | UNIT | GUARANTEE VALUE |  |
| --- | --- | --- | --- | --- |
|  | 132KV CVT |  | SCHEDULE A: MIN. REQUIREMENTS | SCHEDULE B: BIDDER GUARANTEE |
| 1 | Type Designation |  | Bidder to indicate |  |
| 2 | Applicable Standard |  | IEC 61869 - 5 |  |
| 3 | Rated Primary Voltage | kV | 132 |  |
| 4 | Highest System Voltage | kV | 145 |  |
| 5 | Rated Frequency | Hz | 50 |  |
| 6 | Power Frequency Withstand Voltage (one min.) | kVrms | 275 |  |
| 7 | Lightning Impulse Withstand Voltage, 1.2/50µs | kVpk | 650 |  |
| 8 | Power Frequency Withstand Voltage Test on Secondary | kVrms | 275 |  |
| 9 | Power Frequency Withstand Voltage Test on HF Terminal | kVrms | 275 |  |
| 10 | Method of transformation |  | Capacitive |  |
| 11 | Capacitance | F | 3500 +10%, -5% |  |
| 12 | Number of Secondary Windings |  | 2 |  |
| 13 | Range of Frequency for Accuracy - Winding I - Winding II |  | 99% - 101% 96% - 102% |  |
| 14 | Rated Voltage Factor |  | 1.2 continuous, 1.5 for 30 sec. |  |
| 15 | Ratio Winding I Winding II | V V | 132000/√3: 110/√3 132000/√3: 110/√3 |  |
| 16 | Accuracy and Burden - Winding I - Winding II |  | 0.2s, 100VA 3P, 100VA |  |
| 17 | Damping circuit of reactor provided |  | Yes |  |
| 18 | Creepage Distance | KV/mm | 31 |  |
| 19 | Temperature Range | oC | -1 to 48 |  |
| 20 | Altitude of Operation | m | 1500 |  |
| 21 | Humidity (max) | % | 90 |  |
| 22 | Type of Secondary Terminal Blocks |  | Clip on Stud Type |  |
| 23 | Type of Primary Terminal |  | Aluminium – Bar Type |  |
| 24 | CVT outline and dimension drawing provided |  | Yes |  |
| 25 | Support structures provided |  | Yes |  |
| 26 | Foundation detail drawing required |  | Yes |  |
| 27 | Quality assurance certification required |  | Yes |  |
| 28 | Type tests to be provided |  | Yes |  |

### 132KV SURGE ARRESTERS

| DESCRIPTION |  | UNIT | GUARANTEED VALUES |  |
| --- | --- | --- | --- | --- |
| Station type lightning arrestor complete with steel support structures |  |  | ZESCO MIN. REQUIREMENTS | BIDDER TO FILL IN |
| Type of Surge Arrestor |  |  | Zinc Oxide, gapless Station Class |  |
| System parameters |  |  |  |  |
| 1 | Nominal system voltage (L-L) | kV | 132 |  |
| 2 | Highest system voltage (L-L) | kV | 145 |  |
| 3 | Rated system frequency | Hz | 50 |  |
| 4 | Type of system earthing |  | Effective |  |
| 5 | Basic Insulation Level (BIL) | kV | 550 |  |
| Ratings and type of surge arrester |  |  |  |  |
| 6 | Operating Duty Class | kA | 10 |  |
| 7 | Rated voltage of surge arrester (L-L) | kV | 132 |  |
| 8 | Maximum Continuous Operating Voltage – MCOV (L-G) | kV | 88 |  |
| 9 | Minimum Rated Voltage (L-G) | kV | 120 |  |
| 10 | Nominal, 4/10 µs, discharge current rating of surge arrester | kA | 100 |  |
| 11 | Power frequency withstand voltage | kV | 230 |  |
| 12 | Creepage Distance | mm/kV | 31 |  |
| 13 | Pollution Withstand Level |  | 5 |  |
| 14 | Rated Energy Absorption Capability | kJ/kV | 5 |  |
| 15 | Continuous Current | µA | 250 |  |
| 16 | Pressure Relief Rated Large Current | kA | 50 |  |
| 17 | Interior Gas Pressure | MPa | 0.035-0.05 |  |
| 18 | Type |  | ZnO |  |
|  | Maximum lightning impulse residual voltage for a 10 kA, 8/20 µs, discharge current | kV | 252 |  |
| 19 | Line discharge class rating |  | 3 (Station) |  |
| 20 | Lighting arrestor counter, leakage current meter and their accessories to be provided |  | Required |  |
| 21 | Gapless or gapped type metal-oxide surge arrester |  | Gapless |  |
| 22 | Insulation Material |  | High Temperature Vulcanised Silicon Rubber |  |
| 23 | Corrosion protection of metal and alloy parts: galvanizing specification and/or stainless-steel grade |  | To SANS 121, SANS 32 |  |
| Environmental Parameters |  |  |  |  |
| 24 | Design altitude of surge arrester (above sea level) | m | 1500 |  |
| 25 | Design ambient temperature of surge arrester | °C | -1 to 45 |  |
| 26 | Humidity | % | 85 |  |
| Other requirements |  |  |  |  |
| 27 |  |  |  |  |
| 28 |  |  |  |  |
| 29 | Previous type test results/certificates to be provided with the bid | Yes/No | Yes |  |
| 30 | Routine test results/certificates to be provided on delivery | Yes/No | Yes |  |
| 31 | Design drawings showing dimensions, including foundations and brochures, to be provided with the bid | Yes/No | Yes |  |
| 32 | Quality assurance certification to be provided with the bid | Yes/No | Yes |  |
| 33 | Galvanized steel support structures complete with bolts & washers to be provided on delivery | Yes/No | Yes |  |
| 34 | Applicable standard(s) |  | IEC 60099-4 |  |

### 132kV SWITCHGEAR AND EQUIPMENT SCHEDULE OF INFORMATIVE DATA

| 132 kV SWITCHGEAR |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | 132 kV |  |
| 2B.1 | Insulators |  |  |  |
|  | - Reference standard |  |  |  |
|  | - Type reference |  |  |  |
|  | - Insulating material |  |  |  |
|  | - Material of socket |  |  |  |
|  | - Material of pin ball |  |  |  |
|  | - Material of cotter pin |  |  |  |
|  | - Number of units per suspension string |  |  |  |
|  | - Number of units per tension string |  |  |  |
|  | - Net weight per unit | kg |  |  |
|  | - Weight of suspension string with fittings | kg |  |  |
|  | - Weight of tension string with fittings | kg |  |  |
|  | - Negative 50% impulse flash-over voltage of suspension string | kV |  |  |
|  | - Positive 50% impulse flash-over voltage of suspension string | kV |  |  |
|  | - Negative 50% impulse flash-over voltage of tension string | kV |  |  |
|  | - Positive 50% impulse flash-over voltage of tension string | kV |  |  |
| b.7 | Conductors |  |  |  |
|  | - Reference standard |  |  |  |
|  | a. Line bay |  |  |  |
|  | - Type |  |  |  |
|  | - Material |  |  |  |
|  | - Weight | kg/m |  |  |
|  | - Weight of the heaviest reels including conductors | kg |  |  |
|  | - Size of the biggest reel |  |  |  |
|  | - Diameter | mm |  |  |
|  | - Width | mm |  |  |

### 132 kV SWITCHGEAR SCHEDULE 2b INFORMATIVE DATA

| 132 kV SWITCHGEAR |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | 132 kV |  |
| b.8 | Overhead Wires |  |  |  |
|  | - Reference standard |  |  |  |
|  | - Type |  |  |  |
|  | - Material |  |  |  |
|  | - Weight | kg/m |  |  |
|  | - Weight of the heaviest reels including conductors | kg |  |  |
|  | - Size of the biggest reel |  |  |  |
|  | - Diameter | mm |  |  |
|  | - Width | mm |  |  |
|  | b. Transformer bay |  |  |  |
|  | - Type |  |  |  |
|  | - Material |  |  |  |
|  | - Weight | kg/m |  |  |
|  | - Weight of the heaviest reels including conductors | kg |  |  |
|  | - Size of the biggest reel |  |  |  |
|  | - Diameter | mm |  |  |
|  | - Width | mm |  |  |
|  | c. Busbars |  |  |  |
|  | - Type |  |  |  |
|  | - Material |  |  |  |
|  | - Weight | kg/m |  |  |
|  | - Weight of the heaviest reels including conductors | kg |  |  |
|  | - Size of the biggest reel |  |  |  |
|  | - Diameter | mm |  |  |
|  | - Width | mm |  |  |
| b.10 | Accessories |  |  |  |
|  | - Reference standards |  |  |  |
|  | - Type of accessories |  |  |  |
|  | - Material of accessories used |  |  |  |

### 33KV CIRCUIT BREAKERS

| Item | Parameter Description For 36kv Circuit Breaker | Unit | Technical Guarantee Data |  |
| --- | --- | --- | --- | --- |
|  |  |  | Schedule A: Min. Requirements | Schedule B: Bidder Guarantee |
|  |  |  | 36kV SF6 outdoor circuit Breaker |  |
| 1 | Scope: Design, manufacture, testing, supply & installation. |  | Yes |  |
| 2 Design & Construction |  |  |  |  |
| 2.1 | Type designation |  | Bidder to Indicate |  |
| 2.2 | Reference Standard |  | IEC 62271-100 IEC 62271-1 |  |
| 2.3 | No. of poles/circuit breaker |  | 3 |  |
| 2.4 | Type of control mechanism |  | Motor operated spring |  |
| 2.4.1 | Mechanical class |  | M2 |  |
| 2.5 | Protection level of electrical cubicle |  | IP54 |  |
| 2.6 | Protection level of operating mechanism |  | IP55 |  |
| 2.7 | Type of insulator |  | Porcelain or silicone rubber |  |
| 2.8 | Insulating gas |  | Vacuum or SF6 |  |
| 2.9 | Rated absolute pressure at 20oC |  | Bidder to indicate |  |
| 2.10 | Relative leakage rate | %/yr | ˂0,5% (for SF6) |  |
| 2.11 | Circuit breaker class |  | Outdoor |  |
| 2.12 | Support structures supplied |  | Yes |  |
| 3 Service Conditions |  |  |  |  |
| 3.1 | Altitude of installation (a.s.l.) | m | 1500 |  |
| 3.2 | Operating ambient temperature | oC | -1 to +48 |  |
| 3.3 | Relative humidity (max) | % | 90 |  |
| 3.4 | Pollution levels | mm/kV | 31 |  |
| 4 Rated Characteristics |  |  |  |  |
| 4.1 | Rated voltage | kV | 33 |  |
| 4.2 | Maximum service voltage | kV | 36 |  |
| 4.3 | Rated frequency | Hz | 50 |  |
| 4.4 | Rated continuous current | A | 1600 |  |
| 4.5 | Rated peak withstand current | kApk | 80 |  |
| 4.6 | Rated short time withstand current | kA | 31.5 |  |
| 4.7 | Rated duration of short circuit | s | 3 |  |
| 4.8 | One min. power frequency withstand voltage: |  |  |  |
|  | phase to earth | kV | 75 |  |
|  | Across open contacts | kV | 75 |  |
| 4.9 | Rated lightning impulse withstand voltage: |  |  |  |
|  | phase to earth | kVpk | 170 |  |
|  | across open contacts | kVpk | 170 |  |
| 5. Breaking and Making Characteristics |  |  |  |  |
| 5.1 | Rated short circuit breaking current | kA | 31.5 |  |
| 5.2 | First pole to clear factor |  | 1.5 |  |
| 5.3 | DC component (% of AC component) | % | 43 |  |
| 5.4 | Peak value of rated short circuit making current | kApk | 80 |  |
| 5.5 | Rated breaking current for short line faults |  | As per IEC Standard |  |
| 5.6 | Rated out of phase breaking current | Id (kA) | 10 |  |
| 5.7 | Rated overvoltage factor for unloaded transformers |  | ˂2.5 |  |
| 5.8 | Rated line charging breaking current | A | 50 |  |
| 5.9 | Rated cable charging breaking current |  | 160 |  |
| 6. Operating Times |  |  |  |  |
| 6.1 | Rated opening time – from opening coil energizing to separation of main contacts | ms | ˂28 |  |
| 6.2 | Rated breaking time – from opening coil energizing to arc extinction | ms | ˂50 |  |
| 6.3 | Rated closing time – from closing coil energizing to main contact making | ms | ˂70 |  |
| 6.4 | Rated operating sequence |  | O-0.3s-CO-180s-CO |  |
| 6.5 | Rated operating sequence without motor supply |  | O-CO |  |
| 7 Low Voltage Specification |  |  |  |  |
| 7.1 | Motor voltage | V | 110/220V DC |  |
| 7.2 | Circuit motor protection |  | MCB |  |
| 7.3 | Motor voltage min. range | % | 85 |  |
| 7.4 | Motor voltage max. range | % | 110 |  |
| 7.5 | Opening voltage min. range | % | 65 |  |
| 7.6 | Opening voltage max. range | % | 110 |  |
| 7.7 | Closing voltage min. range | % | 75 |  |
| 7.8 | Closing voltage max. range | % | 110 |  |
| 7.9 | Lighting and heating circuit voltage | V | 220, AC |  |
| 7.10 | Local electrical control with two push button |  | Yes |  |
| 7.11 | Anti-pumping relay |  | Yes |  |
| 7.12 | Local/remote selector switch |  | Yes |  |
| 7.13 | Number of trip coils |  | 2 |  |
| 7.14 | Provision for trip coil supervision |  | Yes |  |
| 7.15 | Pole discrepancy feature |  | n/a |  |
| 7.16 | Signalling contacts for spring position/status |  | Yes, 1NO |  |
|  | Signalling contacts for SF6 gas low, block etc |  | Yes |  |
| 7.17 | Number of available auxiliary NO contacts |  | 8 |  |
| 7.18 | Number of available NC auxiliary contacts |  | 8 |  |
| 7.19 | Position indicator – O/I |  | Yes |  |
| 7.20 | Indicator for spring status |  | Yes |  |
| 7.21 | Operations Counter |  | Yes |  |
| 7.22 | Gas for first filling plus 30% |  | Yes |  |
| 7.23 | SF6 filling equipment supplied |  | Yes |  |
| 7.24 | SF6 gas leakage detector supplied |  | Yes |  |
| 8 Documents and Drawings with Bid |  |  |  |  |
| 8.1 | Circuit breaker outline drawing |  | Yes |  |
| 8.2 | Foundation detail drawings |  | Yes |  |
| 8.3 | Quality assurance certification |  | Yes |  |
| 8.4 | Typical low voltage elementary diagram included in Bid |  | Yes |  |
| 9 Test Reports with Bid |  |  |  |  |
| 9.1 | Dielectric test |  | Yes |  |
| 9.2 | Temperature rise test |  | Yes |  |
| 9.3 | Short time withstand current test |  | Yes |  |
| 9.4 | Mechanical endurance test |  | Class M2 – 10,000 operations |  |
| 9.5 | Capacitive current breaking test |  | Yes |  |
| 9.6 | Operating times test |  | Yes |  |
| 9.7 | Main contact resistance test |  | Yes |  |

### 33KV DISCONNECTOR

| Item | Parameter Description For 36kv Isolator C/W Earth Switch | Unit | Technical Guarantee Data |  |
| --- | --- | --- | --- | --- |
|  |  |  | Schedule A: Min. Requirements | Schedule B: Bidder Guarantee |
| 1 | Rated Voltage | kV | 33 |  |
| 2 | Maximum service voltage | kV | 36 |  |
| 3 | Number of poles |  | 3 |  |
| 4 | Rated frequency | Hz | 50 |  |
| 5 | Rated normal current | A | 1600 |  |
| 6 | Rated short time current for isolator and earth switch | kA | 31.5 |  |
| 7 | Rated peaks withstand current for isolator and earth switch | kApk | 80 |  |
| 8 | One minute power frequency withstand voltage |  |  |  |
|  | To earth and between poles | kVrms | 75 |  |
|  | Across isolating distance | kVrms | 75 |  |
| 9 | Lightning impulse withstand voltage |  |  |  |
|  | To earth and between poles | kVrms | 170 |  |
|  | Across isolating distance | kVrms | 170 |  |
| 10 | Creepage distance | mm/kV | 31 |  |
| 11 | Ambient temperature range | oC | -1 to +48 |  |
| 12 | Relative humidity (max) | % | 90 |  |
| 13 | Altitude above sea level | m | 1500 |  |
| 14 | Operating mechanism type |  | Motor operated, control voltage 110/220V DC |  |
| 15 | Earthing switch operating mechanism |  | Independent manual drive, mechanically interlocked with main blades |  |
| 16 | Type of break |  | Centre rotating horizontal double break |  |
| 17 | Applicable standard |  | IEC 62271-102 |  |
| 18 | Mounting structures supplied |  | Yes |  |
| 29 | Isolator outline drawing |  | To be provided with Bid |  |
| 20 | Foundation detail drawings |  | To be provided with Bid |  |
| 21 | Quality assurance certification |  | To be provided with Bid |  |
| 22 | Type tests |  | Bidder to provide previous test certificates/results |  |

### 33KV CURRENT TRANSFORMERS

| Item | Technical Details | Unit | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- |
| 1 | Type (oil filled/solid dielectric) |  | Bidder to specify |  |
| 2 | Insulator (porcelain/silicon rubber) |  | Bidder to specify |  |
| 3 | Burden | VA | 15 |  |
| 4 | Ratio |  | 800-400/1 |  |
| 5 | Core 1 |  | Class 0.2s |  |
| 6 | Core 2 |  | Class 5P20 |  |
| 7 | Core 3 |  | Class X, (Vk, Ie, Rct to suit) |  |
|  | Core 4 |  | Class 5P20 |  |
|  | Core 5 |  | Class X, (Vk, Ie, Rct to suit) |  |
|  | Core 6 |  | Class 0.2s |  |
| 8 | Lightning impulse withstand (Dry) | kV | 170 |  |
| 9 | Power Frequency withstand (1 min) | kV | 75 |  |
| 12 | Operating ambient temperature | oC | -1 to 40 |  |
| 13 | Technical/Manufacturer’s Brochure. |  | To be provided with bid |  |
| 14 | TYPE TEST |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| 15 | DRAWINGS |  | Supplier shall provide drawings showing dimensions |  |
| 16 | QUALITY ASSURANCE |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 33kV INDUCTIVE VOLTAGE TRANSFORMERS

| Item | Technical Detail | Unit | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- |
|  | Type |  | Bidder to specify |  |
|  | Insulation |  | Silicon Rubber |  |
|  | Burden | VA | 100 |  |
|  | Primary Voltage | kV | 33/√3 |  |
|  | Secondary Voltage | V | 110/√3; 110/√3 |  |
|  | Lightning impulse withstand (Dry) | kV | 170 |  |
|  | Power Frequency withstand (1 min) | kVrms | 70 |  |
|  | Voltage Factor |  | 1.2 continuous; 1.9/30 sec |  |
|  | Accuracy Class Core1(metering) |  | 0.2s |  |
|  | Accuracy Class Core2(protection) |  | 3P |  |
|  | Operating ambient temperature | oC | -1 to 40 |  |
|  | Technical/Manufacturer’s Brochure. |  | To be provided with bid |  |
|  | TYPE TEST |  | Supplier shall provide previous type test certificate/results together with the bid |  |
|  | DRAWINGS |  | Supplier shall provide drawings showing dimensions |  |
|  | QUALITY ASSURANCE |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 33KV SURGE ARRESTERS

| Description |  | Unit | Guaranteed Values |  |
| --- | --- | --- | --- | --- |
|  |  |  | ZESCO Min. Requirements | Bidder To Fill In |
| 1. Type of Surge Arrestor |  |  | Zinc Oxide, gapless Station Class |  |
| 2. System Parameters | Nominal System Voltage | kV | 33 |  |
|  | Maximum System Voltage | kV | 36 |  |
|  | Number of Phases |  | 3 |  |
|  | Type of Earthing |  | Solid |  |
|  | Rated Frequency | Hz | 50 |  |
| 3. Surge Arrestor Characteristics |  |  |  |  |
|  | Nominal Discharge Current | kA | 10 |  |
|  | Max. Continuous Operating Voltage | kV | 28 |  |
|  | Line Discharge Class |  | 3 |  |
|  | Gapless or gapped type metal-oxide surge arrester |  | Gapless |  |
|  | Max. Residual Voltage with 8/20µs current wave | kVpk | 201 |  |
|  | High Current Discharge Withstand Strength, 4/10µs | kApk | 100 |  |
| 4. Insulation Withstand Voltages |  |  |  |  |
|  | Power Frequency Withstand Voltage | kV | 70 |  |
|  | Lightning Impulse Withstand Voltage | kV | 170 |  |
| 5. Mechanical Strength and Service Conditions |  |  |  |  |
|  | Specified Continuous Load | Nm | 1600 |  |
|  | Creepage Distance | mm/kV | 25 |  |
|  | Type of Housing and Insulating Material |  | Brown porcelain or Silicone Rubber |  |
|  | Altitude | m | 1500 |  |
|  | Operating Temperature Range | oC | -1 to +48 |  |
|  | Humidity | % | Up to 90% |  |
|  | Type Tests |  | Supplier to Provide Previous Test Certificates/Results |  |
|  | Drawings |  | Supplier to Provide Dimensional Drawings & Mounting Arrangements |  |
|  | Quality Assurance |  | Supplier to Provide Quality Assurance Certificate with Bid |  |
|  | Technical Details/Drawings |  | Bidders to Provide Complete Technical Details/Brochure with Bid |  |
| 6. Standards | Applicable Standard |  | IEC 60099-4 |  |

### 11KV INCOMER CIRCUIT BREAKER FOR 31.5MVA AND 40MVA TRANSFORMERS TECHNICAL SCHEDULE

| Description | Unit | Guaranteed Values |  |
| --- | --- | --- | --- |
| 11KV INCOMER CIRCUIT BREAKER FOR 31.5MVA TX |  | ZESCO Minimum Requirements | Tenderer’s Guarantee |
| Switchgear |  |  |  |
| Switchgear Type |  | 11kV indoor circuit breaker complete wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| Switchgear Model |  | Bidder to specify |  |
| Switchgear Manufacturer |  | Bidder to specify |  |
| Country of Manufacture |  | Bidder to specify |  |
| Environmental Conditions |  |  |  |
| Altitude above sea level | m | 1500 |  |
| Humidity | % | 85 |  |
| Guaranteed No. of operations |  | 10000 |  |
| Operating ambient temperature | °C | 2 to 45 |  |
| Specific creepage distance | mm/kV | 31 |  |
| Electrical Endurance Class (IEC 602271) |  | E2 |  |
| Panel – General |  |  |  |
| Type |  | Front access door with window |  |
| Mounting |  | Floor standing |  |
| Panel Dimensions (D X W x H) | mm | Bidder to specify |  |
| Panel Colour |  | RAL 7035 |  |
| Busbar Rated Current | A | 2500 |  |
| Rated Short Time withstand Current | kA | 31.5, for 3 sec. |  |
| Busbar rated Voltage | kV | 11 |  |
| Busbar Insulation level | kV | 17.5 |  |
| Impulse withstand voltage | kV | 95 |  |
| Control / Indications |  |  |  |
| Measurements /Instruments |  | MDI Ammeter / Electronic Energy meter / IED |  |
| Display of Measured Values |  | Electronic Energy meter / IED |  |
| Selector Switches |  | Local/Remote |  |
| Control Switches |  | CB Open/Close |  |
| AC/DC Wiring Protection |  | MCBs |  |
| Alarm Indication |  | On Relay LEDs |  |
| Status Indication |  | On IED |  |
| Panel Heating/Lighting |  | Yes |  |
| Test Interface |  | Yes |  |
| Control |  | Trip /close switch, Local/Remote Selector Switch, Pendant Switch |  |
| Indications |  | CB open, CB closed, Spring not charged,CB test and service postions Earth switch ON, Cable Live |  |
| Anti-pumping Relay |  | Yes |  |
| Protection IED |  |  |  |
| Device |  | IED |  |
| Functions |  | Three-phase overcurrent protection, three stage |  |
|  |  | earth-fault protection, three stage |  |
|  |  | Sensitive earth fault |  |
|  |  | Negative-sequence overcurrent protection |  |
|  |  | Phase discontinuity Protection |  |
|  |  | Under Frequency Protection in four stages, for loadshedding |  |
|  |  | Over/under voltage protection |  |
|  |  | Three-phase thermal protection for feeders, cables and distribution transformers |  |
|  |  | Multi-shot auto-reclose |  |
|  |  | Circuit breaker failure Protection |  |
|  |  | Arc Protection |  |
| Logic |  | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| Condition monitoring |  | Non-volatile memory for; |  |
|  |  | Circuit-breaker condition Monitoring |  |
|  |  | Trip circuit supervision |  |
|  |  | Trip counters for circuit-breaker |  |
|  |  | Current circuit supervision |  |
|  |  | Disturbance (event) recorder |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
| Measurement |  | Residual current |  |
|  |  | Phase unbalance |  |
|  |  | Thermal level |  |
|  |  | HMI/Binary input based open/close control of switchgear. |  |
| Communication |  | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | Provide two Fibre Optic ports for connection to Industrial network switch. |  |
|  |  | Provide GPS for IED time synchronization. |  |
|  |  | All relay interrogation hardware and software |  |
| AC Current Inputs |  | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| Auxiliary Voltage |  | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| Frequency |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| Light Emitting Diodes (LEDs) |  | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| Binary Inputs |  | The binary inputs shall; |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
|  |  | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| Relay Terminal Connections |  | At least 4mm2 for the CT circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| Reference International Standard |  | The IEC 60255 standard for protection relays shall apply. |  |
| Product Version |  | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
|  |  | The relays shall have a manufacturer support product life of not less than 7 years |  |
| METERING |  |  |  |
| Voltage Transformer |  |  |  |
| VT ratio | V | 11kV/√3, 110V/√3, 110/√3 |  |
| Burden | VA | 100/phase |  |
| Class |  | Class 0.2s For metering and Class 3P for protection |  |
| Voltage Factor |  | 1.2 continuous; 1.9/30 sec |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Current Transformer |  |  |  |
| Core 1 (Metering) – Ratio/Burden/Class |  | 2000/1A, 15VA, Class 0.2s |  |
| Core 2 (Protection) - Ratio/Burden/Class |  | 2000/1A, 15VA, 5P20 |  |
| Core 3 (Differential) - Ratio/Burden/Class |  | 2000/1A Class X, (Vk. Ie Rct to suit) |  |
| Core 4 (REF) - Ratio/Burden/Class |  | 2000/1A Class X, (Vk. Ie, Rct to suit) |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Circuit Breaker Basic Data |  |  |  |
| Rated voltage (Highest system voltage) | kV | 12 |  |
| Rated continuous current at 40 °C ambient temperature: | A | 2500 |  |
| Interruption Medium |  | Vacuum |  |
| Rated frequency | Hz | 50 |  |
| Rated short time withstand current (3s) | kA | 31.5 |  |
| Closing time | ms | 80 |  |
| Opening time | ms | 45 |  |
| Reclose Sequence |  | O-0.3s-CO-15s-CO |  |
| Termination | kV | Euromould bushings |  |
| Manual Closing/Opening |  | Yes |  |
| Manual charging |  | Yes |  |
| Circuit Breaker Insulation Level |  |  |  |
| Lightning impulse dry withstand voltage | kV | 95 |  |
| One minute power-frequency wet withstand voltage | kV | 28 |  |
| Circuit Breaker Operating Mechanism |  |  |  |
| Mechanism |  | Magnetic/ Motorised Coil actuator trip free mechanism, with mechanical ON/ OFF indicator, operating counter |  |
| Guaranteed No. of operations |  | 10000 |  |
| Rated supply voltage of Trip/Close Coils | V dc | 110/220 |  |
| Rated supply voltage of Spring Charge Motor | V dc | 110/220 |  |
| Spare Auxiliary contacts |  | 6xNO, 6xNC |  |
| Interlocks |  | Mechanical and Electrical (Refer to item 13 in this document under general requirements for details) |  |
| Cable and Integral Earthing |  |  |  |
| Cable Entry |  | Bottom |  |
| Cable Type |  | XLPE |  |
| No. cores – size |  | 3C x 185mm2 |  |
| Integral Earthing |  | Yes |  |
| Circuit Breaker Type Test, Drawings and Quality assurance |  |  |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions Further the supplier shall provide: Manuals: Three sets of manuals of all the installed equipment. (Operating and Maintenance Manuals.) Drawings: Three sets of hard copy drawings and one soft copy in CAD version 2004 or later, format. |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |

| Item |  |  | Unit | Value | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- | --- |
| 11KV INCOMER CIRCUIT BREAKER FOR 40MVA |  |  |  | 11kV indoor circuit breaker completely wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| BASIC DATA |  |  |  |  |  |
| Rated voltage (Highest system voltage) |  |  | kV | 12 |  |
| Rated continuous current at 40 oC ambient temperature: |  |  | A | 2500 |  |
| Interruption Medium |  |  |  | vacuum |  |
| Rated frequency |  |  | Hz | 50 |  |
| Rated short time withstand current (3s) |  |  | kA | 31.5 |  |
| Arc Sensor installed in cable and bus chamber |  |  |  | YES |  |
| RATED INSULATION LEVEL |  |  |  |  |  |
| Lightning impulse dry withstand voltage |  |  | kV | 95 |  |
| One minute power-frequency wet withstand voltage |  |  | kV | 28 |  |
| OPERATING MECHANISM |  |  |  |  |  |
| Mechanism |  |  |  | ‘Trip Free’ spring mechanism |  |
| Rated supply voltage of closing mechanism |  |  | V dc | 110/220 |  |
| Rated supply voltage of shunt opening release |  |  | V dc | 110/220 |  |
| ENVIRONMENTAL CONDITIONS |  |  |  |  |  |
| Altitude above sea level |  |  | m | 1500 |  |
| Humidity |  |  | % | 85 |  |
| Electrical Endurance Class (IEC 602271) |  |  |  | E2 |  |
| Guaranteed No. of operations |  |  |  | 10000 |  |
| Operating ambient temperature |  |  | oC | -1 to 40 |  |
| Specific creepage distance |  |  | mm/kV | 31 |  |
| CT | CT ratio |  |  | 2000/1/1/1/1A |  |
|  | Core 1 | Burden | VA | 15 |  |
|  |  | Class |  | Class X Diff |  |
|  | Core 2 | Burden | VA | 15 |  |
|  |  | Class |  | ClassX, Vk=300V for REF protection |  |
|  | Core 3 | Burden | VA | 15 |  |
|  |  | Class |  | Class 5P20 For OCEF protection |  |
|  | Core 4 | Burden | VA | 15 |  |
|  |  | Class |  | Class 0.2s Metering |  |
| VT | VT ratio |  | V | 11000/110 |  |
|  | Burden |  | VA | 50 |  |
|  | Class |  |  | Class 0.5 for metering and 3P for protection |  |
|  | Voltage Factor |  |  | 1.2 continuous; 1.9/30 sec |  |
| TYPE TEST |  |  |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| DRAWINGS |  |  |  | Supplier shall provide drawings showing dimensions |  |
| QUALITY ASSURANCE |  |  |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 11KV INCOMER CIRCUIT BREAKER FOR 12.5MVA TRANSFORMERS TECHNICAL SCHEDULE

| Description | Unit | Guaranteed Values |  |
| --- | --- | --- | --- |
| 11KV INCOMER CIRCUIT BREAKER FOR 12.5MVA TRANSFORMERS |  | ZESCO Minimum Requirements | Tenderer’s Guarantee |
| Switchgear |  |  |  |
| Switchgear Type |  | 11kV indoor circuit breaker complete wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| Switchgear Model |  | Bidder to specify |  |
| Switchgear Manufacturer |  | Bidder to specify |  |
| Country of Manufacture |  | Bidder to specify |  |
| Environmental Conditions |  |  |  |
| Altitude above sea level | m | 1500 |  |
| Humidity | % | 85 |  |
| Guaranteed No. of operations |  | 10000 |  |
| Operating ambient temperature | oC | 2 to 45 |  |
| Specific creepage distance | mm/kV | 31 |  |
| Electrical Endurance Class (IEC 602271) |  | E2 |  |
| Panel – General |  |  |  |
| Type |  | Front access door with window |  |
| Mounting |  | Floor standing |  |
| Panel Dimensions (D X W x H) | mm | Bidder to specify |  |
| Panel Colour |  | RAL 7035 |  |
| Busbar Rated Current | A | 2500 |  |
| Rated Short Time withstand Current | kA | 31.5, for 3 sec. |  |
| Busbar rated Voltage | kV | 11 |  |
| Busbar Insulation level | kV | 17.5 |  |
| Impulse withstand voltage | kV | 95 |  |
| Control / Indications |  |  |  |
| Measurements /Instruments |  | MDI Ammeter / Electronic Energy meter / IED |  |
| Display of Measured Values |  | Electronic Energy meter / IED |  |
| Selector Switches |  | Local/Remote |  |
| Control Switches |  | CB Open/Close |  |
| AC/DC Wiring Protection |  | MCBs |  |
| Alarm Indication |  | On Relay LEDs |  |
| Status Indication |  | On IED |  |
| Panel Heating/Lighting |  | Yes |  |
| Test Interface |  | Yes |  |
| Control |  | Trip /close switch, Local/Remote Selector Switch, Pendant Switch |  |
| Indications |  | CB open, CB closed, Spring not charged,CB test and service postions Earth switch ON, Cable Live |  |
| Anti-pumping Relay |  | Yes |  |
| Protection IED |  |  |  |
| Device |  | IED |  |
| Functions |  | Three-phase overcurrent protection, three stage |  |
|  |  | earth-fault protection, three stage |  |
|  |  | Sensitive earth fault |  |
|  |  | Negative-sequence overcurrent protection |  |
|  |  | Phase discontinuity Protection |  |
|  |  | Under Frequency Protection in four stages, for loadshedding |  |
|  |  | Over/under voltage protection |  |
|  |  | Three-phase thermal protection for feeders, cables and distribution transformers |  |
|  |  | Multi-shot auto-reclose |  |
|  |  | Circuit breaker failure Protection |  |
|  |  | Arc Protection |  |
| Logic |  | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| Condition monitoring |  | Non-volatile memory for; |  |
|  |  | Circuit-breaker condition Monitoring |  |
|  |  | Trip circuit supervision |  |
|  |  | Trip counters for circuit-breaker |  |
|  |  | Current circuit supervision |  |
|  |  | Disturbance (event) recorder |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
| Measurement |  | Residual current |  |
|  |  | Phase unbalance |  |
|  |  | Thermal level |  |
|  |  | HMI/Binary input based open/close control of switchgear. |  |
| Communication |  | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | Provide two Fibre Optic ports for connection to Industrial network switch. |  |
|  |  | Provide GPS for IED time synchronization. |  |
|  |  | All relay interrogation hardware and software |  |
| AC Current Inputs |  | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| Auxiliary Voltage |  | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| Frequency |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| Light Emitting Diodes (LEDs) |  | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| Binary Inputs |  | The binary inputs shall; |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
|  |  | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| Relay Terminal Connections |  | At least 4mm2 for the CT circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| Reference International Standard |  | The IEC 60255 standard for protection relays shall apply. |  |
| Product Version |  | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
|  |  | The relays shall have a manufacturer support product life of not less than 7 years |  |
| METERING |  |  |  |
| Voltage Transformer |  |  |  |
| VT ratio | V | 11kV/√3, 110V/√3, 110/√3 |  |
| Burden | VA | 100/phase |  |
| Class |  | Class 0.2 For metering and Class 3P for protection |  |
| Voltage Factor |  | 1.2 continuous; 1.9/30 sec |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Current Transformer |  |  |  |
| Core 1 (Metering) – Ratio/Burden/Class |  | 1600/800/1A, 15VA, Class 0.2 |  |
| Core 2 (Protection) - Ratio/Burden/Class |  | 1600/800/1A, 15VA, 5P20 |  |
| Core 3 (Differential) - Ratio/Burden/Class |  | 1600/800/1A Class X, (Vk. Ie Rct to suit) |  |
| Core 4 (REF) - Ratio/Burden/Class |  | 1600/800/1A Class X, (Vk. Ie Rct to suit) |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Circuit Breaker Basic Data |  |  |  |
| Rated voltage (Highest system voltage) | kV | 12 |  |
| Rated continuous current at 40 oC ambient temperature: | A | 1250 |  |
| Interruption Medium |  | Vacuum |  |
| Rated frequency | Hz | 50 |  |
| Rated short time withstand current (3s) | kA | 31.5 |  |
| Closing time | ms | 80 |  |
| Opening time | ms | 45 |  |
| Reclose Sequence |  | O-0.3s-CO-15s-CO |  |
| Termination | kV | Euromould bushings |  |
| Manual Closing/Opening |  | Yes |  |
| Manual charging |  | Yes |  |
| Circuit Breaker Insulation Level |  |  |  |
| Lightning impulse dry withstand voltage | kV | 95 |  |
| One minute power-frequency wet withstand voltage | kV | 28 |  |
| Circuit Breaker Operating Mechanism |  |  |  |
| Mechanism |  | Magnetic/ Motorised Coil actuator trip free mechanism, with mechanical ON/ OFF indicator, operating counter |  |
| Guaranteed No. of operations |  | 10000 |  |
| Rated supply voltage of Trip/Close Coils | V dc | 110/220 |  |
| Rated supply voltage of Spring Charge Motor | V dc | 110/220 |  |
| Spare Auxiliary contacts |  | 6xNO, 6xNC |  |
| Interlocks |  | Mechanical and Electrical (Refer to item 13 in this document under general requirements for details) |  |
| Cable and Integral Earthing |  |  |  |
| Cable Entry |  | Bottom |  |
| Cable Type |  | XLPE |  |
| No. cores – size |  | 3C x 185mm2 |  |
| Integral Earthing |  | Yes |  |
| Circuit Breaker Type Test, Drawings and Quality assurance |  |  |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions Further the supplier shall provide: Manuals: Three sets of manuals of all the installed equipment. (Operating and Maintenance Manuals.) Drawings: Three sets of hard copy drawings and one soft copy in CAD version 2004 or later, format. |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 11KV OUTGOING CIRCUIT BREAKER TECHNICAL SCHEDULE

| Description | Unit | Guaranteed Values |  |
| --- | --- | --- | --- |
| 11KV OUTGOING CIRCUIT BREAKER |  | ZESCO Minimum Requirements | Tenderer’s Guarantee |
| Switchgear |  |  |  |
| Switchgear Type |  | 11kV indoor circuit breaker complete wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| Switchgear Model |  | Bidder to specify |  |
| Switchgear Manufacturer |  | Bidder to specify |  |
| Country of Manufacture |  | Bidder to specify |  |
| Environmental Conditions |  |  |  |
| Altitude above sea level | m | 1500 |  |
| Humidity | % | 85 |  |
| Guaranteed No. of operations |  | 10000 |  |
| Operating ambient temperature | oC | 2 to 45 |  |
| Specific creepage distance | mm/kV | 31 |  |
| Electrical Endurance Class (IEC 602271) |  | E2 |  |
| Panel – General |  |  |  |
| Type |  | Front access door with window |  |
| Mounting |  | Floor standing |  |
| Panel Dimensions (D X W x H) | mm | Bidder to specify |  |
| Panel Colour |  | RAL 7035 |  |
| Busbar Rated Current | A | 2500 |  |
| Rated Short Time withstand Current | kA | 31.5, for 3 sec. |  |
| Busbar rated Voltage | kV | 11 |  |
| Busbar Insulation level | kV | 17.5 |  |
| Impulse withstand voltage | kV | 95 |  |
| Control / Indications |  |  |  |
| Measurements /Instruments |  | MDI Ammeter / Electronic Energy meter / IED |  |
| Display of Measured Values |  | Electronic Energy meter / IED |  |
| Selector Switches |  | Local/Remote |  |
| Control Switches |  | CB Open/Close |  |
| AC/DC Wiring Protection |  | MCBs |  |
| Alarm Indication |  | On Relay LEDs |  |
| Status Indication |  | On IED |  |
| Panel Heating/Lighting |  | Yes |  |
| Test Interface |  | Yes |  |
| Control |  | Trip /close switch, Local/Remote Selector Switch, Pendant Switch |  |
| Indications |  | CB open, CB closed, Spring not charged,CB test and service postions Earth switch ON, Cable Live |  |
| Anti-pumping Relay |  | Yes |  |
| Protection IED |  |  |  |
| Device |  | IED |  |
| Functions |  | Three-phase overcurrent protection, three stage |  |
|  |  | earth-fault protection, three stage |  |
|  |  | Sensitive earth fault |  |
|  |  | Negative-sequence overcurrent protection |  |
|  |  | Phase discontinuity Protection |  |
|  |  | Under Frequency Protection in four stages, for loadshedding |  |
|  |  | Over/under voltage protection |  |
|  |  | Three-phase thermal protection for feeders, cables and distribution transformers |  |
|  |  | Multi-shot auto-reclose |  |
|  |  | Circuit breaker failure Protection |  |
|  |  | Arc Protection |  |
| Logic |  | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| Condition monitoring |  | Non-volatile memory for; |  |
|  |  | Circuit-breaker condition Monitoring |  |
|  |  | Trip circuit supervision |  |
|  |  | Trip counters for circuit-breaker |  |
|  |  | Current circuit supervision |  |
|  |  | Disturbance (event) recorder |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
| Measurement |  | Residual current |  |
|  |  | Phase unbalance |  |
|  |  | Thermal level |  |
|  |  | HMI/Binary input based open/close control of switchgear. |  |
| Communication |  | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | Provide two Fibre Optic ports for connection to Industrial network switch. |  |
|  |  | Provide GPS for IED time synchronization. |  |
|  |  | All relay interrogation hardware and software |  |
| AC Current Inputs |  | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| Auxiliary Voltage |  | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| Frequency |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| Light Emitting Diodes (LEDs) |  | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| Binary Inputs |  | The binary inputs shall; |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
|  |  | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| Relay Terminal Connections |  | At least 4mm2 for the CT circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| Reference International Standard |  | The IEC 60255 standard for protection relays shall apply. |  |
| Product Version |  | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
|  |  | The relays shall have a manufacturer support product life of not less than 7 years |  |
| METERING |  |  |  |
| Current Transformer |  |  |  |
| Core 1 (Metering) – Ratio/Burden/Class |  | 800/400/1A, 15VA, Class 0.2 |  |
| Core 2 (Protection) - Ratio/Burden/Class |  | 800/400//11A, 15VA, 5P20 |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Circuit Breaker Basic Data |  |  |  |
| Rated voltage (Highest system voltage) | kV | 12 |  |
| Rated continuous current at 40 °C ambient temperature: | A | 800 |  |
| Interruption Medium |  | Vacuum |  |
| Rated frequency | Hz | 50 |  |
| Rated short time withstand current (3s) | kA | 31.5 |  |
| Closing time | ms | 80 |  |
| Opening time | ms | 45 |  |
| Reclose Sequence |  | O-0.3s-CO-15s-CO |  |
| Termination | kV | Euromould bushings |  |
| Manual Closing/Opening |  | Yes |  |
| Manual charging |  | Yes |  |
| Circuit Breaker Insulation Level |  |  |  |
| Lightning impulse dry withstand voltage | kV | 95 |  |
| One minute power-frequency wet withstand voltage | kV | 28 |  |
| Circuit Breaker Operating Mechanism |  |  |  |
| Mechanism |  | Magnetic/ Motorised Coil actuator trip free mechanism, with mechanical ON/ OFF indicator, operating counter |  |
| Guaranteed No. of operations |  | 10000 |  |
| Rated supply voltage of Trip/Close Coils | V dc | 110/220 |  |
| Rated supply voltage of Spring Charge Motor | V dc | 110/220 |  |
| Spare Auxiliary contacts |  | 6xNO, 6xNC |  |
| Interlocks |  | Mechanical and Electrical (Refer to item 13 in this document under general requirements for details) |  |
| Cable and Integral Earthing |  |  |  |
| Cable Entry |  | Bottom |  |
| Cable Type |  | XLPE |  |
| No. cores – size |  | 3C x 185mm2 |  |
| Integral Earthing |  | Yes |  |
| Circuit Breaker Type Test, Drawings and Quality assurance |  |  |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions Further the supplier shall provide: Manuals: Three sets of manuals of all the installed equipment. (Operating and Maintenance Manuals.) Drawings: Three sets of hard copy drawings and one soft copy in CAD version 2004 or later, format. |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### BUS SECTION CIRCUIT BREAKER PANEL TECHNICAL SCHEDULE

| Description | Unit | Guaranteed Values |  |
| --- | --- | --- | --- |
| BUS SECTION CIRCUIT BREAKER PANEL |  | ZESCO Minimum Requirements | Tenderer’s Guarantee |
| Switchgear |  |  |  |
| Switchgear Type |  | 11kV indoor circuit breaker complete wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| Switchgear Model |  | Bidder to specify |  |
| Switchgear Manufacturer |  | Bidder to specify |  |
| Country of Manufacture |  | Bidder to specify |  |
| Environmental Conditions |  |  |  |
| Altitude above sea level | m | 1500 |  |
| Humidity | % | 85 |  |
| Guaranteed No. of operations |  | 10000 |  |
| Operating ambient temperature | oC | 2 to 45 |  |
| Specific creepage distance | mm/kV | 31 |  |
| Electrical Endurance Class (IEC 602271) |  | E2 |  |
| Panel – General |  |  |  |
| Type |  | Front access door with window |  |
| Mounting |  | Floor standing |  |
| Panel Dimensions (D X W x H) | mm | Bidder to specify |  |
| Panel Colour |  | RAL 7035 |  |
| Busbar Rated Current | A | 2500 |  |
| Rated Short Time withstand Current | kA | 31.5, for 3 sec. |  |
| Busbar rated Voltage | kV | 11 |  |
| Busbar Insulation level | kV | 17.5 |  |
| Impulse withstand voltage | kV | 95 |  |
| Control / Indications |  |  |  |
| Measurements /Instruments |  | MDI Ammeter / Electronic Energy meter / IED |  |
| Display of Measured Values |  | Electronic Energy meter / IED |  |
| Selector Switches |  | Local/Remote |  |
| Control Switches |  | CB Open/Close |  |
| AC/DC Wiring Protection |  | MCBs |  |
| Alarm Indication |  | On Relay LEDs |  |
| Status Indication |  | On IED |  |
| Panel Heating/Lighting |  | Yes |  |
| Test Interface |  | Yes |  |
| Control |  | Trip /close switch, Local/Remote Selector Switch, Pendant Switch |  |
| Indications |  | CB open/closed, Spring not charged,CB test and service postions. |  |
| Anti-pumping Relay |  | Yes |  |
| Bus bar earthing |  | Using a bus earthing panel complete with three phase earth switch or busbar earthing handcart including all safety interlocks |  |
| Protection IED |  |  |  |
| Device |  | IED |  |
| Functions |  | Three-phase overcurrent protection, three stage |  |
|  |  | earth-fault protection, three stage |  |
|  |  | Sensitive earth fault |  |
|  |  | Negative-sequence overcurrent protection |  |
|  |  | Phase discontinuity Protection |  |
|  |  | Under Frequency Protection in four stages, for loadshedding |  |
|  |  | Over/under voltage protection |  |
|  |  | Three-phase thermal protection for feeders, cables and distribution transformers |  |
|  |  | Multi-shot auto-reclose |  |
|  |  | Circuit breaker failure Protection |  |
|  |  | Arc Protection |  |
| Logic |  | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| Condition monitoring |  | Non-volatile memory for; |  |
|  |  | Circuit-breaker condition Monitoring |  |
|  |  | Trip circuit supervision |  |
|  |  | Trip counters for circuit-breaker |  |
|  |  | Current circuit supervision |  |
|  |  | Disturbance (event) recorder |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
| Measurement |  | Residual current |  |
|  |  | Phase unbalance |  |
|  |  | Thermal level |  |
|  |  | HMI/Binary input based open/close control of switchgear. |  |
| Communication |  | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | Provide two Fibre Optic ports for connection to Industrial network switch. |  |
|  |  | Provide GPS for IED time synchronization. |  |
|  |  | All relay interrogation hardware and software |  |
| AC Current Inputs |  | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  | High immunity to 88 saturation and harmonic distortion |  |
| Auxiliary Voltage |  | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| Frequency |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| Light Emitting Diodes (LEDs) |  | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| Binary Inputs |  | The binary inputs shall; |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
|  |  | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| Relay Terminal Connections |  | At least 4mm2 for the CT circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| Reference International Standard |  | The IEC 60255 standard for protection relays shall apply. |  |
| Product Version |  | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
|  |  | The relays shall have a manufacturer support product life of not less than 7 years |  |
| Current Transformer |  |  |  |
| Core 1 (Metering) – Ratio/Burden/Class |  | 2000/1000/1A, 15VA, Class 0.2 |  |
| Core 2 (Protection) - Ratio/Burden/Class |  | 2000/1000/1A, 15VA, 5P20 |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Circuit Breaker Basic Data |  |  |  |
| Rated voltage (Highest system voltage) | kV | 12 |  |
| Rated continuous current at 40 oC ambient temperature: | A | 2500 |  |
| Interruption Medium |  | Vacuum |  |
| Rated frequency | Hz | 50 |  |
| Rated short time withstand current (3s) | kA | 31.5 |  |
| Closing time | ms | 80 |  |
| Opening time | ms | 45 |  |
| Reclose Sequence |  | O-0.3s-CO-15s-CO |  |
| Termination | kV | Euromould bushings |  |
| Manual Closing/Opening |  | Yes |  |
| Manual charging |  | Yes |  |
| Circuit Breaker Insulation Level |  |  |  |
| Lightning impulse dry withstand voltage | kV | 95 |  |
| One minute power-frequency wet withstand voltage | kV | 28 |  |
| Circuit Breaker Operating Mechanism |  |  |  |
| Mechanism |  | Magnetic/ Motorised Coil actuator trip free mechanism, with mechanical ON/ OFF indicator, operating counter |  |
| Guaranteed No. of operations |  | 10000 |  |
| Rated supply voltage of Trip/Close Coils | V dc | 110/220 |  |
| Rated supply voltage of Spring Charge Motor | V dc | 110/220 |  |
| Spare Auxiliary contacts |  | 6xNO, 6xNC |  |
| Interlocks |  | Mechanical and Electrical (Refer to item 13 in this document under general requirements for details) |  |
| Circuit Breaker Type Test, Drawings and Quality assurance |  |  |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions Further the supplier shall provide: Manuals: Three sets of manuals of all the installed equipment. (Operating and Maintenance Manuals.) Drawings: Three sets of hard copy drawings and one soft copy in CAD version 2004 or later, format. |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 11KV INCOMER CIRCUIT BREAKER FOR SWITCHING STATIONS TECHNICAL SCHEDULE

| Description | Unit | Guaranteed Values |  |
| --- | --- | --- | --- |
| 11KV INCOMER CIRCUIT BREAKER FOR SWITCHING STATIONS |  | ZESCO Minimum Requirements | Tenderer’s Guarantee |
| Switchgear |  |  |  |
| Switchgear Type |  | 11kV indoor circuit breaker complete wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| Switchgear Model |  | Bidder to specify |  |
| Switchgear Manufacturer |  | Bidder to specify |  |
| Country of Manufacture |  | Bidder to specify |  |
| Environmental Conditions |  |  |  |
| Altitude above sea level | m | 1500 |  |
| Humidity | % | 85 |  |
| Guaranteed No. of operations |  | 10000 |  |
| Operating ambient temperature | oC | 2 to 45 |  |
| Specific creepage distance | mm/kV | 31 |  |
| Electrical Endurance Class (IEC 602271) |  | E2 |  |
| Panel – General |  |  |  |
| Type |  | Front access door with window |  |
| Mounting |  | Floor standing |  |
| Panel Dimensions (D X W x H) | mm | Bidder to specify |  |
| Panel Colour |  | RAL 7035 |  |
| Busbar Rated Current | A | 1250 |  |
| Rated Short Time withstand Current | kA | 31.5, for 3 sec. |  |
| Busbar rated Voltage | kV | 11 |  |
| Busbar Insulation level | kV | 17.5 |  |
| Impulse withstand voltage | kV | 95 |  |
| Control / Indications |  |  |  |
| Measurements /Instruments |  | MDI Ammeter / Electronic Energy meter / IED |  |
| Display of Measured Values |  | Electronic Energy meter / IED |  |
| Selector Switches |  | Local/Remote |  |
| Control Switches |  | CB Open/Close |  |
| AC/DC Wiring Protection |  | MCBs |  |
| Alarm Indication |  | On Relay LEDs |  |
| Status Indication |  | On IED |  |
| Panel Heating/Lighting |  | Yes |  |
| Test Interface |  | Yes |  |
| Control |  | Trip /close switch, Local/Remote Selector Switch, Pendant Switch |  |
| Indications |  | CB open, CB closed, Spring not charged,CB test and service postions Earth switch ON, Cable Live |  |
| Anti-pumping Relay |  | Yes |  |
| Protection IED |  |  |  |
| Device |  | IED |  |
| Functions |  | Three-phase overcurrent protection, three stage |  |
|  |  | earth-fault protection, three stage |  |
|  |  | Sensitive earth fault |  |
|  |  | Negative-sequence overcurrent protection |  |
|  |  | Phase discontinuity Protection |  |
|  |  | Under Frequency Protection in four stages, for loadshedding |  |
|  |  | Over/under voltage protection |  |
|  |  | Three-phase thermal protection for feeders, cables and distribution transformers |  |
|  |  | Multi-shot auto-reclose |  |
|  |  | Circuit breaker failure Protection |  |
|  |  | Arc Protection |  |
| Logic |  | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| Condition monitoring |  | Non-volatile memory for; |  |
|  |  | Circuit-breaker condition Monitoring |  |
|  |  | Trip circuit supervision |  |
|  |  | Trip counters for circuit-breaker |  |
|  |  | Current circuit supervision |  |
|  |  | Disturbance (event) recorder |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
| Measurement |  | Residual current |  |
|  |  | Phase unbalance |  |
|  |  | Thermal level |  |
|  |  | HMI/Binary input based open/close control of switchgear. |  |
| Communication |  | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | Provide two Fibre Optic ports for connection to Industrial network switch. |  |
|  |  | Provide GPS for IED time synchronization. |  |
|  |  | All relay interrogation hardware and software |  |
| AC Current Inputs |  | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| Auxiliary Voltage |  | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| Frequency |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| Light Emitting Diodes (LEDs) |  | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| Binary Inputs |  | The binary inputs shall; |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
|  |  | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| Relay Terminal Connections |  | At least 4mm2 for the CT circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| Reference International Standard |  | The IEC 60255 standard for protection relays shall apply. |  |
| Product Version |  | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
|  |  | The relays shall have a manufacturer support product life of not less than 7 years |  |
| METERING |  |  |  |
| Voltage Transformer |  |  |  |
| VT ratio | V | 11kV/√3, 110V/√3, 110/√3 |  |
| Burden | VA | 100/phase |  |
| Class |  | Class 0.2s For metering and Class 3P for protection |  |
| Voltage Factor |  | 1.2 continuous; 1.9/30 sec |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Current Transformer |  |  |  |
| Core 1 (Metering) – Ratio/Burden/Class |  | 800/400/1A, 15VA, Class 0.2 |  |
| Core 2 (Protection) - Ratio/Burden/Class |  | 800/400/1A, 15VA, 5P20 |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Circuit Breaker Basic Data |  |  |  |
| Rated voltage (Highest system voltage) | kV | 12 |  |
| Rated continuous current at 40 °C ambient temperature: | A | 1250 |  |
| Interruption Medium |  | Vacuum |  |
| Rated frequency | Hz | 50 |  |
| Rated short time withstand current (3s) | kA | 31.5 |  |
| Closing time | ms | 80 |  |
| Opening time | ms | 45 |  |
| Reclose Sequence |  | O-0.3s-CO-15s-CO |  |
| Termination | kV | Euromould bushings |  |
| Manual Closing/Opening |  | Yes |  |
| Manual charging |  | Yes |  |
| Circuit Breaker Insulation Level |  |  |  |
| Lightning impulse dry withstand voltage | kV | 95 |  |
| One minute power-frequency wet withstand voltage | kV | 28 |  |
| Circuit Breaker Operating Mechanism |  |  |  |
| Mechanism |  | Magnetic/ Motorised Coil actuator trip free mechanism, with mechanical ON/ OFF indicator, operating counter |  |
| Guaranteed No. of operations |  | 10000 |  |
| Rated supply voltage of Trip/Close Coils | V dc | 110/220 |  |
| Rated supply voltage of Spring Charge Motor | V dc | 110/220 |  |
| Spare Auxiliary contacts |  | 6xNO, 6xNC |  |
| Interlocks |  | Mechanical and Electrical (Refer to item 13 in this document under general requirements for details) |  |
| Cable and Integral Earthing |  |  |  |
| Cable Entry |  | Bottom |  |
| Cable Type |  | XLPE |  |
| No. cores – size |  | 3C x 185mm2 |  |
| Integral Earthing |  | Yes |  |
| Circuit Breaker Type Test, Drawings and Quality assurance |  |  |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions Further the supplier shall provide: Manuals: Three sets of manuals of all the installed equipment. (Operating and Maintenance Manuals.) Drawings: Three sets of hard copy drawings and one soft copy in CAD version 2004 or later, format. |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 11KV OUTGOING FEEDER CIRCUIT BREAKER FOR SWITCHING STATIONS TECHNICAL SCHEDULE

| Description | Unit | Guaranteed Values |  |
| --- | --- | --- | --- |
| 11KV OUTGOING FEEDER CIRCUIT BREAKER FOR SWITCHING STATIONS |  | ZESCO Minimum Requirements | Tenderer’s Guarantee |
| Switchgear |  |  |  |
| Switchgear Type |  | 11kV indoor circuit breaker complete wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| Switchgear Model |  | Bidder to specify |  |
| Switchgear Manufacturer |  | Bidder to specify |  |
| Country of Manufacture |  | Bidder to specify |  |
| Environmental Conditions |  |  |  |
| Altitude above sea level | m | 1500 |  |
| Humidity | % | 85 |  |
| Guaranteed No. of operations |  | 10000 |  |
| Operating ambient temperature | oC | 2 to 45 |  |
| Specific creepage distance | mm/kV | 31 |  |
| Electrical Endurance Class (IEC 602271) |  | E2 |  |
| Panel – General |  |  |  |
| Type |  | Front access door with window |  |
| Mounting |  | Floor standing |  |
| Panel Dimensions (D X W x H) | mm | Bidder to specify |  |
| Panel Colour |  | RAL 7035 |  |
| Busbar Rated Current | A | 1250 |  |
| Rated Short Time withstand Current | kA | 31.5, for 3 sec. |  |
| Busbar rated Voltage | kV | 11 |  |
| Busbar Insulation level | kV | 17.5 |  |
| Impulse withstand voltage | kV | 95 |  |
| Control / Indications |  |  |  |
| Measurements /Instruments |  | MDI Ammeter / Electronic Energy meter / IED |  |
| Display of Measured Values |  | Electronic Energy meter / IED |  |
| Selector Switches |  | Local/Remote |  |
| Control Switches |  | CB Open/Close |  |
| AC/DC Wiring Protection |  | MCBs |  |
| Alarm Indication |  | On Relay LEDs |  |
| Status Indication |  | On IED |  |
| Panel Heating/Lighting |  | Yes |  |
| Test Interface |  | Yes |  |
| Control |  | Trip /close switch, Local/Remote Selector Switch, Pendant Switch |  |
| Indications |  | CB open, CB closed, Spring not charged,CB test and service postions Earth switch ON, Cable Live |  |
| Anti-pumping Relay |  | Yes |  |
| Protection IED |  |  |  |
| Device |  | IED |  |
| Functions |  | Three-phase overcurrent protection, three stage |  |
|  |  | earth-fault protection, three stage |  |
|  |  | Sensitive earth fault |  |
|  |  | Negative-sequence overcurrent protection |  |
|  |  | Phase discontinuity Protection |  |
|  |  | Under Frequency Protection in four stages, for loadshedding |  |
|  |  | Over/under voltage protection |  |
|  |  | Three-phase thermal protection for feeders, cables and distribution transformers |  |
|  |  | Multi-shot auto-reclose |  |
|  |  | Circuit breaker failure Protection |  |
|  |  | Arc Protection |  |
| Logic |  | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| Condition monitoring |  | Non-volatile memory for; |  |
|  |  | Circuit-breaker condition Monitoring |  |
|  |  | Trip circuit supervision |  |
|  |  | Trip counters for circuit-breaker |  |
|  |  | Current circuit supervision |  |
|  |  | Disturbance (event) recorder |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
| Measurement |  | Residual current |  |
|  |  | Phase unbalance |  |
|  |  | Thermal level |  |
|  |  | HMI/Binary input based open/close control of switchgear. |  |
| Communication |  | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | Provide two Fibre Optic ports for connection to Industrial network switch. |  |
|  |  | Provide GPS for IED time synchronization. |  |
|  |  | All relay interrogation hardware and software |  |
| AC Current Inputs |  | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| Auxiliary Voltage |  | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| Frequency |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| Light Emitting Diodes (LEDs) |  | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| Binary Inputs |  | The binary inputs shall; |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
|  |  | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| Relay Terminal Connections |  | At least 4mm2 for the CT circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| Reference International Standard |  | The IEC 60255 standard for protection relays shall apply. |  |
| Product Version |  | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
|  |  | The relays shall have a manufacturer support product life of not less than 7 years |  |
| METERING |  |  |  |
| Current Transformer |  |  |  |
| Core 1 (Metering) – Ratio/Burden/Class |  | 600/300/1A, 15VA, Class 0.2 |  |
| Core 2 (Protection) - Ratio/Burden/Class |  | 600/300/1A, 15VA, 5P20 |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Circuit Breaker Basic Data |  |  |  |
| Rated voltage (Highest system voltage) | kV | 12 |  |
| Rated continuous current at 40 oC ambient temperature: | A | 630 |  |
| Interruption Medium |  | Vacuum |  |
| Rated frequency | Hz | 50 |  |
| Rated short time withstand current (3s) | kA | 31.5 |  |
| Closing time | ms | 80 |  |
| Opening time | ms | 45 |  |
| Reclose Sequence |  | O-0.3s-CO-15s-CO |  |
| Termination | kV | Euromould bushings |  |
| Manual Closing/Opening |  | Yes |  |
| Manual charging |  | Yes |  |
| Circuit Breaker Insulation Level |  |  |  |
| Lightning impulse dry withstand voltage | kV | 95 |  |
| One minute power-frequency wet withstand voltage | kV | 28 |  |
| Circuit Breaker Operating Mechanism |  |  |  |
| Mechanism |  | Magnetic/ Motorised Coil actuator trip free mechanism, with mechanical ON/ OFF indicator, operating counter |  |
| Guaranteed No. of operations |  | 10000 |  |
| Rated supply voltage of Trip/Close Coils | V dc | 110/220 |  |
| Rated supply voltage of Spring Charge Motor | V dc | 110/220 |  |
| Spare Auxiliary contacts |  | 6xNO, 6xNC |  |
| Interlocks |  | Mechanical and Electrical (Refer to item 13 in this document under general requirements for details) |  |
| Cable and Integral Earthing |  |  |  |
| Cable Entry |  | Bottom |  |
| Cable Type |  | XLPE |  |
| No. cores – size |  | 3C x 185mm2 |  |
| Integral Earthing |  | Yes |  |
| Circuit Breaker Type Test, Drawings and Quality assurance |  |  |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions Further the supplier shall provide: Manuals: Three sets of manuals of all the installed equipment. (Operating and Maintenance Manuals.) Drawings: Three sets of hard copy drawings and one soft copy in CAD version 2004 or later, format. |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 11KV BUS SECTION CIRCUIT BREAKER FOR SWITCHING STATIONS TECHNICAL SCHEDULE

| Description | Unit | Guaranteed Values |  |
| --- | --- | --- | --- |
| 11KV BUS SECTION CIRCUIT BREAKER FOR SWITCHING STATIONS |  | ZESCO Minimum Requirements | Tenderer’s Guarantee |
| Switchgear |  |  |  |
| Switchgear Type |  | 11kV indoor circuit breaker complete wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| Switchgear Model |  | Bidder to specify |  |
| Switchgear Manufacturer |  | Bidder to specify |  |
| Country of Manufacture |  | Bidder to specify |  |
| Environmental Conditions |  |  |  |
| Altitude above sea level | m | 1400 |  |
| Humidity | % | 85 |  |
| Guaranteed No. of operations |  | 10000 |  |
| Operating ambient temperature | oC | 2 to 45 |  |
| Specific creepage distance | mm/kV | 31 |  |
| Electrical Endurance Class (IEC 602271) |  | E2 |  |
| Panel – General |  |  |  |
| Type |  | Front access door with window |  |
| Mounting |  | Floor standing |  |
| Panel Dimensions (D X W x H) | mm | Bidder to specify |  |
| Panel Colour |  | RAL 7035 |  |
| Busbar Rated Current | A | 1250 |  |
| Rated Short Time withstand Current | kA | 31.5, for 3 sec. |  |
| Busbar rated Voltage | kV | 11 |  |
| Busbar Insulation level | kV | 17.5 |  |
| Impulse withstand voltage | kV | 95 |  |
| Control / Indications |  |  |  |
| Measurements /Instruments |  | MDI Ammeter / Electronic Energy meter / IED |  |
| Display of Measured Values |  | Electronic Energy meter / IED |  |
| Selector Switches |  | Local/Remote |  |
| Control Switches |  | CB Open/Close |  |
| AC/DC Wiring Protection |  | MCBs |  |
| Alarm Indication |  | On Relay LEDs |  |
| Status Indication |  | On IED |  |
| Panel Heating/Lighting |  | Yes |  |
| Test Interface |  | Yes |  |
| Control |  | Trip /close switch, Local/Remote Selector Switch, Pendant Switch |  |
| Indications |  | CB open/closed, Spring not charged,CB test and service postions |  |
| Anti-pumping Relay |  | Yes |  |
| Bus bar earthing |  | Using a busbar earthing panel complete with three phase earth switch or busbar earthing handcart including all safety interlocks |  |
| Protection IED |  |  |  |
| Device |  | IED |  |
| Functions |  | Three-phase overcurrent protection, three stage |  |
|  |  | earth-fault protection, three stage |  |
|  |  | Sensitive earth fault |  |
|  |  | Negative-sequence overcurrent protection |  |
|  |  | Phase discontinuity Protection |  |
|  |  | Under Frequency Protection in four stages, for loadshedding |  |
|  |  | Over/under voltage protection |  |
|  |  | Three-phase thermal protection for feeders, cables and distribution transformers |  |
|  |  | Multi-shot auto-reclose |  |
|  |  | Circuit breaker failure Protection |  |
|  |  | Arc Protection |  |
| Logic |  | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| Condition monitoring |  | Non-volatile memory for; |  |
|  |  | Circuit-breaker condition Monitoring |  |
|  |  | Trip circuit supervision |  |
|  |  | Trip counters for circuit-breaker |  |
|  |  | Current circuit supervision |  |
|  |  | Disturbance (event) recorder |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
| Measurement |  | Residual current |  |
|  |  | Phase unbalance |  |
|  |  | Thermal level |  |
|  |  | HMI/Binary input based open/close control of switchgear. |  |
| Communication |  | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | Provide two Fibre Optic ports for connection to Industrial network switch. |  |
|  |  | Provide GPS for IED time synchronization. |  |
|  |  | All relay interrogation hardware and software |  |
| AC Current Inputs |  | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| Auxiliary Voltage |  | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| Frequency |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| Light Emitting Diodes (LEDs) |  | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| Binary Inputs |  | The binary inputs shall; |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
|  |  | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| Relay Terminal Connections |  | At least 4mm2 for the CT circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| Reference International Standard |  | The IEC 60255 standard for protection relays shall apply. |  |
| Product Version |  | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
|  |  | The relays shall have a manufacturer support product life of not less than 7 years |  |
| METERING |  |  |  |
| Current Transformer |  |  |  |
| Core 1 (Metering) – Ratio/Burden/Class |  | 800/400/1A, 15VA, Class 0.2 |  |
| Core 2 (Protection) - Ratio/Burden/Class |  | 800/400/1A, 15VA, 5P20 |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |
| Circuit Breaker Basic Data |  |  |  |
| Rated voltage (Highest system voltage) | kV | 12 |  |
| Rated continuous current at 40 oC ambient temperature: | A | 1250 |  |
| Interruption Medium |  | Vacuum |  |
| Rated frequency | Hz | 50 |  |
| Rated short time withstand current (3s) | kA | 31.5 |  |
| Closing time | ms | 80 |  |
| Opening time | ms | 45 |  |
| Reclose Sequence |  | O-0.3s-CO-15s-CO |  |
| Termination | kV | Euromould bushings |  |
| Manual Closing/Opening |  | Yes |  |
| Manual charging |  | Yes |  |
| Circuit Breaker Insulation Level |  |  |  |
| Lightning impulse dry withstand voltage | kV | 95 |  |
| One minute power-frequency wet withstand voltage | kV | 28 |  |
| Circuit Breaker Operating Mechanism |  |  |  |
| Mechanism |  | Magnetic/ Motorised Coil actuator trip free mechanism, with mechanical ON/ OFF indicator, operating counter |  |
| Guaranteed No. of operations |  | 10000 |  |
| Rated supply voltage of Trip/Close Coils | V dc | 110/220 |  |
| Rated supply voltage of Spring Charge Motor | V dc | 110/220 |  |
| Spare Auxiliary contacts |  | 6xNO, 6xNC |  |
| Interlocks |  | Mechanical and Electrical (Refer to item 13 in this document under general requirements for details) |  |
| Cable and Integral Earthing |  |  |  |
| Cable Entry |  | Bottom |  |
| Cable Type |  | XLPE |  |
| No. cores – size |  | 3C x 185mm2 |  |
| Integral Earthing |  | Yes |  |
| Circuit Breaker Type Test, Drawings and Quality assurance |  |  |  |
| Type Test |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| Drawings |  | Supplier shall provide drawings showing dimensions Further the supplier shall provide: Manuals: Three sets of manuals of all the installed equipment. (Operating and Maintenance Manuals.) Drawings: Three sets of hard copy drawings and one soft copy in CAD version 2004 or later, format. |  |
| Quality assurance |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 11KV SURGE ARRESTERS

| Item | Detail | Units | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- |
| 1 | Type of arrester |  | 11kV gapless type metal oxide surge arrester – Station class |  |
| 2 | Nominal system voltage | kV | 11 |  |
| 3 | Highest system voltage | kV | 12 |  |
| 4 | Basic Insulation Level (BIL) | kV | 95 |  |
| 5 | #### Ratings and type of surge arrester |  |  |  |
| 5.1 | Specification to which surge arrester complies |  | IEC 60099-4:1991 |  |
| 5.2 | Rated voltage of surge arrester | kV | 12 |  |
| 5.3 | Nominal, 8/20 µs, discharge current rating of surge arrester | kA | 10 |  |
| 5.4 | Maximum continuous operating voltage of surge arrester | kV | 10.2 |  |
| 5.5 | Gapless or gapped type metal-oxide surge arrester |  | Gapless |  |
| 5.6 | Material of insulation |  | Silicon Rubber |  |
| 5.7 | Cantilever strength of surge arrester |  | 300 |  |
| 5.8 | Rated frequency of surge arrester | Hz | 50 |  |
| 5.9 | Design altitude of surge arrester (above sea level) | m | 1 500m |  |
| 5.10 | Design ambient temperature of surge arrester | oC | -1 to 40 |  |
| 5.11 | Specific phase-to-ground creepage of surge arrester | .mm/kV | 31 |  |
| 6 | Automatic earth lead disconnectors requirements |  |  |  |
| 6.1 | Are automatic earth lead disconnectors fitted? |  | YES |  |
| 6.2 | Corrosion protection of metal and alloy parts: galvanizing specification and/or stainless-steel grade |  | See 5.4 (e.g. SABS 763, 316 stainless steel, etc.) |  |
| 7 | Installation arrangement |  |  |  |
| 7.1 | Maximum angle from vertical at which surge arrester is fully functional |  | 45 |  |
| 8 | Test |  |  |  |
| 8.1 | Are test reports available from a recognized authority? |  | YES |  |
| 8.2 | Minimum one-minute wet power frequency withstand voltage of external insulation of surge arrester housing | kV | 28 |  |
| 8.3 | Maximum steep current impulse residual voltage for a 10 kA, 1/20 µs, discharge current | kV | 50 |  |
| 8.4 | Maximum lightning impulse residual voltage for a 10 kA, 8/20 µs, discharge current | kV | 40 |  |
| 8.5 | Lightning, 1,2/50 µs, impulse withstand level of external insulation of surge arrester housing |  | 80 |  |
| 8.6 | Line discharge class rating |  | 1 |  |
| 8.7 | Long duration current, 2 000 µs, impulse withstand | A | 250 A |  |
| 8.8 | High current, 4/10 µs, impulse withstand | kA | 100 kA |  |
| 8.9 | Is the automatic earth lead disconnector tested in accordance with IEC 60099-4 |  | YES |  |
| 8.10 | Specification to which the pressure relief device complies |  | IEC 60099-1 |  |
| 8.11 | High current pressure relief value | kA | 15 kA |  |
| 8.12 | Low current pressure relief value | kA | 0.8 kA |  |
| 8.13 | Maximum radio influence voltage at 1 MHz, with the surge arrester energized at the rated voltage | µV | 250 µV |  |
| 8.14 | Type tests |  | Supplier to provide previous type test certificate/results together with the bid |  |
| 8.15 | Routine test |  | Supplier to provide routine test certificate/results together on delivery |  |
| 8.16 | Drawing |  | Supplier to provide drawings showing dimensions with the bid |  |
| 8.17 | Quality Assurance |  | Supplier to provide Quality Assurance certificate with the bid |  |
| 8.18 | Technical details/brochure |  | Bidders to provide complete technical details/brochure with the bid |  |
| 8.19 | Galvanized steel supports complete with bolts |  | To be provided by the supplier |  |

### LOW VOLTAGE A.C. SWITCHBOARDS SCHEDULE 4a TECHNICAL GUARANTEES

| LOW VOLTAGE A.C. SWITCHBOARDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig. | Tolerance |
| 1.1 | For all Equipment |  |  |  |
|  | - Rated voltage | V |  |  |
|  | - Service voltage | V |  |  |
|  | - Rated frequency | Hz |  |  |
|  | - Power frequency test voltage, 1 min. | kV |  |  |
| 1.2 | Main Switchboard's Busbars |  |  |  |
|  | - Rated current | A |  |  |
|  | - Thermal overload capacity, 1 sec. | kArms |  |  |
|  | - Dynamic capacity | kA peak |  |  |
|  | - Temperature rise of busbars at rated current | °C |  |  |
| 1.3 | Circuit Breakers (to be filled in for each type and size) |  |  |  |
|  | - Rated current | A |  |  |
|  | - Power frequency test voltage, 1 min. | kV |  |  |
|  | - Permissible short-time current, 1 sec. | kArms |  |  |
|  | - Dynamic short time current | kA peak |  |  |
|  | - Breaking capacity at service voltage | kArms |  |  |
|  | - Making capacity | kA peak |  |  |
|  | - Temperature rise of the contacts at rated current | °C |  |  |
| 1.4 | Current Transformers |  |  |  |
|  | - Rated primary current | A |  |  |
|  | - Rated secondary current | A |  |  |
|  | - Power frequency test voltage, 1 min |  |  |  |
|  | - primary | kV |  |  |
|  | - secondary | kV |  |  |
|  | - Thermal overload capacity, 1 sec. | kArms |  |  |
|  | - Dynamic capacity | kA peak |  |  |
|  | - Cores for measuring instruments |  |  |  |
|  | - burden | VA |  |  |
|  | - class |  |  |  |
|  | - instrument security factor |  |  |  |

### SCHEDULE 3a TECHNICAL GUARANTEES

| LOW VOLTAGE A.C. SWITCHBOARDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
|  | - Cores for protection relays |  |  |  |
|  | - burden | VA |  |  |
|  | - class |  |  |  |
|  | - accuracy limit factor |  |  |  |
| 1.5 | Manufacturer's Name |  |  |  |
|  | - Main switchboards |  |  |  |
|  | - Circuit breakers |  |  |  |
|  | - Sub-distribution limit factor |  |  |  |
| 1.6 | Country of Manufacture |  |  |  |
|  | - Main switchboards |  |  |  |
|  | - Circuit breakers |  |  |  |
|  | - Sub-distribution limit factor |  |  |  |

### LOW VOLTAGE A.C. SWITCHBOARDS SCHEDULE 4b INFORMATIVE DATA

| LOW VOLTAGE A.C. SWITCHBOARDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
| b.1 | Main Switchboards |  |  |  |
|  | - Reference standard |  |  |  |
|  | - Type designation |  |  |  |
|  | - Overall dimensions |  |  |  |
|  | - length | mm |  |  |
|  | - width | mm |  |  |
|  | - height | mm |  |  |
|  | - Weight of complete board |  |  |  |
| b.2 | Circuit Breakers and Contactors (to be filled in for each type and size) |  |  |  |
|  | - Reference standard |  |  |  |
|  | - Type designation |  |  |  |
|  | - Type of main contacts |  |  |  |
|  | - Type of arc control device |  |  |  |
|  | - Weight | kg |  |  |
|  | - Power consumption |  |  |  |
|  | - closing coil | W |  |  |
|  | - tripping coil | W |  |  |
|  | - motor, when starting | W |  |  |
|  | - motor, when running | W |  |  |
|  | - Running time for motor for loading the spring | sec. |  |  |
| b.3 | Current Transformers |  |  |  |
|  | - Type |  |  |  |
|  | - Weight | kg |  |  |
|  | - Type of insulation |  |  |  |
| b.4 | Sub-distribution Boards (to be filled in for each type) |  |  |  |
|  | - Type |  |  |  |
|  | - Dimensions |  |  |  |
|  | - length |  |  |  |
|  | - width |  |  |  |
|  | - height |  |  |  |
|  | - Weight |  |  |  |

## SPECIFICATION FOR SUBSTATION DC BATTERY BANK

### GENERAL DESCRIPTION

This specification covers the supply of a DC battery bank and/or charger for substation application to operate the following equipment but not limited to circuit breakers, motor operated switches, SCADA RTU, emergency lights, data recording equipment, auxiliary relays and protective relays.

### STANDARDS

The battery furnished shall be designed, manufactured, tested and shall meet the performances in accordance with the latest applicable IEC and IEEE standards.

### DESIGN

The battery offered shall be of the maintenance free Valve Regulated Lead Acid (VRLA) type. The batteries shall be supplied complete with a plastic covered heavy duty steel rack for stacking/assembly of the battery.

The arrangement of the rack shall be such as to allow for easy access and adequate space for normal maintenance in a battery room.

The battery cells shall be hermetically sealed, sturdy, weatherproof and long lasting. The safety valves, if provided shall be explosion free.

Each container shall be permanently labelled with information such as manufacturer, volt/cell, and Ah capacity @ 10hr rate of discharge.

The battery shall be shipped dry and fully charged. Accessories including electrolyte shall be shipped in separate cartons.

Each battery set to be supplied with two spare cells, dry and fully charged.

Battery to be supplied with inter-cell connectors including bolts and nuts and appropriately sized cable(s) of not less than 30m.

For VRLA cells, the following shall be included for each battery set;

Set of special tools if required.

### ZESCO MINIMUM TECHNICAL REQUIREMENTS FOR DC BATTERY BANK

| Item | Technical Detail | Units | ZESCO Requirements | Bidder Guarantee |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 110V DC battery |  |  |
| 1 | DC Output Voltage | V | 110 or 220 |  |  |
| 2 | Capacity @ 10hr discharge rate | Ah | 10hrs Autonomy |  |  |
| 3 | Type of Battery |  | VRLA or Lithium |  |  |
| 4 | Number of cells for battery |  | Enough to give 110 or 220 DC output nominal + 2 cells as spares |  |  |
| 5 | Cell Float Voltage | V | 1.85 – 2.2 (VRLA) |  |  |
|  |  |  | 3.2 – 3.5 (Lithium) |  |  |
| 6 | Cell Dimension | mm |  |  |  |
| 7 | Material of container |  |  |  |  |
| 8 | Material for terminals |  |  |  |  |
| 9 | Short circuit rating of terminal/connectors leads | kA |  |  |  |
| 10 | Installation rack to be provided |  | Yes |  |  |
| 11 | Rack dimension | mm |  |  |  |
| 12 | Operating Temperature | oC | -1 to + 40 |  |  |
| 13 | Humidity | % | 20-90 |  |  |

SUBMITTALS:

Manufacturer’s product description, catalogue data and information.

Installation, Operation and maintenance manual including recommended spare parts.

#### SPECIFICATION FOR DC BATTERY CHARGER

The charger shall be of the automatic constant voltage output free standing type designed for float charge operation. They shall be suitable for operation from the 230V, ±10% AC supply, 50Hz. The charger shall have the following design and performance characteristics:

| Item | Item Description | ZESCO Min. REQUIREMENT | Bidder Guarantee |
| --- | --- | --- | --- |
| 1 | quantity | 01 |  |
| 2 | input | 380V Ac, 3ph, 50hz/400V AC, 3ph, 50hz |  |
| 3 | output | 110V or 220V dc nominal |  |
| 4 | float voltage | 129V or 258V dc |  |
| 5 | boost voltage | 142V or 284V dc |  |
| 6 | charger rating | 0.2C to 0.4C |  |
| 7 | standing load | 0.5C |  |
| 8 | charger type | Thyristor controlled six pulse constant voltage current limit type (CVC) |  |
| 9 | smoothing | 5% p-p Volts (0.7% of battery Ah capacity C/5) |  |
| 10 | regulation | ± 10% mains variation, ≤ ±1% on DC output. |  |
| 11 | major components | 1/3ph + n AC input protection MCB (HRC fuses) AC input MOV surge suppression Mains on neon lamp Double wound single phase mains transformer + earth screen Thyristor controller module Thyristor stack on heat sinks Hole storage protection Switch (internally mounted) for Normal/Initial DC smoothing choke + capacitor(s). |  |
| 12 | indications | Flush mounted dc output Ammeter, 0-150A Flush mounted DC Voltmeter, 0-160/450V Flush mounted AC Voltmeter, 0-250/450V Control/Ammeter shunts |  |
| 13 | alarms | Charger fail alarm Mains failure Low Volt/Battery Fail alarm High Volt alarm 28 day auto battery boost 12 hourly auto battery test system |  |
| 14 | protection | AC input protection MCB DC output fuse for reverse polarity protection Automatic current limiting into load fault condition Input/Output alarm terminals |  |
| 15 | cabinet | Floor standing non-self-contained, with front access via a pad lockable hinged front door. |  |
| 16 | finish | Standard powder coating with final colour light grey. Ingress protection IP 54 |  |
| 17 | cable entry | Bottom only vi undrilled galvanised steel bolted removable gland plates |  |
| 18 | operating conditions | Altitude: 1500m a.s.l Temperature: -1 to 40 oC Humidity: 20-90 % Cooling: Natural air convection |  |
| 19 | rated output | 0.5C |  |

#### DC SUPPLY SCHEDULE 5a TECHNICAL GUARANTEES (additional)

| DC SUPPLY |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
| a.1 | Batteries (to be filled in for each type of battery) |  |  |  |
|  | - Rated voltage | V |  |  |
|  | - Max. variation of voltage under all conditions of service | % |  |  |
|  | - Number of cells |  |  |  |
|  | - Capacity at 10h, 40°C | Ah |  |  |
|  | - Discharge time of the batteries | hours |  |  |
|  | - Current during this discharge | A |  |  |
| a.2 | Chargers (to be filled in for each type of charger) |  |  |  |
|  | - Rated voltage of the DC mains | V |  |  |
|  | - Rated current of the DC mains | A |  |  |
|  | - Supply voltage | V |  |  |
|  | - Rated frequency | Hz |  |  |
|  | - Stability of the output voltage | % |  |  |
|  | - Max. deviation of the current limitation at rated current | % |  |  |
|  | - Max. ripple (without the battery connected in parallel) | % P/P |  |  |
|  | - Max. charging time of completely discharged battery, with the load being connected | hours |  |  |
| a.3 | 110/220 V DC Main Distributions |  |  |  |
|  | - Rated voltage | V |  |  |
|  | - Rated current of the busbars | A |  |  |
|  | - Test voltage, 1 min. | kV |  |  |
| a.4 | 48 V DC Main Distribution |  |  |  |
|  | - Rated voltage | V |  |  |
|  | - Rated current of the busbars | A |  |  |
|  | - Test voltage, 1 min | kV |  |  |

#### SCHEDULE 5a TECHNICAL GUARANTEES

| DC SUPPLY |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
| a.5 | Manufacturer's Name |  |  |  |
|  | - 110/220 V batteries |  |  |  |
|  | - 48 V batteries |  |  |  |
|  | - Chargers |  |  |  |
|  | - Main distribution boards |  |  |  |
| a.6 | Country of Manufacture |  |  |  |
|  | - 110 V batteries |  |  |  |
|  | - 48 V batteries |  |  |  |
|  | - Chargers |  |  |  |
|  | - Main distribution boards |  |  |  |

#### DC SUPPLY SCHEDULE 5b INFORMATIVE DATA

| DC SUPPLY |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
| b.1 | Batteries (to be filled in for each type of battery |  |  |  |
|  | - Type |  |  |  |
|  | - Type of cells |  |  |  |
|  | - Max. charging current | A |  |  |
|  | - Floating charging current | A |  |  |
|  | - Floating charging voltage | V |  |  |
|  | - Acid density of fully charged battery | °BE |  |  |
|  | - Water consumption per cell per year | cm3 |  |  |
|  | - Internal resistance per cell | ohm |  |  |
|  | - Internal resistance of the complete battery | ohm |  |  |
|  | - Max. permissible ambient air temperature | °C |  |  |
|  | - Material of the cell containers |  |  |  |
|  | - Material of the battery terminals |  |  |  |
|  | - Type of connection between the cells |  |  |  |
|  | - Weight per cell including acid | kg |  |  |
|  | - Weigh of the complete battery including acid and wood bases | kg |  |  |
|  | - Overall dimension of the complete battery including the wood bases |  |  |  |
|  | - length | mm |  |  |
|  | - height | mm |  |  |
|  | - width | mm |  |  |
| b.2 | Chargers (to be filled in for each type of charger) |  |  |  |
|  | - Type |  |  |  |
|  | - Max. load current with battery fully charged | A |  |  |
|  | - Max. load current with battery discharged | A |  |  |
|  | - Output voltage with battery fully charged | V |  |  |
|  | - Output voltage with battery discharged | V |  |  |
|  | - Max. AC power consumption at rated load | kVA |  |  |
|  | - Rated rupturing current of the breakers | kA |  |  |
|  | - Fuses | A |  |  |
|  | - Weight | kg |  |  |

#### SCHEDULE 5b INFORMATIVE DATA

| DC SUPPLY |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
|  | - Overall dimensions |  |  |  |
|  | - length | mm |  |  |
|  | - height | mm |  |  |
|  | - width | mm |  |  |
| b.3 | 110 V Main Distribution |  |  |  |
|  | - Type |  |  |  |
|  | - Overall dimensions |  |  |  |
|  | - length | mm |  |  |
|  | - height | mm |  |  |
|  | - width | mm |  |  |
|  | - Weight | kg |  |  |
| b.4 | 48 V Main Distributions |  |  |  |
|  | - Type |  |  |  |
|  | - Overall dimensions |  |  |  |
|  | - length | mm |  |  |
|  | - height | mm |  |  |
|  | - width | mm |  |  |
|  | - Weight | kg |  |  |

### METERING TECHNICAL GUARANTEES

#### Meter Specifications

| Item | Detail | Unit | ZESCO Data | Bidder’s Guaranteed Technical Data |
| --- | --- | --- | --- | --- |
| 1 | Nominal Voltage, (phase to phase) Un | V | 110 |  |
| 2 | Capabilities |  | Time of use (TOU) metering, Import and Export measuring, shall record the kWh, kVAh, kVArh, and the Maximum Demand (kVA, kW) with date & time of occurrence for both import and export directions. The Maximum Demand shall be user programmable to kVA or kW. ALL READINGS TO BE PRIMARY VALUES. Instrument Transformer CT and VT ratios shall be programmable on the meter. The readings shall be scalable to Mega or kilo depending on magnitude. |  |
| 3 | Voltage Range | V | 80 – 115%Un |  |
| 4 | Tolerance | % | -20, +15 |  |
| 5 | Supply Frequency | Hz | 50 |  |
| 6 | Frequency Variation | % | ±2.5 |  |
| 7 | Current Rating, In | A | 1/5 programmable to any CT ratio |  |
| 8 | Starting Current (0.002 In) | mA | 2/10 |  |
| 9 | Maximum Current Rating (1.5 In) | A | 1.5/7.5 |  |
| 10 | Maximum Power Consumption | VA W | 15 3 |  |
| 11 | Integration Period |  | User programmable (1 to 60 minutes) |  |
| 12 | System |  | 3 phase 4 wire, 3 phase 3 wire. The meter shall be programmable for the two systems. |  |
| 13 | Accuracy Class |  | Class 0.2s or better |  |
| 14 | Short Circuit Rating | A | 20Imax |  |
| 15 | Impulse Voltage | kV | 3 |  |
| 16 | CT Polarity reversal |  | Able to detect and record date of occurrence and restoration with phase identification |  |
| 17 | Operating Temperature Range | oC | -5, +50 |  |
| 18 | Altitude | m | 1400 |  |
| 19 | Humidity | % | 85 |  |
| 20 | IP Rating |  | IP54 |  |
| 21 | Installation |  | At least two seals |  |
| 22 | Meter Display Information and measurements |  | 9-digit electronic display |  |
| 23 | Communications |  | As in section 2 below. |  |
| 24 | Over-current protection with a short circuit current | kA | 2.5 |  |
| 25 | Meter shall have provision for the user to view a pre-configured cycle | YES/NO | YES |  |
| 26 | Lightning protection according to: |  | BS 1524 and IEC62053-22 |  |
| 27 | Anti-Tempering Features |  | Tamper protection Tamper logging/indications AMR functionalities |  |
| 28 | Applicable electronic Meter software | Lot | Windows based software for site programming and downloading. The meter should be fully user programmable and downloadable. |  |
| 29 | Time of Use Registers (TOU) | No. | 8 |  |
| 30 | Maximum Demand Registers | No. | 8 |  |
| 31 | Volt Free Output Relays (Internal & normally open) for energy pulse outputs. | No. | 4 |  |
| 32 | Casing |  | House Service Pattern Case, extended Terminal Cover |  |
| 33 | Historical Data |  | Load Profiling (450 days, 1 Channel, 30 minutes), at least twelve months historical active energy, reactive energy and maximum demand billing data logging in meter memory. At least twelve months of sets of historical data |  |
| 34 | Quality Assurance Certificate |  | To be provided with the bid |  |
| 35 | Routine test results |  | To be provided on delivery of meters |  |
| 36 | Previous Type test results |  | To be provided with the bid |  |
| 37 | Meter features and functionalities brochure including drawings showing dimensions of meter |  | To be provided with the bid |  |
| 38 | Applicable standards |  | IEC 62052-11, IEC 62053-21, IEC 62053-22, IEC 62053-23, IEC 62053-61, IEC 62056 |  |
| 39 | Sample meter |  | To be provided with bid |  |

#### Panel Specifications

| Item | Details | Data | Bidder’s Guaranteed Technical Data |
| --- | --- | --- | --- |
| 1 | Mounting | Indoor floor standing |  |
| 2 | Material | Made of metal. Should not corrode, weather resistant, easily cleaned and can be painted. |  |
| 4 | Enclosures Accessories | Meter test terminal blocks with shorting links provisions for current circuits and isolating links for voltages. Mounting rails for terminal blocks for currents and voltages. Glanded or shrouded cable entry and exit holes. The panels should be vermin proof. The panel should have earth bar. The panel should have 230V A.C. supply provision and lighting. |  |
| 5 | IP Rating | IP31 |  |
| 6 | Panel door | Front doors Hinged on the right (right hand opening) and rubber lined. |  |
| 7 | Colour | Grey |  |
| 8 | Environmental temperature withstands | -,+5, + 40oC |  |
| 9 | Viewing window | Front door shall have shatterproof window for viewing status of meters. |  |
| 10 | Samples drawings and pictures | To be provided at bidding. Panel should generally be similar to the existing ZESCO metering panels in size and provisions. Dimensions: The front view dimensions: 800mm x2200mm Side view dimensions: 830mm x 2200mm Outside door dimension: 760mm x 1930mm View Glass: 420mm x 1570mm Inner door: 700mm x 1870mm. Pictures attached. |  |

#### Meter enclosure

| Item | Details | Data | Bidder’s Guaranteed Technical Data |
| --- | --- | --- | --- |
| 1 | Mounting | Wall mountable. Mounting metal straps and/or brackets to be provided with all mounting accessories. |  |
| 2 | Material | Heat and fire resistant Resistance to fire spread, UV stable polycarbonate/ABS blend with flame retardant (IEC 60695-2-1). No toxic gases emission. Should not corrode, weather resistant, easily cleaned and can be painted. |  |
| 4 | Enclosures Accessories | Meter test terminal locks with shorting links provisions for current circuits and isolating links for voltages. Terminal block should have cover and sealable. Glanded or shrouded cable entry and exit holes. The shrouds/glands should be ingress protected, IP65. |  |
| 5 | IP Rating | 65 |  |
| 6 | Enclosure door | Sealable and lockable with standard key. Hinged on the right (right hand opening). |  |
| 7 | Standard | Compliant to BS 8567 |  |
| 8 | Area Application | Outdoor and in difficult conditions |  |
| 9 | Colour | White |  |
| 11 | Environmental temperature withstands | -5, +50 oC |  |
| 14 | Security Sealing | At least Two sealing points |  |
| 15 | Viewing window | Enclosure should have transparent viewing window to view status of meter |  |
| 16 | Sample drawings and pictures | To be provided with bid |  |

#### Metering Server

| S/N | DESCRIPTION | BIDDER’S GUARANTEED TECHNICAL DATA |
| --- | --- | --- |
| 1 | HP Proliant DL380 Rack Server/Dell Power Edge R750 |  |
| 2 | Complete Ventilated Rack mounted Packaging |  |
| 3 | 500W Dual power supply Efficient Chassis |  |
| 4 | Linux Server OS UK |  |
| 5 | Linux 64 Bit Factory Image Recovery |  |
| 6 | Intel Xeon 2.80Ghz CPU or better |  |
| 7 | 64GB DDR3-1600 ECC (4x16GB) RAM |  |
| 9 | NVIDIA NVS 310 512MB Graphics |  |
| 10 | NVIDIA NVS 310 512MB 2nd Graphics |  |
| 11 | 4TB SATA Solid State Hard Drive in RAID-5 |  |
| 12 | USB Standard Keyboard |  |
| 13 | USB Optical Scroll Mouse |  |
| 14 | 16X SuperMulti DVDRW SATA 1st ODD |  |
| 15 | 4 x Intel CT x1 PCIe NIC |  |
| 16 | 3-Year Warranty EURO |  |
| 17 | RAID Card |  |
| 18 | Processor Air Cooling Kit |  |
| 19.0 | Software Operating system |  |
| 19.1 | Linux Server Office |  |
| 19.2 | Microsoft Office 2019 OEM Basic Anti-virus |  |
| 19.3 | McAfee, 1year SW updates included |  |
| 20 | Monitors: 17-inch LED Monitor built into Server Rack |  |

#### Note: This specification constitutes the minimum requirement for the server. It must come installed with all relevant software to make it fully functional as an AMI metering server.

#### Metering Workstation

| Item | Description | Bidder’s Guaranteed Technical Data |
| --- | --- | --- |
| 1 | HP Z420 Workstation |  |
| 2 | HP Single Unit Packaging |  |
| 3 | HP Z420 600W 90% Efficient Chassis |  |
| 4 | Microsoft Windows 7 Ultimate Edition 64bit OS UK |  |
| 5 | Windows 7 64 Bit Factory Image Recovery |  |
| 6 | Intel Xeon E5-1603 2.80Ghz 10MB 1066 4C CPU |  |
| 7 | 6GB DDR3-1600 ECC (3x2GB) RAM |  |
| 9 | NVIDIA NVS 310 512MB Graphics |  |
| 10 | NVIDIA NVS 310 512MB 2nd Graphics |  |
| 11 | 500GB 7200 RPM SATA 1st Hard Drive |  |
| 12 | HP USB Standard Keyboard |  |
| 13 | HP USB Optical Scroll Mouse |  |
| 14 | 16X SuperMulti DVDRW SATA 1st ODD |  |
| 15 | Intel CT x1 PCIe NIC |  |
| 16 | HP 3/3/3 Warranty EURO |  |
| 17 | HP Z420 Country Kit |  |
| 18 | HP Processor Air Cooling Kit |  |
| 19.0 | Software Operating system |  |
| 19.1 | Windows 7 is included in HW above. Office |  |
| 19.2 | Microsoft Office 2010 OEM Basic Anti-virus |  |
| 19.3 | McAfee, 1 year SW updates included |  |
| 20 | Monitors: HP ZR2440w 61 cm (24") LED Backlit IPS Monitor |  |

## POWER CABLES, CONTROL CABLES, CABLE RACKS SCHEDULE

### 132kV XLPE CABLE TECHNICAL SCHEDULES

| Item | Description | Technical Detail | Unit | Data |
| --- | --- | --- | --- | --- |
| 1 | Description | 132kV Single Core XLPE cable |  |  |
| 2 | Type |  |  |  |
| 3 | Quantity | Length | m | specify |
| 4 | Conductor | copper wires, round stranded compacted |  |  |
|  |  | Cross section Area of conductor | mm2 | 1000 |
|  |  | Diameter of conductor | mm | 37.9 |
| 5 | Conductor Screen | Semi- conductive shielding material |  |  |
|  |  | Nominal thickness | mm | 1 |
| 6 | Insulation | XLPE |  |  |
|  |  | Nominal thickness | mm | 18 |
|  |  | minimum thickness | mm | 16 |
| 7 | Insulation Screen | Semi-conductive shielding material |  |  |
|  |  | Nominal thickness | mm | 1 |
| 8 | Wrapper | Semi-conductive water blocking tape |  |  |
|  |  | Nominal thickness | mm | 2.0 |
| 9 | Metallic tape | Copper tape |  |  |
|  |  | Nominal thickness | mm | 0.12 |
| 10 | Wrapper | Semi- conductive water - blocking tape with suitable water swellable absorbant with 50% overlap |  |  |
|  |  | Nominal thickness | mm | 2 |
| 11 | Metallic Sheath | Seamless or Corrugated Aluminium sheath with anti-corrosive material |  |  |
|  |  | Nominal thickness | mm | 0.5 |
| 12 | Outer Sheath | Extruded black HDPE with anti-termite and Anti rodent treatment |  |  |
|  |  | Nominal thickness | mm | 4 |
|  |  | minimum thickness | mm | 3.8 |
|  |  | Approximate diameter | mm | 89 |
| 13 | Cross section of screen |  | mm2 | 95 |
| 14 | Cable weight (Copper-conductor) |  | kg/m | 13.7 |
| 15 | DC resistance at 20˚C IEC 60228 |  | Ω/km | 0.0176 |
| 16 | AC resistance |  |  |  |
| 17 | Capacitance |  | µF/km | 0.25 |
| 18 | Charging current per phase at 50 Hz |  | A/km | 6.1 |
| 19 | Inductance Flat formation |  | mH/km | 0.52 |
| 20 | Surge impedance |  | Ω | 23.7 |
| 21 | Maximum System Voltage Umax |  | kV | 145 |
| 22 | Norminal System Voltage U |  | kV | 132 |
| 23 | Power frequency withstand voltage |  | kV | 275 |
| 24 | Maximum impulse withstand voltage( 1.2/50) |  | kVp | 650 |
| 25 | Continuous current carrying Capacity in ground in Flat formation at 90˚C |  | A | 1165 |
| 26 | Maximum Symetrical Short circuit current |  | kA | 40 |
| 27 | Maximum Symetrical Short circuit current duration |  | s | 1 |
| 28 | AC test voltage for 30 minutes |  | kV | 190 |
| 29 | Partial discharge test |  | kV | 114 |
| 30 |  | Applicable Standards | IEC 60840 |  |
| 31 | CABLE MARKINGS |  |  |  |
|  | Name of manufacturer |  |  |  |
|  | Year of manufacture |  |  |  |
|  | Area of conductor |  |  |  |
|  | Specified voltage of cable in kV |  |  |  |
|  | Type of cable |  |  |  |
| 32 | Previous Type test results/certification for cable provided with bid | Yes/No | Yes |  |
| 33 | Routine tests to be provided on delivery | Yes/No | Yes |  |
| 34 | Quality assurance manuals/certification provided with bid | Yes/No | Yes |  |
| 35 | Cross section drawing of cable clearing showing all details to be provided with bid | Yes/No | Yes |  |
| 36 | Delivery period | 3 months |  |  |

### SCHEDULE B: TO BE COMPLETED BY BIDDER

| Item | Description | Technical Detail | Unit | Data |
| --- | --- | --- | --- | --- |
| 1 | Description | 132kV Single Core XLPE cable |  |  |
| 2 | Type |  |  |  |
| 3 | Quantity |  |  |  |
| 4 | Conductor | copper wires, round stranded compacted |  |  |
|  |  | Cross section Area of conductor | mm2 |  |
|  |  | Diameter of conductor | mm |  |
| 5 | Conductor Screen | Semi- conductive shielding material |  |  |
|  |  | Nominal thickness | mm |  |
| 6 | Insulation | XLPE |  |  |
|  |  | Nominal thickness | mm |  |
|  |  | minimum thickness | mm |  |
| 7 | Insulation Screen | Semi-conductive shielding material |  |  |
|  |  | Nominal thickness | mm |  |
| 8 | Wrapper | Semi-conductive water blocking tape |  |  |
|  |  | Nominal thickness | mm |  |
| 9 | Metallic tape | Copper tape |  |  |
|  |  | Nominal thickness | mm |  |
| 10 | Wrapper | Semi- conductive water - blocking tape with suitable water swellable absorbant with 50% overlap |  |  |
|  |  | Nominal thickness | mm |  |
| 11 | Metallic Sheath | Seamless or Corrugated Aluminium sheath with anti-corrosive material |  |  |
|  |  | Nominal thickness | mm |  |
| 12 | Outer Sheath | Extruded black HDPE with anti-termite and Anti rodent treatment |  |  |
|  |  | Nominal thickness | mm |  |
|  |  | minimum thickness | mm |  |
|  |  | Approximate diameter | mm |  |
| 13 | Cross section of screen |  | mm2 |  |
| 14 | Cable weight (Copper-conductor) |  | kg/m |  |
| 15 | DC resistance at 20˚C IEC 60228 |  | Ω/km |  |
| 16 | AC resistance |  |  |  |
| 17 | Capacitance |  | µF/km |  |
| 18 | Charging current per phase at 50 Hz |  | A/km |  |
| 19 | Inductance Flat formation |  | mH/km |  |
| 20 | Surge impedance |  | Ω |  |
| 21 | Maximum System Voltage Umax |  | kV |  |
| 22 | Norminal System Voltage U |  | kV |  |
| 23 | Power frequency withstand voltage |  | kV |  |
| 24 | Maximum impulse withstand voltage( 1.2/50) |  | kVp |  |
| 25 | Continuous current carrying Capacity in ground in Flat formation at 90˚C |  | A |  |
| 26 | Maximum Symetrical Short circuit current |  | kA |  |
| 27 | Maximum Symetrical Short circuit current duration |  | s |  |
| 28 | AC test voltage for 30 minutes |  | kV |  |
| 29 | Partial discharge test |  | kV |  |
| 30 |  | Applicable Standards |  |  |
| 31 | CABLE MARKINGS |  |  |  |
|  | Name of manufacturer |  |  |  |
|  | Year of manufacture |  |  |  |
|  | Area of conductor |  |  |  |
|  | Specified voltage of cable in kV |  |  |  |
|  | Type of cable |  |  |  |
| 32 | Previous Type test results/certification for cable provided with bid | Yes/No |  |  |
| 33 | Routine tests to be provided on delivery | Yes/No |  |  |
| 34 | Quality assurance manuals/certification provided with bid | Yes/No |  |  |
| 35 | Cross section drawing of cable clearing showing all details to be provided with bid | Yes/No | Yes |  |
| 36 | Delivery period |  |  |  |

### 132kV XLPE CABLE COMPOSITE OUTDOOR TERMINATION

SCHEDULE A: MINIMUM ZESCO REQUIREMENTS

| XLPE Cable Composite Outdoor Termination |  |  |  |
| --- | --- | --- | --- |
| No. | Technical Detail | Unit | Data |
| 1 | Description |  | 132kV Single Core Termination Kit for use on XLPE/PE cable |
| 2 | Type |  | Bidder to specify; Outdoor termination kit |
| 3 | Quantity | Each | 14 |
| 4 | Nominal Voltage (Uo/U) | kV | 76/132 |
| 5 | Highest System voltage | kV | 145 |
| 6 | Frequency | Hz | 50±1% |
| 7 | Basic Impluse level (BIL) | kV | 650 |
| 8 | Maximum Rated temperature of conductor |  |  |
|  | - At the normal run | ˚C | 90 |
|  | - At Transient state (short-circuit current sustaining time is not less than 5s | ˚C | 250 |
| 9 | Cable Size | mm2 | 1000 |
| 10 | Bushing Material |  | Silicone Rubber |
| 11 | Creepage distance | mm | ≥ 4800 |
| 12 | Material of stress cone |  | EPDM |
| 13 | Material of Stress cone |  |  |
|  | Insulating filler in the bushing |  |  |
|  | - material |  | Silicone oil |
|  | - dielectric coefficient |  | 50Hz: 2.76 |
|  | - volume resistivity | Ω.m | 1 x 1013 |
| 14 | Diameter of contact Pin | mm | ɸ50mm (for 1000mm2) |
| 15 | Termination weight | kg | 150 |
| 16 | Height | mm | 2060 |
| 17 | Storage temperature |  |  |
| 18 | Electrical connection between the wiping sleeve and metal sheet |  | weld |
| 19 | Seal method of wiping sleeve |  | “O” ring |
| 20 | Material screen layer of the termination |  |  |
|  | - Material |  | Copper braid tape |
|  | - Max. short circuit currents (1s) |  |  |
| 21 | The main test | kV |  |
|  | - Power frequency voltage test 1 min |  |  |
|  | - Partial discharge at room temperature |  |  |
|  | - Load cycling test at constant- voltage (20periods) |  |  |
|  | - Partial discharge at high temperature |  |  |
|  | - Impulse voltage test |  |  |
|  | - Power frequency voltage test for 30min |  |  |
|  | - Power frequency |  |  |
|  | Previous Type test results/certification for termination joint kit provided with bid | Yes/No | Yes |
| 22 | Quality assurance manuals/certification provided with bid | Yes/No | Yes |
| 23 | Drawings showing dimensions of the termination and mechanical connectos provided with bid | Yes/No | Yes |
| 24 | Assembling instructions with detailed illustrations on installation of connectors to be provided with each termination kit. | Yes/No | Yes |
| 25 | Routine tests to be provided on delivery | Yes/No | Yes |
| 26 | Cable insulation dimension for stress relief | mm | 2 – 7 |
| 27 | Design service life | Year | ≥30 |
| 28 | Environment Temperature |  |  |
| 29 | Altitude |  |  |
| 30 | Applicable Standards |  | IEC 60840 |
|  | Cable Support Structures |  |  |
| 31 | End cable support structures shall accomadate (02) cables and 02 end cable termination kits per phase. | Each | 6 |
| 32 | Drawings showing the dimensions of the end cable support structures complete with two termination kits per phase to be provided with bid | Yes/ No | Yes |
| 33 | Each termination kit shall be supported on pedestal insulators to isolate them from their steel support structures | Yes/No | Yes |
| 34 | Suitable connectors between the two terminals of the end cable termination in each phase to be provided | Each | 6 |
| 35 | Bonding of Sheath/Screen |  |  |
|  | The screens at both ends of the cable shall be brought out and single point bonding shall be used. Surge limiter to be provided at one end of the cable to limit rise of sheath voltage | Yes/No | Yes |
| 36 | Supply and fit | Each | Yes |
| 37 | Delivery period |  | 3months |

Typical Termination Kit

SCHEDULE B: TO BE COMPLETED BY BIDDER

| XLPE Cable Composite Outdoor Termination |  |  |  |
| --- | --- | --- | --- |
| No. | Technical Detail | Unit | Data |
| 1 | Description |  |  |
| 2 | Type |  |  |
| 3 | Quantity | Each |  |
| 4 | Nominal Voltage (Uo/U) | kV |  |
| 5 | Highest System voltage | kV |  |
| 6 | Frequency | Hz |  |
| 7 | Basic Impluse level (BIL) | kV |  |
| 8 | Maximum Rated temperature of conductor |  |  |
|  | - At the normal run | ˚C |  |
|  | - At Transient state (short-circuit current sustaining time is not less than 5s | ˚C |  |
| 9 | Cable Section | mm2 |  |
| 10 | Bushing Material |  |  |
| 11 | Creepage distance | mm |  |
| 12 | Material of stress cone |  |  |
| 13 | Material of Stress cone |  |  |
|  | Insulating filler in the bushing |  |  |
|  | - material |  |  |
|  | - dielectric coefficient |  |  |
|  | - volume resistivity | Ω.m |  |
| 14 | Diameter of contact Pin | mm |  |
| 15 | Termination weight | kg |  |
| 16 | Height | mm |  |
| 17 | Storage temperature |  |  |
| 18 | Electrical connection between the wiping sleeve and metal sheet |  |  |
| 19 | Seal method of wiping sleeve |  |  |
| 20 | Material screen layer of the termination |  |  |
|  | - Material |  |  |
|  | - Max. short circuit currents (1s) |  |  |
| 21 | The main test | kV |  |
|  | - Power frequency voltage test 1 min |  |  |
|  | - Partial discharge at room temperature |  |  |
|  | - Load cycling test at constant- voltage (20periods) |  |  |
|  | - Partial discharge at high temperature |  |  |
|  | - Impulse voltage test |  |  |
|  | - Power frequency voltage test for 30min |  |  |
|  | - Power frequency |  |  |
|  | Previous Type test results/certification for termination joint kit provided with bid | Yes/No |  |
| 22 | Quality assurance manuals/certification provided with bid | Yes/No |  |
| 23 | Drawings showing dimensions of the termination and mechanical connectos provided with bid | Yes/No |  |
| 24 | Assembling instructions with detailed illustrations on installation of connectors to be provided with each termination kit. | Yes/No |  |
| 25 | Routine tests to be provided on delivery | Yes/No |  |
| 26 | Cable insulation dimension for stress relief | mm |  |
| 27 | Design service life | Year |  |
| 28 | Environment Temperature |  |  |
| 29 | Altitude |  |  |
| 30 | Applicable Standards |  |  |
|  | Cable Support Structures |  |  |
| 31 | End cable support structures shall accomadate (02) cables and 02 end cable termination kits per phase. | Each |  |
| 32 | Drawings showing the dimensions of the end cable support structures complete with two termination kits per phase to be provided with bid | Yes/ No |  |
| 33 | Each termination kit shall be supported on pedestal insulators to isolate them from their steel support structures | Yes/No |  |
| 34 | Suitable connectors between the two terminals of the end cable termination in each phase to be provided complete with clamps | Each |  |
| 35 | Bonding of Sheath/Screen |  |  |
|  | The screens at both ends of the cable shall be brought out and single point bonding shall be used. Surge limiter to be provided at one end of the cable to limit rise of sheath voltage | Yes/No |  |
| 32 | Delivery period |  |  |

### TECHNICAL GUARANTEES Sheet 1 of 1

| POWER CABLES, CONTROL CABLES, CABLE RACKS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
| a.1 | 11 kV Cables |  |  |  |
|  | - Continuous current carrying capacity | A |  |  |
|  | - Max. temperature rise of conductor | °C |  |  |
|  | - Short-circuit capacity, 1 second | kA |  |  |
|  | - Test voltage, 50 Hz, 1 minute | kVrms |  |  |
| a.2 | Not applicable |  |  |  |
| a.3 | Low Voltage Power Cables |  |  |  |
|  | - Max. temperature rise of conductor | °C |  |  |
|  | - Short circuit capacity for AC main cables | kA |  |  |
|  | - Test voltage, 50 Hz, 1 minute | kVrms |  |  |
| a.4 | Control and Measuring Cables |  |  |  |
|  | - Test voltage, 50 Hz, 1 minute | kVrms |  |  |
| a.5 | Manufacturer's Name |  |  |  |
|  | - 11 kV cables |  |  |  |
|  | - Low voltage power cables |  |  |  |
|  | - Control and measuring cables |  |  |  |
| a.6 | Country of Manufacture |  |  |  |
|  | - 11 kV cables |  |  |  |
|  | - Low voltage power cables |  |  |  |
|  | - Control and measuring cables |  |  |  |

### 8b INFORMATIVE DATA Sheet 1 of 2

| POWER CABLES, CONTROL CABLES, CABLE RACKS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
| b.1 | 11 kV Cables |  |  |  |
|  | - Conductor material |  |  |  |
|  | - Cross section/equiv. Cu. cross-section | mm² |  |  |
|  | - Insulation material |  |  |  |
|  | - Armouring/screen |  |  |  |
|  | - Material of outer sheath |  |  |  |
|  | - Protective coating |  |  |  |
|  | - Overall diameter of cable | mm |  |  |
|  | - Weight of heaviest reel, including cable | kg |  |  |
|  | - Size of biggest reel, diameter/width | mm/mm |  |  |
| b.2 | Not applicable |  |  |  |
| b.3 | Low Voltage Cables |  |  |  |
|  | - Conductor material |  |  |  |
|  | - Insulation material |  |  |  |
|  | - Armouring/screen |  |  |  |
|  | - Protective coating |  |  |  |
|  | - Overall diameter of cable of biggest cable | mm |  |  |
|  | - Weight of heaviest reel, including cable | kg |  |  |
|  | - Size of biggest reel, diameter/width | mm/mm |  |  |

### 8b INFORMATIVE DATA Sheet 2 of 2

| POWER CABLES, CONTROL CABLES, CABLE RACKS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
| b.4 | Control and Measuring Cables |  |  |  |
|  | - Conductor material - Multistranding of cores |  |  |  |
|  | - Insulation material |  |  |  |
|  | - Armouring/screen |  |  |  |
|  | - Protective coating |  |  |  |
|  | - Overall diameter of cable of biggest cable | mm |  |  |
|  | - Weight of heaviest reel, including cable | kg |  |  |
|  | - Size of biggest reel, diameter/width - Length of drum cable | mm/mm |  |  |
| b.5 | Special Cables |  |  |  |
|  | To be used for: |  |  |  |
|  | - Relevant informative data |  |  |  |

| POWER CABLES, CONTROL CABLES, CABLE RACKS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Particulars | Unit | Guar. Fig | Tolerance |
| a.1 | 33 kV Cables |  |  |  |
|  | - Continuous current carrying capacity | A |  |  |
|  | - Max. temperature rise of conductor | °C |  |  |
|  | - Short-circuit capacity, 1 second | kA |  |  |
|  | - Test voltage, 50 Hz, 1 minute | kVrms |  |  |
| a.2 | Not applicable |  |  |  |
| a.3 | Low Voltage Power Cables |  |  |  |
|  | - Max. temperature rise of conductor | °C |  |  |
|  | - Short circuit capacity for AC main cables | kA |  |  |
|  | - Test voltage, 50 Hz, 1 minute | kVrms |  |  |
| a.4 | Control and Measuring Cables |  |  |  |
|  | - Test voltage, 50 Hz, 1 minute | kVrms |  |  |
| a.5 | Manufacturer's Name |  |  |  |
|  | - 33 kV cables |  |  |  |
|  | - Low voltage power cables |  |  |  |
|  | - Control and measuring cables |  |  |  |
| a.6 | Country of Manufacture |  |  |  |
|  | - 33 kV cables |  |  |  |
|  | - Low voltage power cables |  |  |  |
|  | - Control and measuring cables |  |  |  |

## EARTHING SYSTEM

### SCHEDULE 9a TECHNICAL GUARANTEES Sheet 1 of 1

| EARTHING SYSTEM |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Activity | Unit | Rate | Total price |
| 1. 2. 3. | Soil Resistance measurements initial values Substation earthing system design as per IEEE 80:2013 Resistance to Earth of Earthing Electrode System (for each substation) |  |  |  |
|  | - Under the control building max. |  |  |  |
|  | - Under the switchyard max. |  |  |  |
|  | - Complete earthing system |  |  |  |

### SCHEDULE VI-V-9 b INFORMATIVE DATA Sheet 1 of 1

| Item | Particulars | Unit | Guar. Fig | Tolerance |
| --- | --- | --- | --- | --- |
|  | - Reference standard |  |  |  |
|  | - Material of earth conductor |  |  |  |
|  | - Max. temp of any earth conductor during 1 sec. rated phase - ground fault |  |  |  |
|  | - Method of interconnecting earth grid conductors |  |  |  |

## HV POWER TRANSFORMERS SCHEDULES TECHNICAL GUARANTEES

### 125/160MVA 330/132/11kV TRANSFORMERS TECHNICAL GUARANTEES

| 125/160MVA 330/132/11kV TRANSFORMERS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Technical Details | Units | Schedule A: Minimum Requirements | Schedule B: Bidder Guarantee |
| 1. | General Information |  |  |  |
| 1.1 | Manufacturer |  | Specify |  |
| 1.2 | Model Number |  | Specify |  |
| 1.3 | Country of origin |  | Specify |  |
| 1.4 | Type |  | Three Phase with three (03) windings, Power transformer with On -Load Tap changer |  |
| 1.5 | Class |  | Oil immersed/cooled |  |
| 1.6 | Winding Insulation |  | HV: Graded MV: Graded Tertiary: Fully Insulated |  |
| 2. | Operating Conditions |  |  |  |
| 2.1 | Installation |  | Outdoor in substation |  |
| 2.2 | Altitude (above sea level) |  | 1500 |  |
| 2.3 | Ambient temperature (min, max) | ℃ | -1 to 48 |  |
| 2.4 | Humidity | % | 90 |  |
|  | Creepage distance | mm/kV | 31[very heavy] |  |
| 2. | Rated Data and Characteristics |  |  |  |
|  | Rated frequency | Hz | 50 |  |
| 2.1 | Rated Power | MVA |  |  |
| 2.2 | HV winding LV winding Tertiary |  | 160 160 5 – Tertiary shall be loaded. Terminals to be brought of Transformer and dimensioned for laoding |  |
|  | Rated Voltage |  |  |  |
| 2.3 | HV winding | kV | 330 |  |
| 2.4 | LV winding | kV | 132 |  |
| 2.5 | Tertiary winding | kV | 11 |  |
| 2.6 | Highest System Voltage |  |  |  |
| 2.7 | HV winding | kV | 362 |  |
| 2.8 | LV winding | kV | 145 |  |
| 2.9 | Tertiary winding | kV | 12 (to be loaded) |  |
| 2.10 | Rated current In, at ONAF rated power and rated voltage |  |  |  |
| 2.11 | HV winding LV winding Tertiary winding | A | 280 700 262 |  |
| 2.12 | Cooling |  | 160MVA ONAF and 125MVA ONAN |  |
| 2.13 | Type of cooling equipment |  | Detachable radiator coolers integral with main tank provided with fans and oil pumps. Hot dip galvanised fins required |  |
|  | Tap Changer |  |  |  |
| 2.11 | Manufacturer |  | MR Germany |  |
| 2.15 | Model |  | Vacutap – MR |  |
| 2.16 | Type |  | CFVV (Bi-directional, High-speed resistor, Vacuum type on-load tap changer on HV winding, with motor drive unit supplied on 380V AC for motor and controls at 220V AC, 50Hz with local/remote control/indication and RTCC panel) |  |
| 2.17 | Rated current | A | 300 |  |
| 2.18 | Tap transition device |  | Resistor |  |
| 2.19 | Contact life at rated through current | No of operations | >300,000 |  |
| 2.20 | on-load tap changer location |  | Neutral end of HV winding to regulate LV voltage |  |
| 2.21 | regulating range | % | +10 x 1.25% -10 x 1.25% |  |
| 2.22 | parallel automatic control |  | Yes, Master follower |  |
| 2.23 | Connection of the three phase windings (vector group IEC 60076) |  | YNyn0d1 |  |
|  | Type of earth connection for neutral |  |  |  |
| 2.24 | HV neutral |  | Solid |  |
| 2.25 | LV neutral |  | Solid |  |
| 2.26 | No-load Current through: |  |  |  |
| 2.27 | HV winding | A |  |  |
| 2.26 | LV winding | A | 0.4% In, (of rated current) |  |
| 2.27 | Tertiary winding | A | - |  |
| 2.29 | Short Circuit Impedance |  | Base: rated voltage and 160MVA |  |
|  | Impedance voltage at nominal tap: |  |  |  |
| 2.30 | HV/LV | % | specify |  |
| 2.31 | HV/Ter. |  | specify |  |
| 2.32 | LV/Ter |  | specify |  |
| 2.33 | Tolerance to be applied to the short circuit impedance, in terms of % of the guaranteed value on: |  |  |  |
| 2.34 | Nominal voltage tap | % | Specify |  |
| 2.35 | Other taps | % | Specify |  |
| 2.36 | Transformer capacity to withstand external short circuits: |  | Specify |  |
| 2.37 | Short circuit duration | s | 3 |  |
| 2.38 | Symmetrical short circuit current withstand during the indicated period and asymmetrical short circuit withstand: |  |  |  |
|  | HV winding | kA RMS kA (Peak) | As per IEC 60076 |  |
| 2.39 | LV winding | kA RMS kA (Peak) | As per IEC 60076 |  |
| 2.40 | Tertiary winding | kA RMS kA (Peak) | As per IEC 60076 |  |
| 2.41 | Pre-fault voltage | p.u. | 1.10 |  |
| 2.42 | Guaranteed losses |  |  |  |
| 2.43 | No-load loss at rated frequency and on the principal tapping (no plus tolerance allowed) - at 100% of the rated voltage - at 110% of the rated voltage (design calculation sheet shall be submitted with the bid) | kW | 58 65 |  |
| 2.44 | Tolerance to be applied to no-load losses (in % of guaranteed value) | % | ±10 |  |
| 2.45 | Load loss (I2R +stray) at 75°C and the maximum HV rating and rated frequency (total on HV & LV windings) - on principal tapping (design calculation sheet shall be submitted with the bid) | kW | 285 |  |
| 2.46 | Auxiliaries consumption at second stage of cooling (ONAF) | kW |  |  |
| 2.47 | Tolerance to be applied to total losses (in % of guaranteed value) for all the windings | % | ±10 |  |
| 2.48 | Rated Insulation level: |  |  |  |
| 2.49 | Short time power frequency withstand: |  |  |  |
| 2.50 | HV winding – Line terminal HV neutral | kV RMS | 520 125 |  |
| 2.51 | LV winding - Line terminal LV neutral | kV RMS | 132kV 275; 95 |  |
| 2.52 | Tertiary winding | kV RMS | 28 |  |
| 2.53 | Control wiring | kV RMS | 2.0 |  |
|  | Basic impulse level |  |  |  |
| 2.54 | HV winding – Line terminal HV neutral | kV (peak) | 1175 185 |  |
| 2.55 | LV winding – Line terminal LV neutral | kV (peak) | 132kV 650: 185 |  |
| 2.56 | Tertiary winding | kV (peak) | 95 |  |
| 2.57 | Temperature rise limits at maximum power output at ONAN and ONAF ratings and at lowest tap and corresponding voltage: |  |  |  |
| 2.58 | Top oil at ambient temperature | ℃ | 55 |  |
| 2.59 | Average winding at ambient temperature | ℃ | 60 |  |
| 2.60 | Maximum hot spot temperature of winding | ℃ | As per IEC 60076 |  |
|  | Permissible overload in emergency cases: |  |  |  |
| 2.61 | Long time emergency overload based on highest winding temperature which exceeds by 5°C the guaranteed limit at rated power (in % of the rated voltage) | % | As per overloading guide specified in IEC 60354 |  |
|  | Oil: |  |  |  |
| 2.62 | Manufacturer Type Standard Data sheet attached |  | Indicate Indicate IEC 60296; 2003 Ed. Must be attached |  |
| 2.63 | Bushings |  |  |  |
| 2.63.1 | HV bushings |  |  |  |
|  | - class - quantity - type designation - rated current - short circuit withstand - basic insulation level - power frequency withstand (1 min) - terminal/housing material - creepage distance | kV A kA rms kV pk kV rms mm/kV | 362 3 OIP condenser type 800 20 1175 510 Porcelain or composite polymer 31 |  |
| 2.63.2 | LV Bushings |  |  |  |
|  | - class - quantity - type designation - rated current - short circuit withstand - basic insulation level - power frequency withstand (1 min) - terminal/housing material - creepage distance | kV A kA rms kA pk kA rms mm/kV | 145 3 Oil condenser type 1250 20 170 70 Porcelain or composite polymer 31 |  |
| 2.63.3 | Tertiary bushings: - class - quantity - type designation - rated current - short circuit withstand - basic insulation level - power frequency withstand (1 min) - terminal/housing material - creepage distance | kV kA kA rms kA pk kA rms mm/kV | 12 3 (to be brought out) 800 10 95 38 Solid Porcelain 31 |  |
|  | Neutral Bushings |  |  |  |
| 2.63.4 | HV neutral - class - quantity - type designation - rated current - short circuit withstand - basic insulation level - power frequency withstand (1 min) - terminal/housing material - creepage distance | kV A kA rms kV pk kV rms mm/kV | 72,5 1 Oil impregnated cond, 1250 10 325 140 Porcelain or composite silicone 31 |  |
| 2.63.5 | LV neutral - class - quantity - type designation - rated current - short circuit withstand - basic insulation level - power frequency withstand (1 min) - terminal/housing material - creepage distance | kV A kA rms kV pk kV rms mm/kV | 72.5 1 Oil impregnated cond. 1500 10 325 140 Porcelain or composite silicone 31 |  |
| 3. | Design Data: |  |  |  |
| 3.1 | Core type (core or Shell) |  | Core |  |
| 3.2 | Maximum flux density in the columns at: |  |  |  |
|  | Rated voltage | Tesla | 1.7 |  |
|  | 110% of rated voltage | Tesla | 1.85 |  |
| 3.3 | Maximum flux density in the yokes at: |  |  |  |
|  | Rated voltage | Tesla | 1.7 |  |
|  | 110% of rated voltage | Tesla | 1.85 |  |
| 3.4 | Magnetizing current, at rated frequency, on principal tapping, in percent of rated current at maximum HV rating - at 90% of the rated voltage - at 100% of the rated voltage - at 110% of the rated voltage | % % % | 0.12In 0.15In 0.2In |  |
| 3.5 | Maximum current density at ONAN rated power and rated voltage tap: |  |  |  |
|  | HV winding | A/mm2 | 2.4 Max |  |
|  | LV winding | A/mm2 | 2.4 Max |  |
|  | Tertiary winding | A/mm2 | 2.4 Max |  |
| 3.6 | Winding resistance: |  |  |  |
|  | HV winding | Ohms/phase | Bidder to indicate |  |
|  | LV windings | Ohms/phase | Bidder to indicate |  |
|  | Tertiary winding | Ohms/phase | Bidder to indicate |  |
| 3.7 | Voltage Regulation at ONAN rating and rated voltage tap (in % of the rated voltage): - with unity power factor: - with 0.9 power factor (lagging): - with 0.8 power factor (lagging): | % % % | 1.45 3.04 4.2 |  |
| 3.8 | Winding conductor material |  | Copper |  |
| 3.9 | Type of winding HV LV Ter. |  | Disc Helical Helical |  |
| 3.10 | Type of insulation |  |  |  |
|  | HV, LV & Ter., |  | Thermally upgraded kraft paper + Pressboard |  |
|  | Tapping’s & Connections |  | Kraft/Crepe paper |  |
|  | Core bolts & washers if any |  | Boltless |  |
|  | Core lamination design |  | Step-lap |  |
| 3.11 | Audible Noise level |  |  |  |
|  | Voltage in % of rated value | % | 105 |  |
|  | ONAN rating | dB(A) | 76 |  |
|  | ONAF maximum rating | dB(A) | 78 |  |
| 3.12 | Weights and Dimensions |  |  |  |
|  | Total weight of transformer, equipped for service | Kg | Specify |  |
| 3.13 | Weight: |  |  |  |
|  | Oil | Kg | Specify |  |
|  | Core and coil assembling | kg | Specify |  |
|  | Tank and accessories | kg | Specify |  |
|  | Net copper | kg | Specify |  |
|  | Net core steel | Kg | Specify |  |
|  | Maximum shipping weight | kg | Specify |  |
| 3.14 | Height from foundation to: |  |  |  |
|  | Highest point of HV bushing | mm | Specify |  |
|  | Highest point of tank | mm | Specify |  |
|  | Highest point of conservator tank | mm | Specify |  |
|  | Highest point of lifting hook to remove core and coil assembly | mm | Specify |  |
| 3.15 | Outline Dimensions |  |  |  |
|  | Length | mm |  |  |
|  | Width | mm |  |  |
| 3.16 | Dimensioned layout drawing |  | Yes, to be attached |  |
| 4. | Current transformer incorporated into the Power transformer |  |  |  |
| 4.1 | CT in HV phase bushings: |  |  |  |
| 4.1.1 | Number of cores per bushing | - | 3 |  |
| 4.1.2 | Primary rated current | A | 400 |  |
| 4.1.3 | Secondary rated current | A | 1 |  |
| 4.1.4 | Accuracy class |  |  |  |
|  | Protection | - | (3)5P20, 15VA |  |
|  | Metering | - | (1)CL0.2,15VA |  |
| 4.1.5 | Ratio | - | 400:1 |  |
| 4.1.7 | Continuous secondary current (thermal limit) | A | 1.2 |  |
| 4.2 | CT in LV phase bushings: |  |  |  |
| 4.2.1 | Number of cores per bushing | - | 3 |  |
| 4.2.2 | Primary rated current | A | 700 |  |
| 4.2.3 | Secondary rated current | A | 1 |  |
| 4.2.4 | Accuracy class |  |  |  |
|  | Protection | - | (3)5P20, 15VA |  |
|  | Metering | - | (1) CL0.2,15VA |  |
| 4.2.5 | Ratio | - | 800:1 |  |
| 4.2.7 | Continuous secondary current (thermal limit) | A | 1.2 |  |
| 4.3 | CT in HV neutral bushings: |  |  |  |
| 4.3.1 | Number of cores per bushing | - | 2 |  |
| 4.3.2 | Primary rated current | A | 280 |  |
| 4.3.3 | Secondary rated current | A | 1 |  |
| 4.3.4 | Accuracy class |  |  |  |
|  | Protection | - | 5P20,15 VA |  |
| 4.3.5 | Ratio | - | 300:1 |  |
| 4.3.7 | Continuous secondary current (thermal limit) | A | 1.2 |  |
| 4.4 | CT in LV neutral bushings: |  |  |  |
| 4.4.1 | Number of cores per bushing | - | 2 |  |
| 4.4.2 | Primary rated current | A | 700 |  |
| 4.4.3 | Secondary rated current | A | 1 |  |
| 4.4.4 | Accuracy class |  |  |  |
|  | Protection | - | 5P20,15 VA |  |
| 4.4.5 | Ratio | - | 800:1 |  |
| 4.4.6 | Continuous secondary current (thermal limit) | A | 1.2 |  |
| 5.0 | Accessories, Indication and Protection devices |  |  |  |
| 5.1 | Oil preservation |  | Diaphragm |  |
| 5.2 | Dehydrating breather |  | Yes |  |
| 5.3 | Buchholz relay main tank |  | Yes |  |
| 5.4 | OLTC surge relay |  | Yes |  |
| 5.5 | Dial type winding temperature gauge with alarm & trip contacts |  | Yes |  |
| 5.6 | Dial type oil temperature gauge with alarm & trip contacts |  | Yes |  |
| 5.7 | Provision for remote indication of winding & oil temp.; via transducers |  | Yes |  |
| 5.8 | Cubicles & Cabinets |  | RTCC panel; Cooler control cubicles with remote temperature indication |  |
| 5.9 | Pressure relief device (main tank) |  | Yes |  |
| 5.10 | Pressure relief device (OLTC) |  | Yes |  |
| 5.11 | Buchholz gas/oil sampling collection pipe from ground level |  | Yes |  |
| 5.12 | Transformer base |  | Skid base (no wheel) |  |
| 5.13 | Lifting lugs and jacking pads |  | Yes |  |
| 5.14 | Rating and diagram plate |  | Yes |  |
| 5.15 | Main tank vacuum proof |  | Yes |  |
| 5.16 | Shock/impact recorders during transportation |  | Yes |  |
| 5.17 | Filling medium during transport |  | Dry nitrogen gas |  |
| 6.0 | Standards |  |  |  |
| 6.1 | Manufacturing | - | IEC 60044 IEC 60076 [1-10] IEC 60137 IEC 60214 IEC 60529 IEC 60815 IEC 60947 NEMA TR-1 ASTM D877 |  |
| 6.2 | Quality assurance | - | ISO 9001 |  |
|  | Type test certification (to be submitted with the bid for approval otherwise it will be assumed that no type tests for identical units are available) |  | Yes |  |
| 6.3 | Design Life Expectation at average 70% load factor (design calculation shall be submitted with the bid) | years | 35 |  |
| 7.0 | State identity of transformer manufacturer and all sub-manufacturers including the parts manufactured below: Transformer Core steel OLTC Cooling equipment Current transformers Bushings Dehydrating breather Mineral oil Temperature indicators |  | Bidder to list: |  |
| 10 | Accessories |  |  |  |
| 10.1 | Fire and Explosion protection system/Transformer Protector |  | Yes, Nitrogen Injection system |  |
| 10.2 | Manufacturer |  | Sergi Transformer Protector, France |  |
| 10.3 | Oil Preservation |  | Diaphragm/Air cell |  |
| 10.4 | Oil Conservator type |  | Air cell |  |
| 10.5 | Dehydrating Breather |  | Yes, sealed type silica gel |  |
| 10.6 | Buchholz relay main tank |  | Yes |  |
| 10.7 | OLTC surge relay |  | Yes |  |
| 10.8 | Dial type winding temperature gauge with alarm and trip contacts |  | Yes |  |
| 10.9 | Dial type oil temperature gauge with alarm and trip contacts |  | yes |  |
| 10.10 | Provision for remote indication of oil and winding temperature via transducers |  | yes |  |
| 10.11 | Cubicles and cabinets |  | Tap changer drive mechanism, marshalling kiosk, incorporating cooler control, temperature indications and secondary cabling marshalling with provision for remote temperature indication |  |
| 10.12 | Pressure relief device (Main Tank) |  | yes |  |
| 10.13 | Pressure relief device (OLTC) |  | yes |  |
| 10.14 | Buchholz gas /oil sampling collection pipe and valve accessible from ground level |  | yes |  |
| 10.15 | Transformer base |  | yes |  |
| 10.16 | Lifting lugs and jacking pads |  | yes |  |
| 10.17 | Rating and Diagram plate |  | yes |  |
| 10.18 | Main Tank Vacuum proof |  | Yes |  |
| 10.19 | Shock/Impact recorders fitted during transportation/accelerometer |  | yes |  |
| 10.20 | Oil filtration connections/inlet and drain valves |  | yes |  |
| 10.20 | Online Dissolved Gas Analysis (DGA) connection facilities |  | yes |  |
| 10.21 | Earthing terminals at two opposite locations (to be suitable for 50mm x 3mm flat copper) |  | Yes |  |
| 10.22 | Manholes |  | yes |  |
| 10.23 | Antivibration pads |  | yes |  |
| 10.24 | Oil Sampling device |  | yes |  |
| 11. | Colours |  |  |  |
| 11.1 | Transformer colour |  | Cloud grey (NCS -2305-R99B) |  |
| 11.2 | Conservator colour |  | Cloud white (NCS-0704-G38Y) |  |

### 31.5/40MVA 132/33KV TRANSFORMERS

| 31.5/40MVA 132/33kV TRANSFORMERS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Technical Details |  | Unit | ZESCO Requirement | Bidder’s Guarantee |
|  | General/Accessories |  |  |  |  |
| 1. | Fire and explosion protection/ Transformer protector |  |  | Yes, Nitrogen injection system |  |
| 2. | Manufacturer |  |  | Sergi Transformer Protector, France |  |
|  | Technical Specification |  |  |  |  |
| 1 | Type |  |  | Outdoor, 3 phase, 2 winding oil filled |  |
| 2 | Rated power |  | MVA | 40 |  |
| 3 | Rated voltage – HV/LV (No load voltage ratio) |  | kV | 132/33 |  |
| 4 | Rated frequency |  | Hz | 50 |  |
| 5 | Vector Group |  |  | Dyn11 |  |
| 6 | Phases |  |  | 3 |  |
| 7 | Type of cooling |  |  | 31.5MVA ONAN/ 40MVA ONAF |  |
| 8 | Type of cooling equipment |  |  | Detachable radiator coolers integral with main tank |  |
| 9 | Type of insulating oil |  |  | Mineral oil as per IEC 60296 [No PCB] |  |
| 10 | Mineral oil data sheet required |  |  | Yes, bidder to submit. |  |
| 11 | Winding Material |  |  | Copper |  |
| 12 | Impedance |  | % | As per Relevant IEC standard |  |
| 13 | Maximum flux density in the columns |  | T | 1.6 |  |
| 14 | Maximum flux density in the yoke |  | T | 1.65 |  |
| 15 | No load Current at rated voltage and frequency |  | % | 1.5% of Full Load Current |  |
| 16 | Magnetizing current, at rated frequency, on principal tapping, At 100% of rated voltage |  | % | 0.16% of In (Percent of Rated current) |  |
| 17 | Magnetizing current, at rated frequency, on principal tapping, At 110% of rated voltage |  | % | 0.3% of In (Percent of Rated current) |  |
| 18 | Temperature rise limits at rated voltage and power | Winding | ℃ | 60 |  |
|  |  | Top oil | ℃ | 55 |  |
| 19 | 1.2/50 micro-sec Lightning impulse withstand HV LV |  | kV | 132 650 170 |  |
| 20 | 1-minute Power Frequency withstand HV LV |  | kV | 132 275 70 |  |
| 21 | Bushing Type |  |  | Porcelain - Condenser |  |
| 22 | Bushing creepage distance |  | mm/kV | 31 |  |
| 23 | Equipped with Jacking pads |  |  | Yes |  |
| 24 | Tapping range, steps & location |  |  | +10% to -10% @1.25% |  |
| 25 | Tap changer type |  |  | OLTC (MR Germany) – Vacuum type |  |
| 26 | Tap changer accessories |  |  | Motor drive unit supplied on 380V AC for motor and controls at 220V AC, 50Hz; with local/remote control/indication and RTCC panel with AVR |  |
| 27 | Tap transition device |  |  | Resistor |  |
| 28 | Tap Changer Contact Rated Current |  | A | As per relevant IEC standard |  |
| 29 | Contact life at rated through current |  | No. of operations | ≥ 300,000 |  |
| 30 | Supply to Tap changer motor |  | V ac | 400 |  |
| 31 | Mechanical tap position indicator |  |  | Yes |  |
| 32 | Rated No load Losses |  | kW | ≤ 12 |  |
| 33 | Rated Load Losses |  | kW | ≤ 70 |  |
| 34 | Bushing CT’s to be provided |  |  | Yes |  |
| 35 | Altitude above sea level |  | m | 1500 |  |
| 36 | Ambient temperature |  | 0C | -1 to 48 |  |
| 37 | Relative Humidity (max) |  | % | 85 |  |
| 38 | Buchholz relay for main tank |  |  | Yes |  |
| 39 | Buchholz relay for tap changer |  |  | Yes |  |
| 40 | Buchholz gas/oil collection/sampling pipe from ground level |  |  | Yes |  |
| 41 | Temperature gauges; (oil & winding) |  |  | Yes |  |
| 42 | Provision for remote indication of winding and oil temp. via transducers |  |  | Yes |  |
| 43 | Brackets for mounting surge arrestors |  |  | Yes |  |
| 44 | Pressure relief device (valve) |  |  | Yes |  |
| 45 | Skid under base |  |  | Yes |  |
| 46 | Main tank vacuum proof |  |  | Yes |  |
| 47 | Shock/Impact recorders during transportation |  |  | Yes |  |
| 48 | Bushing CTs included |  |  | Yes |  |
| 49 | Previous type test |  |  | To be provided with bid |  |
| 50 | Drawings |  |  | To be provided with bid |  |
| 51 | QA/QC documentation |  |  | To be provided with bid |  |
| 52 | Design Life Expectation at average 80% load factor (design calculation shall be submitted with the bid) |  | Years | 30 Years minimum |  |

### 31.5/40MVA 132/11KV TRANSFORMERS

| 31.5/40MVA 132/11kV TRANSFORMERS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Technical Details |  | Unit | ZESCO Requirement | Bidder’s Guarantee |
|  | General/Accessories |  |  |  |  |
| 1. | Fire and explosion protection/ Transformer protector |  |  | Yes, Nitrogen injection system |  |
| 2. | Manufacturer |  |  | Sergi Transformer Protector, France |  |
|  | Technical Specification |  |  |  |  |
| 1 | Type |  |  | Outdoor, 3 phase, 2 winding oil filled |  |
| 2 | Rated power |  | MVA | 40 |  |
| 3 | Rated voltage – HV/LV (No load voltage ratio) |  | kV | 132/11 |  |
| 4 | Rated frequency |  | Hz | 50 |  |
| 5 | Vector Group |  |  | Dyn11 |  |
| 6 | Phases |  |  | 3 |  |
| 7 | Type of cooling |  |  | 40MVA ONAF/ONAN 31.5MVA |  |
| 8 | Type of cooling equipment |  |  | Detachable radiator coolers integral with main tank |  |
| 9 | Type of insulating oil |  |  | Mineral oil as per IEC 60296 [No PCB] |  |
| 10 | Mineral oil data sheet required |  |  | Yes, bidder to submit. |  |
| 11 | Winding Material |  |  | Copper |  |
| 12 | Impedance |  | % | As per Relevant IEC standard |  |
| 13 | Maximum flux density in the columns |  | T | 1.6 |  |
| 14 | Maximum flux density in the yoke |  | T | 1.65 |  |
| 15 | No load Current at rated voltage and frequency |  | % | 1.5% of Full Load Current |  |
| 16 | Magnetizing current, at rated frequency, on principal tapping, At 100% of rated voltage |  | % | 0.16% of In (Percent of Rated current) |  |
| 17 | Magnetizing current, at rated frequency, on principal tapping, At 110% of rated voltage |  | % | 0.3% of In (Percent of Rated current) |  |
| 18 | Temperature rise limits at rated voltage and power | Winding | ℃ | 60 |  |
|  |  | Top oil | ℃ | 55 |  |
| 19 | 1.2/50 micro-sec Lightning impulse withstand HV LV |  | kV | 132 650 95 |  |
| 20 | 1-minute Power Frequency withstand HV LV |  | kV | 132 275 28 |  |
| 21 | Bushing Type |  |  | Porcelain - Condenser |  |
| 22 | Bushing creepage distance |  | mm/kV | 31 |  |
| 23 | Equipped with Jacking pads |  |  | Yes |  |
| 24 | Tapping range, steps & location |  |  | +10% to -10% @1.25% |  |
| 25 | Tap changer type |  |  | OLTC (MR Germany) – Vacuum type |  |
| 26 | Tap changer accessories |  |  | Motor drive unit supplied on 380V AC for motor and controls at 220V AC, 50Hz; with local/remote control/indication and RTCC panel with AVR |  |
| 27 | Tap transition device |  |  | Resistor |  |
| 28 | Tap Changer Contact Rated Current |  | A | As per relevant IEC standard |  |
| 29 | Contact life at rated through current |  | No. of operations | ≥ 300,000 |  |
| 30 | Supply to Tap changer motor |  | V ac | 400 |  |
| 31 | Mechanical tap position indicator |  |  | Yes |  |
| 32 | Rated No load Losses |  | kW | ≤ 12 |  |
| 33 | Rated Load Losses |  | kW | ≤ 70 |  |
| 34 | Bushing CT’s to be provided |  |  | Yes |  |
| 35 | Altitude above sea level |  | m | 1500 |  |
| 36 | Ambient temperature |  | 0C | -1 to 48 |  |
| 37 | Relative Humidity (max) |  | % | 85 |  |
| 38 | Bulcholz relay for main tank |  |  | Yes |  |
| 39 | Bulcholz relay for tap changer |  |  | Yes |  |
| 40 | Bulcholz gas/oil collection/sampling pipe from ground level |  |  | Yes |  |
| 41 | Temperature gauges; (oil & winding) |  |  | Yes |  |
| 42 | Provision for remote indication of winding and oil temp. via transducers |  |  | Yes |  |
| 43 | Brackets for mounting surge arrestors |  |  | Yes |  |
| 44 | Pressure relief device (valve) |  |  | Yes |  |
| 45 | Skid under base |  |  | Yes |  |
| 46 | Main tank vacuum proof |  |  | Yes |  |
| 47 | Shock/Impact recorders during transportation |  |  | Yes |  |
| 48 | Bushing CT’s included |  |  | Yes |  |
| 49 | Previous type test |  |  | To be provided with bid |  |
| 50 | Drawings |  |  | To be provided with bid |  |
| 51 | QA/QC documentation |  |  | To be provided with bid |  |
| 52 | Design Life Expectation at average 80% load factor (design calculation shall be submitted with the bid) |  | Years | 30 Years minimum |  |

### 25/31.5MVA 33/11KV TRANSFORMERS

| 25/31.5MVA 33/11kV TRANSFORMERS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Technical Details |  | Unit | ZESCO Requirement | Bidder’s Guarantee |
|  | General/Accessories |  |  |  |  |
| 1. | Fire and explosion protection/ Transformer protector |  |  | Yes, Nitrogen injection system |  |
| 2. | Manufacturer |  |  | Sergi Transformer Protector, France |  |
|  | Technical Specification |  |  |  |  |
| 1 | Type |  |  | Outdoor, 3 phase, 2 winding oil filled |  |
| 2 | Rated power |  | MVA | 31.5 |  |
| 3 | Rated voltage – HV/LV (No load voltage ratio) |  | kV | 33/11 |  |
| 4 | Rated frequency |  | Hz | 50 |  |
| 5 | Vector Group |  |  | Dyn11 |  |
| 6 | Phases |  |  | 3 |  |
| 7 | Type of cooling |  |  | 31.5MVA ONAF/ONAN 25MVA |  |
| 8 | Type of cooling equipment |  |  | Detachable radiator coolers integral with main tank |  |
| 9 | Type of insulating oil |  |  | Mineral oil as per IEC 60296 [No PCB] |  |
| 10 | Mineral oil data sheet required |  |  | Yes, bidder to submit. |  |
| 11 | Winding Material |  |  | Copper |  |
| 12 | Impedance |  | % | As per Relevant IEC standard |  |
| 13 | Maximum flux density in the columns |  | T | 1.6 |  |
| 14 | Maximum flux density in the yoke |  | T | 1.65 |  |
| 15 | No load Current at rated voltage and frequency |  | % | 1.5% of Full Load Current |  |
| 16 | Magnetizing current, at rated frequency, on principal tapping, At 100% of rated voltage |  | % | 0.16% of In (Percent of Rated current) |  |
| 17 | Magnetizing current, at rated frequency, on principal tapping, At 110% of rated voltage |  | % | 0.3% of In (Percent of Rated current) |  |
| 18 | Temperature rise limits at rated voltage and power | Winding | ℃ | 60 |  |
|  |  | Top oil | ℃ | 55 |  |
| 19 | 1.2/50 micro-sec Lightning impulse withstand HV LV |  | kV | 33 170 95 |  |
| 20 | 1 minute Power Frequency withstand HV LV |  | kV | 33 70 28 |  |
| 21 | Bushing Type |  |  | Porcelain - Condenser |  |
| 22 | Bushing creepage distance |  | mm/kV | 31 |  |
| 23 | Equipped with Jacking pads |  |  | Yes |  |
| 24 | Tapping range, steps & location |  |  | +10% to -10% @1.25% |  |
| 25 | Tap changer type |  |  | OLTC (MR Germany) – Vacuum type |  |
| 26 | Tap changer accessories |  |  | Motor drive unit supplied on 380V AC for motor and controls at 220V AC, 50Hz; with local/remote control/indication and RTCC panel with AVR |  |
| 27 | Tap transition device |  |  | Resistor |  |
| 28 | Tap Changer Contact Rated Current |  | A | As per relevant IEC standard |  |
| 29 | Contact life at rated through current |  | No. of operations | ≥ 300,000 |  |
| 30 | Supply to Tap changer motor |  | V ac | 400 |  |
| 31 | Mechanical tap position indicator |  |  | Yes |  |
| 32 | Rated No load Losses |  | kW | ≤ 12 |  |
| 33 | Rated Load Losses |  | kW | ≤ 70 |  |
| 34 | Bushing CT’s to be provided |  |  | Yes |  |
| 35 | Altitude above sea level |  | m | 1300 |  |
| 36 | Ambient temperature |  | 0C | -1 to 48 |  |
| 37 | Relative Humidity (max) |  | % | 85 |  |
| 38 | Bulcholz relay for main tank |  |  | Yes |  |
| 39 | Bulcholz relay for tap changer |  |  | Yes |  |
| 40 | Bulcholz gas/oil collection/sampling pipe from ground level |  |  | Yes |  |
| 41 | Temperature gauges; (oil & winding) |  |  | Yes |  |
| 42 | Provision for remote indication of winding and oil temp. via transducers |  |  | Yes |  |
| 43 | Brackets for mounting surge arrestors |  |  | Yes |  |
| 44 | Pressure relief device (valve) |  |  | Yes |  |
| 45 | Skid under base |  |  | Yes |  |
| 46 | Main tank vacuum proof |  |  | Yes |  |
| 47 | Shock/Impact recorders during transportation |  |  | Yes |  |
| 48 | Bushing CT’s included |  |  | Yes |  |
| 49 | Previous type test |  |  | To be provided with bid |  |
| 50 | Drawings |  |  | To be provided with bid |  |
| 51 | QA/QC documentation |  |  | To be provided with bid |  |
| 52 | Design Life Expectation at average 70% load factor (design calculation shall be submitted with the bid) |  | Years | 30 Years minimum |  |

### 10/12.5MVA 33/11KV TRANSFORMERS

| 10/12.5MVA 33/11kV TRANSFORMERS |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Technical Details |  | Unit | ZESCO Requirement | Bidder’s Guarantee |
|  | General/Accessories |  |  |  |  |
| 1. | Fire and explosion protection/ Transformer protector |  |  | Yes, Nitrogen injection system |  |
| 2. | Manufacturer |  |  | Sergi Transformer Protector, France |  |
|  | Technical Specification |  |  |  |  |
| 1 | Type |  |  | Outdoor, 3 phase, 2 winding oil filled |  |
| 2 | Rated power |  | MVA | 12.5 |  |
| 3 | Rated voltage – HV/LV (No load voltage ratio) |  | kV | 33/11 |  |
| 4 | Rated frequency |  | Hz | 50 |  |
| 5 | Vector Group |  |  | Dyn11 |  |
| 6 | Phases |  |  | 3 |  |
| 7 | Type of cooling |  |  | 12.5MVA ONAF/ONAN 10MVA |  |
| 8 | Type of cooling equipment |  |  | Detachable radiator coolers integral with main tank |  |
| 9 | Type of insulating oil |  |  | Mineral oil as per IEC 60296 [No PCB] |  |
| 10 | Mineral oil data sheet required |  |  | Yes, bidder to submit. |  |
| 11 | Winding Material |  |  | Copper |  |
| 12 | Impedance |  | % | As per Relevant IEC standard |  |
| 13 | Maximum flux density in the columns |  | T | 1.6 |  |
| 14 | Maximum flux density in the yoke |  | T | 1.65 |  |
| 15 | No load Current at rated voltage and frequency |  | % | 1.5% of Full Load Current |  |
| 16 | Magnetizing current, at rated frequency, on principal tapping, At 100% of rated voltage |  | % | 0.16% of In (Percent of Rated current) |  |
| 17 | Magnetizing current, at rated frequency, on principal tapping, At 110% of rated voltage |  | % | 0.3% of In (Percent of Rated current) |  |
| 18 | Temperature rise limits at rated voltage and power | Winding | ℃ | 60 |  |
|  |  | Top oil | ℃ | 55 |  |
| 19 | 1.2/50 micro-sec Lightning impulse withstand HV LV |  | kV | 33 170 95 |  |
| 20 | 1-minute Power Frequency withstand HV LV |  | kV | 33 70 28 |  |
| 21 | Bushing Type |  |  | Porcelain - Condenser |  |
| 22 | Bushing creepage distance |  | mm/kV | 31 |  |
| 23 | Equipped with Jacking pads |  |  | Yes |  |
| 24 | Tapping range, steps & location |  |  | +10% to -10% @1.25% |  |
| 25 | Tap changer type |  |  | OLTC (MR Germany) – Vacuum type |  |
| 26 | Tap changer accessories |  |  | Motor drive unit supplied on 380V AC for motor and controls at 220V AC, 50Hz; with local/remote control/indication and RTCC panel with AVR |  |
| 27 | Tap transition device |  |  | Resistor |  |
| 28 | Tap Changer Contact Rated Current |  | A | As per relevant IEC standard |  |
| 29 | Contact life at rated through current |  | No. of operations | ≥ 300,000 |  |
| 30 | Supply to Tap changer motor |  | V ac | 400 |  |
| 31 | Mechanical tap position indicator |  |  | Yes |  |
| 32 | Rated No load Losses |  | kW | ≤ 12 |  |
| 33 | Rated Load Losses |  | kW | ≤ 70 |  |
| 34 | Bushing CT’s to be provided |  |  | Yes |  |
| 35 | Altitude above sea level |  | m | 1500 |  |
| 36 | Ambient temperature |  | 0C | -1 to 48 |  |
| 37 | Relative Humidity (max) |  | % | 85 |  |
| 38 | Bulcholz relay for main tank |  |  | Yes |  |
| 39 | Bulcholz relay for tap changer |  |  | Yes |  |
| 40 | Bulcholz gas/oil collection/sampling pipe from ground level |  |  | Yes |  |
| 41 | Temperature gauges; (oil & winding) |  |  | Yes |  |
| 42 | Provision for remote indication of winding and oil temp. via transducers |  |  | Yes |  |
| 43 | Brackets for mounting surge arrestors |  |  | Yes |  |
| 44 | Pressure relief device (valve) |  |  | Yes |  |
| 45 | Skid under base |  |  | Yes |  |
| 46 | Main tank vacuum proof |  |  | Yes |  |
| 47 | Shock/Impact recorders during transportation |  |  | Yes |  |
| 48 | Bushing CT’s included |  |  | Yes |  |
| 49 | Previous type test |  |  | To be provided with bid |  |
| 50 | Drawings |  |  | To be provided with bid |  |
| 51 | QA/QC documentation |  |  | To be provided with bid |  |
| 52 | Design Life Expectation at average 70% load factor (design calculation shall be submitted with the bid) |  | Years | 30 Years minimum |  |

## TECHNICAL SPECIFCATION FOR AUXILIARY TRANSFORMERS AND ASSOCIATED SWITCHGEAR

### Preamble

The station auxiliary transformer shall be connected to either the tertiary winding of the main power transformer or the busbar to provide LTAC supplies for the substation. It shall be finished and painted in a color that will match the main transformer. The unit shall be designed and manufactured to the best engineering practice guided by IEC 60076 standard. The specific ratings and other design requirements are given in the schedule below:

### 100KVA, 33/0.4kV STATION AUXILIARY TRANSFORMER

| Item | Technical Details | Units |  | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- | --- |
| 1 | Type |  |  | Outdoor, oil filled |  |
| 2 | Rated power | kVA |  | 100 |  |
| 3 | Nominal Primary Voltage | kV |  | 33 |  |
| 4 | Rated voltage - primary | kV |  | 36 |  |
| 5 | Nominal Secondary Voltage | V |  | 400 |  |
| 6 | Rated voltage – secondary | V |  | 440 |  |
| 7 | Vector Group |  |  | Dyn11 |  |
| 8 | Phases |  |  | 3 |  |
| 9 | Type of cooling |  |  | ONAN |  |
| 10 | Type of insulating oil |  |  | Mineral oil as per IEC 60296 |  |
| 11 | Frequency | Hz |  | 50 |  |
| 12 | Winding Material |  |  | Copper |  |
| 13 | Impedance | % |  | Standard value |  |
| 14 | Temperature rise limits at rated voltage and power | Winding | 0C | 60 |  |
|  |  | Top oil | 0C | 55 |  |
| 15 | Lightning impulse withstand HV/LV | kV |  | 170/2.5 |  |
| 16 | Power Frequency withstand HV/LV | kV |  | 70/1 |  |
| 17 | Bushing Type |  |  | Porcelain HV and LV bushings |  |
| 18 | Bushing creepage distance | mm/kV |  | 31 |  |
| 19 | Equipped with lifting lugs |  |  | Yes |  |
| 20 | Oil Temperature Gauge |  |  | Yes |  |
| 21 | Pressure Release Valve |  |  | Yes |  |
| 22 | Tap changer Type |  |  | Off Load |  |
| 23 | Tapping range |  |  | +5% to -5% in steps of 2.5% |  |
| 24 | Mechanical tap position indicator |  |  | Yes |  |
| 25 | Rated No load Losses | kW |  | ≤ 1% according to EU eco-design regulations of 2021 for tier 2 transformers |  |
| 26 | Rated Load Losses | kW |  | ≤ 1% according to EU eco-design regulations of 2021 for tier 2 transformers |  |
| 27 | Altitude above sea level | m |  | 1400 |  |
| 28 | Operating ambient temperature | 0C |  | -1 to 40 |  |

### TECHNICAL SCHEDULE  FOR AUXILIARY TRANSFORMER SWITCHGEAR (33KV)

| Item | Parameter Description For 36kv Circuit Breaker | Unit | Technical Guarantee Data |  |
| --- | --- | --- | --- | --- |
|  |  |  | Schedule A: Min. Requirements | Schedule B: Bidder Guarantee |
|  |  |  | 36kV Vacuum outdoor circuit Breaker |  |
| 1 | Scope: Design, manufacture, testing, supply & installation. |  | Yes |  |
| 2 Design & Construction |  |  |  |  |
| 2.1 | Type designation |  | Bidder to Indicate |  |
| 2.2 | Reference Standard |  | IEC 62271-100 IEC 62271-1 |  |
| 2.3 | No. of poles/circuit breaker |  | 3 |  |
| 2.4 | Type of control mechanism |  | Motor operated spring |  |
| 2.4.1 | Mechanical class |  | M2 |  |
| 2.5 | Protection level of electrical cubicle |  | IP54 |  |
| 2.6 | Protection level of operating mechanism |  | IP55 |  |
| 2.7 | Type of insulator |  | Porcelain or silicone rubber |  |
| 2.8 | Insulating gas |  | Vacuum |  |
| 2.9 | Rated absolute pressure at 20oC |  | Bidder to indicate |  |
| 2.10 | Relative leakage rate | %/yr | ˂0,5% (for SF6) |  |
| 2.11 | Circuit breaker class |  | Outdoor |  |
| 2.12 | Support structures supplied |  | Yes |  |
| 3 Service Conditions |  |  |  |  |
| 3.1 | Altitude of installation (a.s.l.) | m | 1500 |  |
| 3.2 | Operating ambient temperature | oC | -1 to +48 |  |
| 3.3 | Relative humidity (max) | % | 90 |  |
| 3.4 | Pollution levels | mm/kV | 31 |  |
| 4 Rated Characteristics |  |  |  |  |
| 4.1 | Rated voltage | kV | 33 |  |
| 4.2 | Maximum service voltage | kV | 36 |  |
| 4.3 | Rated frequency | Hz | 50 |  |
| 4.4 | Rated continuous current | A | 50 |  |
| 4.5 | Rated peak withstand current | kApk | 80 |  |
| 4.6 | Rated short time withstand current | kA | 31.5 |  |
| 4.7 | Rated duration of short circuit | s | 3 |  |
| 4.8 | One min. power frequency withstand voltage: |  |  |  |
|  | phase to earth | kV | 75 |  |
|  | Across open contacts | kV | 75 |  |
| 4.9 | Rated lightning impulse withstand voltage: |  |  |  |
|  | phase to earth | kVpk | 170 |  |
|  | across open contacts | kVpk | 170 |  |
| 5. Breaking and Making Characteristics |  |  |  |  |
| 5.1 | Rated short circuit breaking current | kA | 31.5 |  |
| 5.2 | First pole to clear factor |  | 1.5 |  |
| 5.3 | DC component (% of AC component) | % | 43 |  |
| 5.4 | Peak value of rated short circuit making current | kApk | 80 |  |
| 5.5 | Rated breaking current for short line faults |  | As per IEC Standard |  |
| 5.6 | Rated out of phase breaking current | Id (kA) | 10 |  |
| 5.7 | Rated overvoltage factor for unloaded transformers |  | ˂2.5 |  |
| 5.8 | Rated line charging breaking current | A | 50 |  |
| 5.9 | Rated cable charging breaking current |  | 160 |  |
| 6. Operating Times |  |  |  |  |
| 6.1 | Rated opening time – from opening coil energizing to separation of main contacts | ms | ˂28 |  |
| 6.2 | Rated breaking time – from opening coil energizing to arc extinction | ms | ˂50 |  |
| 6.3 | Rated closing time – from closing coil energizing to main contact making | ms | ˂70 |  |
| 6.4 | Rated operating sequence |  | O-0.3s-CO-180s-CO |  |
| 6.5 | Rated operating sequence without motor supply |  | O-CO |  |
| 7 Low Voltage Specification |  |  |  |  |
| 7.1 | Motor voltage | V | 110, DC |  |
| 7.2 | Circuit motor protection |  | MCB |  |
| 7.3 | Motor voltage min. range | % | 85 |  |
| 7.4 | Motor voltage max. range | % | 110 |  |
| 7.5 | Opening voltage min. range | % | 65 |  |
| 7.6 | Opening voltage max. range | % | 110 |  |
| 7.7 | Closing voltage min. range | % | 75 |  |
| 7.8 | Closing voltage max. range | % | 110 |  |
| 7.9 | Lighting and heating circuit voltage | V | 220, AC |  |
| 7.10 | Local electrical control with two push button |  | Yes |  |
| 7.11 | Anti-pumping relay |  | Yes |  |
| 7.12 | Local/remote selector switch |  | Yes |  |
| 7.13 | Number of trip coils |  | 2 |  |
| 7.14 | Provision for trip coil supervision |  | Yes |  |
| 7.15 | Pole discrepancy feature |  | n/a |  |
| 7.16 | Signalling contacts for spring position/status |  | Yes, 1NO |  |
|  | Signalling contacts for SF6 gas low, block etc |  | Yes |  |
| 7.17 | Number of available auxiliary NO contacts |  | 8 |  |
| 7.18 | Number of available NC auxiliary contacts |  | 8 |  |
| 7.19 | Position indicator – O/I |  | Yes |  |
| 7.20 | Indicator for spring status |  | Yes |  |
| 7.21 | Gas for first filling plus 30% |  | Yes |  |
| 7.22 | SF6 filling equipment supplied |  | Yes |  |
| 7.23 | SF6 gas leakage detector supplied |  | Yes |  |
| 8 Documents and Drawings with Bid |  |  |  |  |
| 8.1 | Circuit breaker outline drawing |  | Yes |  |
| 8.2 | Foundation detail drawings |  | Yes |  |
| 8.3 | Quality assurance certification |  | Yes |  |
| 8.4 | Typical low voltage elementary diagram included in Bid |  | Yes |  |
| 9 Test Reports with Bid |  |  |  |  |
| 9.1 | Dielectric test |  | Yes |  |
| 9.2 | Temperature rise test |  | Yes |  |
| 9.3 | Short time withstand current test |  | Yes |  |
| 9.4 | Mechanical endurance test |  | Class M2 – 10,000 operations |  |
| 9.5 | Capacitive current breaking test |  | Yes |  |
| 9.6 | Operating times test |  | Yes |  |
| 9.7 | Main contact resistance test |  | Yes |  |

### 33KV XLPE CABLE TECHNICAL SCHEDULE

| Item | Detail | Unit | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- |
| 1 | Material of Conductor |  | Stranded Copper |  |
| 2 | Conductor Cross section area | mm2 | 300 |  |
| 3 | Number of Cores |  | 1 |  |
| 4 | Insulation |  | XLPE |  |
| 5 | Nominal Voltage (Uo/U) | kV | 19/33 |  |
| 6 | Highest System Voltage | kV | 36 |  |
| 7 | Nominal Current Rating | A | 460 |  |
| 8 | Partial Discharge | pC | <5 |  |
| 9 | Short circuit rating | kA/3s | 52 |  |
| 10 | Single layer Aluminium Wire Armour |  | Yes |  |
| 11 | Type of outer sheath |  | PE |  |
| 14 | Cable length per Drum | m | 500 |  |
| 15 | Type of drum (wooden or steel) |  | Treated Wooden |  |
| 16 | Technical/Manufacturer’s Brochure |  | To be provided |  |
| 17 | TYPE TEST |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| 18 | DRAWINGS |  | Supplier shall provide drawings showing dimensions |  |
| 19 | QUALITY ASSURANCE |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 11KV XLPE CABLE TECHNICAL SCHEDULE

| Item | Detail | Unit | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- |
| 1 | Material of Conductor |  | Stranded Copper |  |
| 2 | Conductor Cross section area | mm2 | 300 |  |
| 3 | Number of Cores |  | 1 |  |
| 4 | Insulation |  | XLPE |  |
| 5 | Nominal Voltage (Uo/U) | kV | 6.35/11 |  |
| 6 | Highest System Voltage | kV | 12 |  |
| 7 | Nominal Current Rating | A | 460 |  |
| 8 | Partial Discharge | pC | <5 |  |
| 9 | Short circuit rating | kA/3s | 52 |  |
| 10 | Single layer Aluminium Wire Armour |  | Yes |  |
| 11 | Type of outer sheath |  | PE |  |
| 14 | Cable length per Drum | m | 500 |  |
| 15 | Type of drum (wooden or steel) |  | Treated Wooden |  |
| 16 | Technical/Manufacturer’s Brochure |  | To be provided |  |
| 17 | TYPE TEST |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| 18 | DRAWINGS |  | Supplier shall provide drawings showing dimensions |  |
| 19 | QUALITY ASSURANCE |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 500KVA, 11/0.4kV STATION AUXILIARY TRANSFORMER

| Item | Technical Details | Units |  | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- | --- |
| 1 | Type |  |  | Outdoor, oil filled |  |
| 2 | Rated power | kVA |  | 500 |  |
| 3 | Nominal Primary Voltage | kV |  | 11 |  |
| 4 | Rated voltage - primary | kV |  | 12 |  |
| 5 | Nominal Secondary Voltage | V |  | 400 |  |
| 6 | Rated voltage – secondary | V |  | 440 |  |
| 7 | Vector Group |  |  | Dyn11 |  |
| 8 | Phases |  |  | 3 |  |
| 9 | Type of cooling |  |  | ONAN |  |
| 10 | Type of insulating oil |  |  | Mineral oil as per IEC 60296 |  |
| 11 | Frequency | Hz |  | 50 |  |
| 12 | Winding Material |  |  | Copper |  |
| 13 | Impedance | % |  | Standard value |  |
| 14 | Temperature rise limits at rated voltage and power | Winding | 0C | 60 |  |
|  |  | Top oil | 0C | 55 |  |
| 15 | Lightning impulse withstand HV/LV | kV |  | 95/2.5 |  |
| 16 | Power Frequency withstand HV/LV | kV |  | 28/1 |  |
| 17 | Bushing Type |  |  | Porcelain HV and LV bushings |  |
| 18 | Bushing creepage distance | mm/kV |  | 31 |  |
| 19 | Equipped with lifting lugs |  |  | Yes |  |
| 20 | Oil Temperature Gauge |  |  | Yes |  |
| 21 | Pressure Release Valve |  |  | Yes |  |
| 22 | Tap changer Type |  |  | Off Load |  |
| 23 | Tapping range |  |  | +5% to -5% in steps of 2.5% |  |
| 24 | Mechanical tap position indicator |  |  | Yes |  |
| 25 | Rated No load Losses | kW |  | ≤ 1% according to EU eco-design regulations of 2021 for tier 2 transformers |  |
| 26 | Rated Load Losses | kW |  | ≤ 1% according to EU eco-design regulations of 2021 for tier 2 transformers |  |
| 27 | Altitude above sea level | m |  | 1500 |  |
| 28 | Operating ambient temperature | 0C |  | -1 to 40 |  |

### 100KVA, 11/0.4kV STATION AUXILIARY TRANSFORMER

| Item | Technical Details | Units |  | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- | --- |
| 1 | Type |  |  | Outdoor, oil filled |  |
| 2 | Rated power | kVA |  | 100 |  |
| 3 | Nominal Primary Voltage | kV |  | 11 |  |
| 4 | Rated voltage - primary | kV |  | 12 |  |
| 5 | Nominal Secondary Voltage | V |  | 400 |  |
| 6 | Rated voltage – secondary | V |  | 440 |  |
| 7 | Vector Group |  |  | Dyn11 |  |
| 8 | Phases |  |  | 3 |  |
| 9 | Type of cooling |  |  | ONAN |  |
| 10 | Type of insulating oil |  |  | Mineral oil as per IEC 60296 |  |
| 11 | Frequency | Hz |  | 50 |  |
| 12 | Winding Material |  |  | Copper |  |
| 13 | Impedance | % |  | Standard value |  |
| 14 | Temperature rise limits at rated voltage and power | Winding | 0C | 60 |  |
|  |  | Top oil | 0C | 55 |  |
| 15 | Lightning impulse withstand HV/LV | kV |  | 95/2.5 |  |
| 16 | Power Frequency withstand HV/LV | kV |  | 28/1 |  |
| 17 | Bushing Type |  |  | Porcelain HV and LV bushings |  |
| 18 | Bushing creepage distance | mm/kV |  | 31 |  |
| 19 | Equipped with lifting lugs |  |  | Yes |  |
| 20 | Oil Temperature Gauge |  |  | Yes |  |
| 21 | Pressure Release Valve |  |  | Yes |  |
| 22 | Tap changer Type |  |  | Off Load |  |
| 23 | Tapping range |  |  | +5% to -5% in steps of 2.5% |  |
| 24 | Mechanical tap position indicator |  |  | Yes |  |
| 25 | Rated No load Losses | kW |  | ≤ 1% according to EU eco-design regulations of 2021 for tier 2 transformers |  |
| 26 | Rated Load Losses | kW |  | ≤ 1% according to EU eco-design regulations of 2021 for tier 2 transformers |  |
| 27 | Altitude above sea level | m |  | 1500 |  |
| 28 | Operating ambient temperature | 0C |  | -1 to 40 |  |

### TECHNICAL SCHEDULE FOR STATION AUXILIARY TRANSFORMER 11KV SWITCHGEAR

| Item |  |  | Unit | Value | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- | --- |
| TYPE |  |  |  | 11kV outdoor circuit breaker completely wired with CTs, VTs and fitted with an IED providing OCEF and SBEF protection, complete with 12m long pendant switch for remote opening and closing |  |
| BASIC DATA |  |  |  |  |  |
| Rated voltage (Highest system voltage) |  |  | kV | 12 |  |
| Rated continuous current at 40 oC ambient temperature: |  |  | A | 630 |  |
| Interruption Medium |  |  |  | vacuum |  |
| Rated frequency |  |  | Hz | 50 |  |
| Rated short time withstand current (3s) |  |  | kA | 31.5 |  |
| Arc Sensor installed in cable and bus chamber |  |  |  | YES |  |
| RATED INSULATION LEVEL |  |  |  |  |  |
| Lightning impulse dry withstand voltage |  |  | kV | 95 |  |
| One minute power-frequency wet withstand voltage |  |  | kV | 28 |  |
| OPERATING MECHANISM |  |  |  |  |  |
| Mechanism |  |  |  | ‘Trip Free’ spring mechanism |  |
| Rated supply voltage of closing mechanism |  |  | V dc | 110 |  |
| Rated supply voltage of shunt opening release |  |  | V dc | 110 |  |
| ENVIRONMENTAL CONDITIONS |  |  |  |  |  |
| Altitude above sea level |  |  | m | 1500 |  |
| Humidity |  |  | % | 85 |  |
| Electrical Endurance Class (IEC 602271) |  |  |  | E2 |  |
| Guaranteed No. of operations |  |  |  | 10000 |  |
| Operating ambient temperature |  |  | oC | -1 to 40 |  |
| Specific creepage distance |  |  | mm/kV | 31 |  |
| CT | CT ratio |  |  | 2000/1/1/1/1A |  |
|  | Core 1 | Burden | VA | 15 |  |
|  |  | Class |  | Class X Diff |  |
|  | Core 2 | Burden | VA | 15 |  |
|  |  | Class |  | ClassX, Vk=300V for REF protection |  |
|  | Core 3 | Burden | VA | 15 |  |
|  |  | Class |  | Class 5P20 For OCEF protection |  |
|  | Core 4 | Burden | VA | 15 |  |
|  |  | Class |  | Class 0.2s Metering |  |
| VT | VT ratio |  | V | 11000/110 |  |
|  | Burden |  | VA | 50 |  |
|  | Class |  |  | Class 0.2s for metering |  |
|  | Voltage Factor |  |  | 1.2 continuous; 1.9/30 sec |  |
| TYPE TEST |  |  |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| DRAWINGS |  |  |  | Supplier shall provide drawings showing dimensions |  |
| QUALITY ASSURANCE |  |  |  | Supplier shall provide Quality Assurance certificate with the bid |  |

### 11KV XLPE 630mm² CABLE TECHNICAL SCHEDULE

| S/N | DETAIL | UNIT | REQUIREMENT | TENDERER’S GUARANTEE |
| --- | --- | --- | --- | --- |
| 1. | Material of Conductor |  | Stranded Copper |  |
| 2. | Conductor Cross section area | mm2 | 630 |  |
| 3. | Number of Cores |  | 1 |  |
| 4. | Insulation |  | XLPE |  |
| 5. | Nominal Voltage (Uo/U) | kV | 6.35/11 |  |
| 6. | Highest System Voltage | kV | 12 |  |
| 7. | Nominal Current Rating | A | 895 |  |
| 8. | Partial Discharge | pC | <5 |  |
| 9. | Short circuit rating | kA/s | 31.5 |  |
| 10. | Single layer Aluminium Wire Armour |  | Yes |  |
| 11. | Type of outer sheath |  | PE |  |
| 12. | Cable length per Drum | m | 300 |  |
| 13. | Type of drum (wooden or steel) |  | Treated Wooden |  |
| 14. | Technical/Manufacturer’s Brochure |  | To be provided |  |
| 15. | TYPE TEST |  | Supplier shall provide previous type test certificate/results together with the bid |  |
| 16. | DRAWINGS |  | Supplier shall provide drawings showing dimensions |  |
| 17. | QUALITY ASSURANCE |  | Supplier shall provide Quality Assurance certificate with the bid |  |

## TECHNICAL SCHEDULE FOR CONTROL PANELS

| Description |  | Unit | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- |
| Panels | Type |  | Front access door with window |  |
|  | Mounting |  | Floor standing |  |
|  | Dimensions (H x W x D) |  | 2000 x 800 x 600 mm |  |
|  | Number |  | 5 |  |
| Functions | Protection |  | IEDs |  |
|  | Control |  | Push buttons on IED |  |
|  | Measurements |  | IEDs |  |
|  | Display of Measured Values |  | On IED mimic/HMI |  |
|  | Selector Switches |  | Local/Remote/Sup |  |
|  | Control Switches |  | CB Open/Close |  |
|  | AC/DC Wiring Protection |  | MCBs |  |
|  | Alarm Indication |  | On IED LEDs |  |
|  | Status Indication |  | On IED mimic/HMI |  |
|  | Panel Heating/Lighting |  | Yes |  |
|  | Test Interface |  | Yes |  |
| Technical Manufacturer’s/brochure |  |  | To be provided |  |

## TECHNICAL SCHEDULE FOR ELECTRONIC MULTIFUNCTIONAL ENERGY AND DEMAND METERS

| Item | Detail | Unit | Requirement | Tenderer’s Guarantee |
| --- | --- | --- | --- | --- |
| 1 | Type |  | CT/VT fed, 3phase 4 wire |  |
| 2 | Inputs |  | 1 A , 110V ac, 50Hz |  |
| 4 | Metering Accuracy |  | Class 0.2s |  |
| 5 | Load Profiling capability |  | Daily or monthly or yearly |  |
| 6 | Maximum Demand Period |  | 5, 10,15,30 or 60 Minutes |  |
| 7 | Display |  | A, kV, kVA, kW, kVAr , kWh, kVArh, kVAh, in primary values, Monthly Maximum Demand, (kW) and Monthly Power Factor. |  |
| 8 | Memory |  | Store at least 12 monthly billing data (kW,kWh,PF) |  |
|  | TYPE TEST |  | Supplier shall provide previous type test certificate/results together with the bid |  |
|  | QUALITY ASSURANCE |  | Supplier shall provide Quality Assurance certificate with the bid |  |

## TECHNICAL SCHEDULE FOR METERING

### Smart Energy Meter

| S/N | DETAIL | UNIT | # ZESCO DATA | # BIDDER’S GUARANTEED TECHNICAL DATA |
| --- | --- | --- | --- | --- |
| 1 | Nominal Voltage, (phase to phase) Un | V | 64-240 AC/DC±20% |  |
| 2 | Capabilities |  | Time of use (TOU) metering, Import and Export measuring, shall record the kWh, kVAh, kVArh, and the Maximum Demand (kVA, kW) with date & time of occurrence for both import and export directions. The Maximum Demand shall be user programmable to kVA or kW. ALL READINGS TO BE PRIMARY VALUES. Instrument Transformer CT and VT ratios shall be programmable on the meter. The readings shall be scalable to Mega or kilo depending on magnitude. |  |
| 3 | Voltage Range | V | 80 – 115%Un |  |
| 4 | Tolerance | % | -20, +15 |  |
| 5 | Supply Frequency | Hz | 50 |  |
| 6 | Frequency Variation | % | ±2.5 |  |
| 7 | Current Rating, In | A | 1/5 programmable to any CT ratio |  |
| 8 | Starting Current (0.002 In) | mA | 2/10 |  |
| 9 | Maximum Current Rating (1.5 In) | A | 1.5/7.5 |  |
| 10 | Maximum Power Consumption | VA W | 15 3 |  |
| 11 | Integration Period |  | User programmable (1 to 60 minutes) |  |
| 12 | System |  | 3 phase 4 wire, 3 phase 3 wire. The meter shall be programmable for the two systems. |  |
| 13 | Accuracy Class |  | Class 0.2s or better |  |
| 14 | Short Circuit Rating | A | 20Imax |  |
| 15 | Impulse Voltage | kV | 3 |  |
| 16 | CT Polarity reversal |  | Able to detect and record date of occurrence and restoration with phase identification |  |
| 17 | Operating Temperature Range | oC | -5, +50 |  |
| 18 | Altitude | m | 1400 |  |
| 19 | Humidity | % | 85 |  |
| 20 | IP Rating |  | IP54 |  |
| 21 | Installation |  | At least two seals |  |
| 22 | Meter Display Information and measurements |  | 9-digit electronic display mimimum, with graphical, backlight extended temperature Size: 69 x 39 mm (H x W), 128x80 pixels Pixel size: 0.5 mm² Max display character size 10 x 5 mm (H x W) as minimum |  |
| 23 | Communications |  |  |  |
|  | Optical Communication |  | - Protocol: DLMS, baud rate:1200 – 19200, half duplex - Hardware IEC 62056-21/IEC1107 |  |
|  | Ethernet port |  | - 10/100 Mbps, Protocol: DLMS and MODBUS TCP simultaneous client - Full duplex |  |
|  | Serial Communication port RS232 |  | Protocol: DLMS, Baud rate: 1200 –57600 bps, Half duplex |  |
|  | RS485 port |  | Protocol: Configurable DLMS/MODBUS RTU, Baud rate: 1200 – 57600 bps, Half duplex |  |
|  | Inbuilt IEC61850 |  | - Logical nodes: LLNO, LPHD, MMXU, MMTR, MHAI, MABT Reports (RCB) - Time synchronization – SNTP/PTP |  |
|  | Connector type |  | standard RJ45 for all the ports except optical |  |
| 24 | Over-current protection with a short circuit current | kA | 2.5 |  |
| 25 | Meter shall have provision for the user to view a pre-configured cycle | YES/NO | YES |  |
| 26 | Lightning protection according to: |  | BS 1524 and IEC62053-22 |  |
| 27 | Anti-Tempering Features |  | - Tamper protection - Tamper logging/indications - AMR functionalities |  |
| 28 | Applicable electronic Meter software | Lot | Windows based software for site programming and downloading. The meter should be fully user programmable and downloadable. |  |
| 29 | Time of Use Registers (TOU) | No. | 8 minimum |  |
| 30 | Maximum Demand Registers | No. | 8 minimum |  |
| 31 | Configurable Volt Free Input/Output Relays (Internal & normally open) for energy pulse outputs. | No. | 4 minimum |  |
| 32 | Fixed output contacts | No. | 4 minimum |  |
| 33 | Battery | 1 | Field-replaceable battery for RTC backup and meter reading during power outage |  |
| 34 | Casing |  | House Service Pattern Case, extended Terminal Cover |  |
| 35 | Historical Data |  | Load Profiling (450 days, 1 Channel, 30 minutes), at least twelve months historical active energy, reactive energy and maximum demand billing data logging in meter memory. At least twelve months of sets of historical data |  |
| 36 | Quality Assurance Certificate |  | To be provided with the bid |  |
| 37 | Routine test results |  | To be provided on delivery of meters |  |
| 38 | Previous Type test results |  | To be provided with the bid |  |
| 39 | Meter features and functionalities brochure including drawings showing dimensions of meter |  | To be provided with the bid |  |
| 40 | Applicable standards |  | IEC 62052-11, IEC 62053-21, IEC 62053-22, IEC 62053-23, IEC 62053-61, IEC 62056 |  |
| 50 | Sample meter |  | To be provided with bid |  |

### Metering Panel/Enclosure

| S/N | DETAILS | DATA | BIDDER’S GUARANTEED TECHNICAL DATA |
| --- | --- | --- | --- |
| 1 | Mounting | Indoor floor standing |  |
| 2 | Material | Made of metal. Should not corrode, weather resistant, easily cleaned and can be painted. |  |
| 4 | Enclosures Accessories | Meter test terminal blocks with shorting links provisions for current circuits and isolating links for voltages. Mounting rails for terminal blocks for currents and voltages. Glanded or shrouded cable entry and exit holes. The panels should be vermin proof. The panel should have earth bar. The panel should have 230V A.C. supply provision and lighting. |  |
| 5 | I`P Rating | IP54 |  |
| 6 | Panel door | Front doors Hinged on the right (right hand opening) and rubber lined. |  |
| 7 | Colour | Grey |  |
| 8 | Environmental temperature withstand | -5,+ 40oC |  |
| 9 | Viewing window | Front door shall have shatterproof window for viewing status of meters. |  |
| 10 | Samples drawings and pictures | To be provided at bidding. Panel should generally be similar to the existing ZESCO metering panels in size and provisions. Dimensions: The front view dimensions: 800mm x2200mm Side view dimensions: 830mm x 2200mm Outside door dimension: 760mm x 1930mm View Glass: 420mm x 1570mm Inner door: 700mm x 1870mm. Pictures attached. |  |

### Metering Server

| S/N | DESCRIPTION | BIDDER’S GUARANTEED TECHNICAL DATA |
| --- | --- | --- |
| 1 | HP Proliant DL380 Rack Server/Dell Power Edge R750 |  |
| 2 | Complete Ventilated Rack mounted Packaging |  |
| 3 | 500W Dual power supply Efficient Chassis |  |
| 4 | Linux Server OS UK |  |
| 5 | Linux 64 Bit Factory Image Recovery |  |
| 6 | Intel Xeon 2.80Ghz CPU or better |  |
| 7 | 64GB DDR3-1600 ECC (4x16GB) RAM |  |
| 9 | NVIDIA NVS 310 512MB Graphics |  |
| 10 | NVIDIA NVS 310 512MB 2nd Graphics |  |
| 11 | 4TB SATA Solid State Hard Drive in RAID-5 |  |
| 12 | USB Standard Keyboard |  |
| 13 | USB Optical Scroll Mouse |  |
| 14 | 16X SuperMulti DVDRW SATA 1st ODD |  |
| 15 | 4 x Intel CT x1 PCIe NIC |  |
| 16 | 3-Year Warranty EURO |  |
| 17 | RAID Card |  |
| 18 | Processor Air Cooling Kit |  |
| 19.0 | Software Operating system |  |
| 19.1 | Linux Server Office |  |
| 19.2 | Microsoft Office 2019 OEM Basic Anti-virus |  |
| 19.3 | McAfee, 1year SW updates included |  |
| 20 | Monitors: 17-inch LED Monitor built into Server Rack |  |

### Metering Workstation

| S/N | DESCRIPTION | BIDDER’S GUARANTEED TECHNICAL DATA |
| --- | --- | --- |
| 1 | HP Z420 Workstation |  |
| 2 | HP Single Unit Packaging |  |
| 3 | HP Z420 600W 90% Efficient Chassis |  |
| 4 | Microsoft Windows 7 Ultimate Edition 64bit OS UK |  |
| 5 | Windows 7 64 Bit Factory Image Recovery |  |
| 6 | Intel Xeon E5-1603 2.80Ghz 10MB 1066 4C CPU |  |
| 7 | 6GB DDR3-1600 ECC (3x2GB) RAM |  |
| 9 | NVIDIA NVS 310 512MB Graphics |  |
| 10 | NVIDIA NVS 310 512MB 2nd Graphics |  |
| 11 | 500GB 7200 RPM SATA 1st Hard Drive |  |
| 12 | HP USB Standard Keyboard |  |
| 13 | HP USB Optical Scroll Mouse |  |
| 14 | 16X SuperMulti DVDRW SATA 1st ODD |  |
| 15 | Intel CT x1 PCIe NIC |  |
| 16 | HP 3/3/3 Warranty EURO |  |
| 17 | HP Z420 Country Kit |  |
| 18 | HP Processor Air Cooling Kit |  |
| 19.0 | Software Operating system |  |
| 19.1 | Windows 7 is included in HW above. Office |  |
| 19.2 | Microsoft Office 2010 OEM Basic Anti-virus |  |
| 19.3 | McAfee, 1year SW updates included |  |
| 20 | Monitors: HP ZR2440w 61 cm (24") LED Backlit IPS Monitor |  |

## TECHNICAL SCHEDULE FOR METERING AND PROTECTION

### CONTROL AND SUPPLY CIRCUITS

| Auxiliary voltage for - Closing - Tripping | 110/220 V DC 110/220 V DC |
| --- | --- |
| Supply voltage for auxiliary equipment | 380 V, 50 Hz Three Phase & Neutral |
| Supply voltage for protection schemes | 110/220 V DC |
| Supply for indications and alarms | 110/220 V DC |
| Power supply for SCADA, and supervisory equipment, carriers, PAX & Fibre Equipment. | 48V -110/220 DC |

### TECHNICAL METERING SCHEDULE

## PROTECTION TECHNICAL SCHEDULES

### LINE CURRENT DIFFERENTIAL PROTECTION RELAYS SCHEDULE 13a – INFORMATIVE DATA

| Item | Feature | ZESCO Minimum Specification | Bidders Specifications |
| --- | --- | --- | --- |
| 1 | LOGIC | Software based assignment/mapping of ; |  |
|  |  | Binary inputs: 32 |  |
|  |  | Binary outputs:32 |  |
|  |  | Internal protection functions |  |
| 2. | MONITORING AND CONTROL | Non volatile memory for; |  |
|  |  | Event recording |  |
|  |  | Disturbance recording |  |
|  |  | Fault location |  |
|  |  | Large LCD display with bay single line real time configuration for; |  |
|  |  | At least eight double indications |  |
|  |  | At least twenty four real time alarms to be available on LCD display |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
|  |  | Inbuilt; |  |
|  |  | Voltage Transformer Supervision |  |
|  |  | Current Transformer Supervision |  |
|  |  | Trip circuit supervision |  |
|  |  | HMI/Binary input based open/close control of at least six bay switch gear. |  |
| 3. | COMMUNICATION | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | All relay interrogation hardware and software |  |
| 4. | AC Current inputs | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  | AC Voltage Inputs | The following shall be the VT requirements; |  |
|  |  | 110V AC nominal phase to phase input |  |
|  |  | Operating voltage of 0 to 200V AC |  |
|  |  | A continuous withstand of 2 times the nominal voltage. |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage. |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| 6. | Auxiliary Voltage | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| 7.FREQUENCY |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| 8. | Light Emitting Diodes (LEDs) | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| 9. | Binary Inputs | The binary inputs shall; |  |
|  |  | Optically be coupled |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
| 10. | Binary outputs contacts | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| 11. | Terminal connections | The following specifications shall apply for terminal connections; |  |
|  |  | At least 4mm2 for the CT and VT input circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| 12. | REFERENCE INTERNATIONAL STANDARD | The IEC 255 standard for protection relays shall apply. |  |
| 13. | LINE CURRENT DIFFERENTIAL PROTECTION | The following specifications shall apply; |  |
|  |  | Pole segregated tripping |  |
|  |  | Using Single mode SFP for 70-100km fibre for communication to remote end relay. |  |
|  |  | Impedance protection with full scheme distance protection |  |
|  |  | Power swing protection |  |
|  |  | Switch on to fault protection |  |
|  |  | Broken conductor check |  |
|  |  | Minimum of six settings groups |  |
| 14. | Over current and Earth fault protection | The following specifications shall apply; |  |
|  |  | At least three stage directional/non directional over current and earth fault elements with carrier aided operation option |  |
|  |  | Selectable IEC/IEEE operation characteristics for all elements |  |
|  |  | Breaker failure |  |
|  |  | Thermal over load protection |  |
| 15. | Power protection | The following specifications shall apply; |  |
|  |  | Directional under/over active and reactive power protection |  |
| 16. | Voltage protection | The following specifications shall apply; |  |
|  |  | At least two stage over/under voltage protection |  |
|  |  | At least two stage residuals over voltage protection |  |
|  |  | Loss of voltage protection |  |
| 17. | Frequency protection | The following specifications shall apply; |  |
|  |  | At least 4 stage Over/under frequency protection |  |
|  |  | Rate of change of frequency protection |  |
| 18. | Control and Synch check | The following specifications shall apply; |  |
|  |  | Reasonably large mimic LCD for bay switchgear position indication and control with at least six open/close control commands of bay switch gear. |  |
|  |  | Manual close and auto-reclose breaker control with split frequency, differential voltage and voltage magnitude plus live |  |
|  |  | Line - live bus, live line - dead bus and dead line – live bus check on synch |  |
| 19. | PRODUCT VERSION | The relays shall be the top of range commercially produced and market proven reliability of service. |  |

### LINE DISTANCE PROTECTION RELAYS SCHEDULE 13a – INFORMATIVE DATA

| Item | Feature | ZESCO Minimum Specification | Bidders Specifications |
| --- | --- | --- | --- |
| 1 | LOGIC | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| 2. | MONITORING AND CONTROL | Non-volatile memory for; |  |
|  |  | Event recording |  |
|  |  | Disturbance recording |  |
|  |  | Fault location |  |
|  |  | Large LCD display with bay single line real time configuration for; |  |
|  |  | At least eight double indications |  |
|  |  | At least twenty four real time alarms to be available on LCD display |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
|  |  | Inbuilt; |  |
|  |  | Voltage Transformer Supervision |  |
|  |  | Current Transformer Supervision |  |
|  |  | Trip circuit supervision |  |
|  |  | HMI/Binary input based open/close control of at least six bay switch gear. |  |
| 3. | COMMUNICATION | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | All relay interrogation hardware and software |  |
| 4. | AC Current inputs | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  | AC Voltage Inputs | The following shall be the VT requirements; |  |
|  |  | 110V AC nominal phase to phase input |  |
|  |  | Operating voltage of 0 to 200V AC |  |
|  |  | A continuous withstand of 2 times the nominal voltage. |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage. |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| 6. | Auxiliary Voltage | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| 7.FREQUENCY |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| 8. | Light Emitting Diodes (LEDs) | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| 9. | Binary Inputs | The binary inputs shall; |  |
|  |  | Optically be coupled |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty four inputs. |  |
| 10. | Binary outputs contacts | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| 11. | Terminal connections | The following specifications shall apply for terminal connections; |  |
|  |  | At least 4mm2 for the CT and VT input circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| 12. | REFERENCE INTERNATIONAL STANDARD | The IEC 255 standard for protection relays shall apply. |  |
| 13. | UNDER IMPEDANCE PROTECTION | The following specifications shall apply; |  |
|  |  | Full scheme distance protection |  |
|  |  | Power swing protection |  |
|  |  | Switch on to fault protection |  |
|  |  | Broken conductor check |  |
|  |  | Minimum of six settings groups |  |
| 14. | Over current and Earth fault protection | The following specifications shall apply; |  |
|  |  | At least three stage directional/non-directional over current and earth fault elements with carrier aided operation option |  |
|  |  | Selectable IEC/IEEE operation characteristics for all elements |  |
|  |  | Breaker failure |  |
|  |  | Thermal over load protection |  |
| 15. | Power protection | The following specifications shall apply; |  |
|  |  | Directional under/over active and reactive power protection |  |
| 16. | Voltage protection | The following specifications shall apply; |  |
|  |  | At least two stage over/under voltage protection |  |
|  |  | At least two stage residuals over voltage protection |  |
|  |  | Loss of voltage protection |  |
| 17. | Frequency protection | The following specifications shall apply; |  |
|  |  | At least 4 stage Over/under frequency protection |  |
|  |  | Rate of change of frequency protection |  |
| 18. | Control and Synch check | The following specifications shall apply; |  |
|  |  | Reasonably large mimic LCD for bay switchgear position indication and control with at least six open/close control commands of bay switch gear. |  |
|  |  | Manual close and auto-reclose breaker control with split frequency, differential voltage and voltage magnitude plus live |  |
|  |  | Line - live bus, live line - dead bus and dead line – live bus check on synch |  |
| 19. | PRODUCT VERSION | The relays shall be the top of range commercially produced and market proven reliability of service. |  |

### SCHEDULE 13b - INFORMATIVE DATA BACK UP PROTECTION RELAYS

| Item | Feature | ZESCO Minimum Specification | Bidders Specifications |
| --- | --- | --- | --- |
| 1 | LOGIC | Software based assignment/mapping of; |  |
|  |  | Binary inputs |  |
|  |  | Binary outputs |  |
|  |  | Internal protection functions |  |
| 2. | MONITORING AND CONTROL | Non-volatile memory for; |  |
|  |  | Event recording |  |
|  |  | Disturbance recording |  |
|  |  | Fault location |  |
|  |  | Large LCD display with bay single line real time configuration for; |  |
|  |  | At least eight double indications |  |
|  |  | At least twenty-four real time alarms to be available on LCD display |  |
|  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
|  |  | Inbuilt; |  |
|  |  | Voltage Transformer Supervision |  |
|  |  | Current Transformer Supervision |  |
|  |  | Trip circuit supervision |  |
|  |  | HMI/Binary input based open/close control of at least six bay switch gear. |  |
| 3. | COMMUNICATION | The following shall be the communication requirements; |  |
|  |  | 61850 to interface all substation IEDs |  |
|  |  | Front port for direct PC – relay administration |  |
|  |  | All relay interrogation hardware and software |  |
| 4. | AC Current inputs | The following shall be the CT requirements; |  |
|  |  | 1A and 5A |  |
|  |  | Continuous withstand – 3 times the nominal value |  |
|  |  | 1 second withstand – 100 times the nominal value |  |
|  |  | High immunity to CT saturation and harmonic distortion |  |
|  | AC Voltage Inputs | The following shall be the VT requirements; |  |
|  |  | 110V AC nominal phase to phase input |  |
|  |  | Operating voltage of 0 to 200V AC |  |
|  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  | High immunity to VT saturation and harmonic distortion |  |
| 6. | Auxiliary Voltage | The following shall be the auxiliary voltage requirements; |  |
|  |  | Rated for DC and AC operation |  |
|  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| 7.FREQUENCY |  | The following shall be the frequency requirements; |  |
|  |  | 50Hz will be used |  |
|  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| 8. | LIGHT EMITTING DIODES (LEDS) | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| 9. | Binary Inputs | The binary inputs shall; |  |
|  |  | Optically be coupled |  |
|  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  | Be programmable to internal protection functions |  |
|  |  | Have a minimum of twenty-four inputs. |  |
| 10. | Binary outputs contacts | The following specifications shall apply for relay binary output contacts; |  |
|  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  | Sub cycle operation time for all assigned protection functions |  |
| 11. | Terminal connections | The following specifications shall apply for terminal connections; |  |
|  |  | At least 4mm2 for the CT and VT input circuits |  |
|  |  | At least 2.5mm2 for DC circuits |  |
| 12. | REFERENCE INTERNATIONAL STANDARD | The IEC 255 standard for protection relays shall apply. |  |
| 13. | UNDER IMPEDANCE PROTECTION | The following specifications shall apply; |  |
|  |  | distance protection |  |
|  |  | Out of step |  |
|  |  | Switch on to fault protection |  |
|  |  | Broken conductor check |  |
|  |  | Minimum of six settings groups |  |
| 14. | Over current and Earth fault protection | The following specifications shall apply; |  |
|  |  | At least three stage directional/non-directional over current and earth fault elements with carrier aided operation option |  |
|  |  | Selectable IEC/IEEE operation characteristics for all elements |  |
|  |  | Breaker failure |  |
|  |  | Thermal overload protection |  |
| 15. | Power protection | The following specifications shall apply; |  |
|  |  | Directional under/overactive and reactive power protection |  |
| 16. | Voltage protection | The following specifications shall apply; |  |
|  |  | At least two stage over/under voltage protection |  |
|  |  | At least two stage residual over voltage protection |  |
|  |  | Loss of voltage protection |  |
| 17. | Frequency protection | The following specifications shall apply; |  |
|  |  | At least 4 stage Over/under frequency protection |  |
|  |  | Rate of change of frequency protection |  |
| 18. | Control and Synch check | The following specifications shall apply; |  |
|  |  | Reasonably large mimic LCD for bay switchgear position indication and control with at least six open/close control commands of bay switch gear. |  |
|  |  | Manual close and auto-reclose breaker control with split frequency, differential voltage and voltage magnitude plus live. |  |
|  |  | Line - live bus, live line - dead bus and deadline – live bus check on synch |  |
| 19. | PRODUCT VERSION | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
| 20. | THERMAL OVER LOAD PROTECTION | This element shall be available |  |
| 21. | NEGATIVE PHASE SEQUENCE PROTECTION | This element shall be available with selectable IEC characteristics |  |
| 22. | BREAKER FAILURE | At least one element. |  |

### TRANSFORMER DIFFERENTIAL PROTECTION RELAYS SCHEDULE 13c - INFORMATIVE DATA

| Item |  | Feature | ZESCO Minimum Specification | Bidders Specifications |
| --- | --- | --- | --- | --- |
| 1 |  | LOGIC | Software based assignment/mapping of; |  |
|  |  |  | Binary inputs |  |
|  |  |  | Binary outputs |  |
|  |  |  | Internal protection functions |  |
| 2. |  | MONITORING AND CONTROL | Non-volatile memory for; |  |
|  |  |  | Event recording |  |
|  |  |  | Disturbance recording |  |
|  |  |  | Fault location |  |
|  |  |  | Large LCD display with bay single line real time configuration for; |  |
|  |  |  | At least eight double indications |  |
|  |  |  | At least twenty-four real time alarms to be available on LCD display |  |
|  |  |  | Real time current, voltage, symmetrical components, real power, reactive power and apparent power real time display. |  |
|  |  |  | Inbuilt; |  |
|  |  |  | Voltage Transformer Supervision |  |
|  |  |  | Current Transformer Supervision |  |
|  |  |  | Trip circuit supervision |  |
|  |  |  | HMI/Binary input based open/close control of at least six bay switch gear. |  |
| 3. |  | COMMUNICATION | The following shall be the communication requirements; |  |
|  |  |  | 61850 to interface all substation IEDs and SCADA interface. |  |
|  |  |  | Front port for direct PC – relay administration |  |
|  |  |  | All relay interrogation hardware and software |  |
| 4. |  | AC Current inputs | The following shall be the CT requirements; |  |
|  |  |  | 1A and 5A |  |
|  |  |  | Continuous withstand – 3 times the nominal value |  |
|  |  |  | 1 second withstand – 100 times the nominal value |  |
|  |  |  | High immunity to CT saturation and harmonic distortion |  |
|  |  | AC Voltage Inputs | The following shall be the VT requirements; |  |
|  |  |  | 110V AC nominal phase to phase input |  |
|  |  |  | Operating voltage of 0 to 200V AC |  |
|  |  |  | A continuous withstand of 2 times the nominal voltage |  |
|  |  |  | A short time (1 second) withstand of at least 3 times the nominal voltage |  |
|  |  |  | High immunity to VT saturation and harmonic distortion |  |
| 6. |  | Auxiliary Voltage | The following shall be the auxiliary voltage requirements; |  |
|  |  |  | Rated for DC and AC operation |  |
|  |  |  | AC: 50 to 250 V AC with a relay administration software/HMI selectable nominal value |  |
|  |  |  | DC: 24 to 250 V DC with a relay administration software/HMI selectable nominal value |  |
| 7.FREQUENCY |  |  | The following shall be the frequency requirements; |  |
|  |  |  | 50Hz will be used |  |
|  |  |  | Stability of all protection functions for operation frequency range of at least 40 to 60Hz for the 50Hz nominal frequency. |  |
| 8. | Light Emitting Diodes (LEDs) |  | The relay shall have at least twelve LEDs programmable to binary input and internal protection function assignments. |  |
| 9. | Binary Inputs |  | The binary inputs shall; |  |
|  |  |  | Optically be coupled |  |
|  |  |  | Have DC input range of 24 to 250V DC with a software/HMI selectable nominal value |  |
|  |  |  | Be programmable to internal protection functions |  |
|  |  |  | Have a minimum of twenty-four inputs. |  |
| 10. | Binary outputs contacts |  | The following specifications shall apply for relay binary output contacts; |  |
|  |  |  | Make and carry at least 30A for 3 seconds for all out put contacts |  |
|  |  |  | Carry at least 10A continuously at 300V for all output contacts |  |
|  |  |  | Loaded contacts to perform not less 10,000 operations |  |
|  |  |  | Unloaded contacts to perform at least 100,000 operations |  |
|  |  |  | Relay healthy and watchdog contacts to be provided |  |
|  |  |  | A minimum of 36 programmable binary output contacts to be provided. |  |
|  |  |  | Sub cycle operation time for all assigned protection functions |  |
| 11. | Terminal connections |  | The following specifications shall apply for terminal connections; |  |
|  |  |  | At least 4mm2 for the CT and VT input circuits |  |
|  |  |  | At least 2.5mm2 for DC circuits |  |
| 12. | REFERENCE INTERNATIONAL STANDARD |  | The IEC 255 standard for protection relays shall apply. |  |
| 13. | OPTIONAL UNDER IMPEDANCE PROTECTION |  | The following specifications shall apply; |  |
|  |  |  | distance protection elements |  |
|  |  |  | Out of step |  |
|  |  |  | Switch on to fault protection |  |
|  |  |  | Broken conductor check |  |
|  |  |  | Minimum of six settings groups |  |
| 14. | Over current and Earth fault protection |  | The following specifications shall apply; |  |
|  |  |  | At least three stage directional/non-directional over current and earth fault elements with carrier aided operation option |  |
|  |  |  | Selectable IEC/IEEE operation characteristics for all elements |  |
|  |  |  | Breaker failure |  |
|  |  |  | Thermal over load protection |  |
| 15. | Power protection |  | The following specifications shall apply; |  |
|  |  |  | Directional under/over active and reactive power protection |  |
| 16. | Voltage protection |  | The following specifications shall apply; |  |
|  |  |  | At least two stage over/under voltage protection |  |
|  |  |  | At least two stage residual over voltage protection |  |
|  |  |  | Loss of voltage protection |  |
| 17. | Frequency protection |  | The following specifications shall apply; |  |
|  |  |  | At least 4 stage Over/under frequency protection |  |
|  |  |  | Rate of change of frequency protection |  |
| 18. | Control and Synch check |  | The following specifications shall apply; |  |
|  |  |  | Reasonably large mimic LCD for bay switchgear position indication and control with at least six open/close control commands of bay switch gear. |  |
|  |  |  | Manual close and auto-reclose breaker control with split frequency, differential voltage and voltage magnitude plus live |  |
|  |  |  | Line - live bus, live line - dead bus and dead line – live bus check on synch |  |
| 19. | PRODUCT VERSION |  | The relays shall be the top of range commercially produced and market proven reliability of service. |  |
| 20 | AUTOMATIC VOLTAGE REGULATOR |  | The AVR function shall have the following features; Position indication Raise/lower commands Block Master/ follower Manual/Auto Independent/parallel Line drop compensation Out of step |  |
| 21. | OVER EXCITATION/OVER FLUXING PROTECTION |  | Over fluxing protection with software selectable characteristic |  |
| 22. | THERMAL OVER LOAD PROTECTION |  | This element shall be available |  |
| 23. | NEGATIVE PHASE SEQUENCE PROTECTION |  | This element shall be available with selectable IEC characteristics |  |
| 24. | DIFFERENTIAL PROTECTION |  | Low impedance four winding differential protection shall be available |  |
| 25. | RESTRICTED EARTH FAULT PROTECTION |  | Four winding restricted earth fault protection shall be available. |  |
| 26. | BREAKER FAILURE |  | There shall be at least three breaker (HV, MV and LV) breaker failure protection elements in the relay. |  |

## TELECOMMUNICATION EQUIPMENT TECHNICAL SCHEDULES

### TECHNICAL SCHEDULE FOR OPTICAL TRANSPORT NETWORK (OTN) EQUIPMENT

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION | BIDDER’S GUARANTEED VALUES |
| --- | --- | --- | --- |
| 1.1 | OPTICAL TRANSPORT NETWORK (OTN) EQUIPMENT |  |  |
| 1.1.1 | Equipment Type | OTN |  |
| 1.1.2 | Equipment Supply Voltage | -48VDC to -54VDC |  |
| 1.1.3 | Transmission Capacity | 4000G or better |  |
| 1.1.4 | Local/Remote Management | Open for integration, managing and monitoring on the already operational ZTE Network Management System (NMS) |  |
| 1.1.5 | Transmission Distance without Signal Degradation | 300km + |  |
| 1.1.6 | Equipment/Product Main Characteristics | Unified cross connect platform (OTN/Packet/VC & ODU0, ODU1, ODU2, ODU3, ODU4, ODUflex) |  |
|  |  | Unified management |  |
|  |  | Reliability design (Supports 1+1 protection of main control, clock and power) |  |
|  |  | Intelligent Optical Network WAS |  |
|  |  | Intelligent ROADM |  |
|  |  | Smooth Expansion and Upgrade |  |
| 1.1.7 | Supported Services/Interfaces | 155MB |  |
|  |  | 1G |  |
|  |  | 2.5G |  |
|  |  | 10G |  |
|  |  | 100G |  |

### TECHNICAL SCHEDULE FOR PACKET TRANSPORT NETWORK (PTN) EQUIPMENT

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION | BIDDER’S GUARANTEED VALUES |  |
| --- | --- | --- | --- | --- |
| 1.1 | PACKET TRANSPORT NETWORK (PTN) EQUIPMENT |  |  |  |
| 1.1.1 | Equipment type | PTN |  |  |
|  | Equipment Supply Voltage | -48VDC to -54VDC |  |  |
| 1.1.2 | Transmission Capacity | 10G & 100G |  |  |
| 1.1.3 | Local/Remote Management | Open for integration, managing and monitoring on the already operational ZTE Network Management System (NMS) |  |  |
| 1.1.4 | Reliability design | Supports 1+1 protection of main control, clock and power) |  |  |
| 1.1.5 | Protection Switching | Automatic |  |  |
| 1.1.6 | Transmission module | Laser |  |  |
| 1.1.7 | Transmitter band | 1310nm |  |  |
| 1.1.8 | Receiver band | Not Applicable |  |  |
| 1.1.9 | Supported interfaces/rates | 100G |  |  |
|  |  | 10G |  |  |
|  |  | GE |  |  |
|  |  | 155Mbps |  |  |
|  |  | 100Mbps |  |  |
|  |  | 10Mbps |  |  |
|  |  | 2Mbps |  |  |
| 1.1.10 | Device board/module minimum configurations | DC Power board | 2 |  |
|  |  | System assist interface board | 1 |  |
|  |  | System main board | 2 |  |
|  |  | 100G optical interface board | 3 |  |
|  |  | 10G Ethernet optical interface board | 2 |  |
|  |  | 16 port Gigabit Ethernet optical interface board | 2 |  |
|  |  | 4port STM1 optical interface board | 2 |  |
|  |  | Electrical Tributary Emulation of E1 board (16 ports) | 1 |  |

### TECHNICAL SCHEDULE FOR SYNCHRONOUS DIGITAL HIERARCHY (SDH) MULTIPLEXER

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION | BIDDER’S GUARANTEED VALUES |
| --- | --- | --- | --- |
| 1.1 | SYNCHRONOUS DIGITAL HIERARCHY (SDH) MULTIPLEXER EQUIPMENT |  |  |
| 1.1.1 | Equipment type | SDH |  |
| 1.1.2 | Equipment Supply Voltage | -48VDC to -54VDC |  |
| 1.1.3 | Operation Mode | Add - Drop |  |
|  | Transmission Capacity | 10G |  |
| 1.1.4 | Local/Remote Management | Open for integration, managing and monitoring on the already operational ZTE Network Management System (NMS) |  |
| 1.1.5 | Reliability design | Supports 1+1 protection of main control, clock and power) |  |
| 1.1.6 | Protection Switching | Automatic |  |
| 1.1.7 | Transmission module | Laser |  |
| 1.1.8 | STM-16 transmission | Optical – 2.5 Gbps |  |
| 1.1.9 | STM- 1 transmission | Optical - 155 Mbps |  |
| 1.1.10 | Fast Ethernet interface | Electrical/Optical - 10/100 Mbps |  |
| 1.1.11 | E1 port | 2 Mbps - 75Ω interface |  |
| 1.1.12 | Fibre/Patch Cord Type | SM – Single Mode |  |
| 1.1.13 | Operating wavelength | 1310 and 1550 nm |  |
| 1.1.14 | Transmission media | SFP – LC Type |  |
| 1.1.15 | Operation configuration | Terminal and Add-Drop |  |
| 1.1.16 | Payload support | STM-64 |  |
|  |  | STM-16 |  |
|  |  | STM-1 |  |
|  |  | E3 |  |
|  |  | E1 |  |
|  |  | FE/GE 10/100/1000 |  |
| 1.1.17 | Service telephone | Engineers Order Wire (EOW) |  |

### TECHNICAL SCHEDULE FOR PRIVATE AUTOMATIC BRANCH  EXCHANGE (PABX) EQUIPMENT

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION/QUANTITY | BIDDER’S GUARANTEED VALUES |
| --- | --- | --- | --- |
| 1.1 | PRIVATE AUTOMATIC BRANCH EXCHANGE (PABX) |  |  |
| 1.1.1 | PABX with basic modules, complete with licences for analogue and digital extensions and seamless integration into existing Zesco PABx network. | 01 |  |
| 1.1.2 | Analogue Subscriber Interface channels | 128 |  |
| 1.1.3 | Digital Subscriber (2B+D) Interface channels | 128 |  |
| 1.1.4 | 2Mbps (30B+D) Digital ISDN port | 04 |  |
| 1.1.5 | 2Mbps (30B+D) Digital ISDN cards | 02 |  |
| 1.1.6 | Ethernet Interface | 02 |  |
| 1.1.7 | 2-Wire Analogue PSTN Trunk lines | 04 |  |
| 1.1.8 | Standard Analogue Telephone sets complete with all accessories and line jacks | 70 |  |
| 1.1.9 | Standard Analogue sets with LCD display for caller line identification (CLI) complete with all accessories and line jacks | 50 |  |
| 1.1.10 | Digital Telephone sets complete with all accessories and power supplies | 42 |  |
| 1.1.11 | IP Telephone sets complete with all accessories and power supplies | 70 |  |
| 1.1.12 | Operator console | 02 |  |
| 1.1.13 | IP Premium user license | 60 |  |
| 1.1.14 | NPRAE E1 card for NCC/Ndola Alcatel crystal hardware PABX for establishing the E1 connectivity with the PABX to be supplied | 01 |  |
| 1.1.15 | Optical to E1 converters with LC interface | 06 |  |
| 1.1.16 | Desktop computer and laptop with suitable specifications for the onsite management of the PABX. | 02 |  |
| 4.1.17 | POTS -to-Ethernet converter with LC interface (45Km reach), 16 ports. | 6 |  |
| 1.2 | PABX SUPPLIMENTARY SERVICES |  |  |
| 1.2.1 | Call logging and accounting software | As stated |  |
| 1.2.2 | Voice mail | As stated |  |
| 1.2.3 | Traffic measurement, recording, and call charge management software | As stated |  |
| 1.2.4 | Maintenance and management software | As stated |  |
| 1.2.5 | H.323 or SIP client PC software (Telephony software) | As stated |  |
| 1.2.6 | Relevant software licenses | As stated |  |
| 1.2.7 | Support for network signalling based on QSIG-ITU protocol | As stated |  |
| 1.2.8 | Budgetary control software or prepayment software | As stated |  |
| 1.2.9 | Intelligent call routing | As stated |  |
| 1.2.10 | Support of standard SIP endpoints | As stated |  |
| 1.2.11 | Voice-centric system | As stated |  |

### TECHNICAL SCHEDULE FOR PULSE CODE MODULATION (PCM) EQUIPMENT

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION |  | BIDDER’S GUARANTEED VALUES |
| --- | --- | --- | --- | --- |
| 1.1 | PULSE CODE MODULATION (PCM) |  |  |  |
| 1.1.1 | Equipment type | PCM |  |  |
| 1.1.2 | Equipment Supply Voltage | -48VDC to -54VDC |  |  |
| 1.1.3 | Transmission rate | 2MB |  |  |
| 1.1.4 | Local/Remote Management | Open for integration, managing and monitoring on the already operational ZTE Network Management System (NMS) |  |  |
| 1.1.5 | Redundancy | 1+1 |  |  |
| 1.1.6 | Transmission rate | 2MB |  |  |
| 1.1.7 | Protection Switching | Automatic |  |  |
| 1.1.8 | Device board quantities | Power board | 4 |  |
|  |  | Control board | 4 |  |
|  |  | 64k data board | 4 |  |
|  |  | FXO, 4 x ports | 4 |  |
|  |  | FXS, 4 x ports | 4 |  |

### TECHNICAL SCHEDULE FOR 48VDC SWITCH MODE POWER SUPPLY CHARGER AND BATTERY

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION | BIDDER’S GUARANTEED VALUES |
| --- | --- | --- | --- |
| 1.1 | 48 VDC POWER SUPPLY CHARGER |  |  |
| 1.1.1 | Type | Switch-Mode power supply, |  |
| 1.1.2 | Input Voltage | 380-400 v, 50 Hz 3-phase A.C. sampling input |  |
| 1.1.3 | Output Voltage | 43V and 58V, |  |
| 1.1.4 | Design | Modular |  |
| 1.1.5 | Short circuit retraction | When current exceeds the rated value. System normalizes after short circuit condition |  |
| 1.1.6 | Local/Remote Management | Open for integration, managing and monitoring on the already operational ZTE Power Management System (PMS) |  |
| 1.1.7 | Stability of Output Voltage | ≤1% for the maximum input Voltage and Frequency, and from 1% and 95% of rated output current; |  |
| 1.1.8 | Maximum deviation of current limitation | ±2% of rated current |  |
| 1.1.9 | Ripple of output voltage | Without Battery: Less than 4% peak-peak of the rated output voltage; With Battery Connected: Less than 1% peak-peak of the rated output voltage. |  |
| 1.1.10 | Instruments | Circuit breakers and protection on AC and DC side; One Voltmeter for DC Voltage; One Ammeter for DC Current; One Lamp indicating the charger is charging; Alarms for “High Voltage”, “Low Voltage”, “Earth Fault” and “Charger Fail” (due to ac failure). |  |
| 1.1.11 | Input over-voltage protection | Yes |  |
| 1.1.12 | Input under-voltage protection | Yes |  |
| 1.1.13 | Overheat protection | Yes |  |
| 1.1.14 | Fan Fault Alarm | Yes |  |
| 1.1.15 | Operation panel & LCD display | Yes |  |
| 1.1.16 | Safety | In accordance with IEC 61204-7 recommendations or better |  |
| 1.2 | 48 VDC BATTERY |  |  |
| 1.2.1 | Type | Lithium |  |
| 1.2.2 | Local/Remote Management | Open for integration, managing and monitoring on the already operational ZTE Power Management System (PMS) |  |
| 1.2.3 | Discharge rate | Shall operate (bidder to submit) |  |
| 1.2.4 | Cell rating | 48VDC, 100Ah |  |
| 1.2.5 | Duty Cycle | Deep discharge (bidder to submit) |  |
| 1.2.6 | Capacity at 10 hours discharge | ≥1200 Ah |  |
| 1.2.7 | Minimum number of cells | 12 |  |
| 1.2.8 | Maximum dimensions of each cell (L x W x H) mm3 | Bidder to submit |  |
| 1.2.9 | Nominal system voltage | 42 Volts |  |
| 1.2.10 | Permissible maximum load voltage | 105% of nominal voltage |  |
| 1.2.11 | Permissible minimum load voltage | 95% of nominal voltage |  |
| 1.2.12 | Permissible maximum load current | Bidder to submit |  |
| 1.2.13 | Rated load current | Bidder to submit |  |
| 1.2.14 | Type of DC system earthing | Solid (copper) |  |
| 1.2.15 | Ambient temperature of operation | -50C to +40 0C |  |
| 1.2.16 | Altitude | 1400 meters above sea level |  |
| 1.2.17 | Humidity | 85% |  |
| 1.2.18 | Operating location | Indoor |  |
| 1.2.19 | Previous type test/certificate | Bidder to submit |  |
| 1.2.20 | Dimensioned outline drawings | Bidder to submit |  |
| 1.2.21 | Installation, operation and maintenance instructions and manuals | Bidder to submit |  |
| 1.2.22 | Quality assurance certificates | Bidder to submit |  |

### TECHNICAL SCHEDULE FOR OPTICAL TIME-DOMAIN REFLECTOMETER (OTDR)

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION | BIDDER’S GUARANTEED VALUES |
| --- | --- | --- | --- |
| 1.1 | OPTICAL TIME-DOMAIN REFLECTOMETER (OTDR) |  |  |
| 1.1.1 | Dimensions | 270 (W) × 165 (H) × 61 (D) mm |  |
| 1.1.2 | Mass (without protection) | Without battery 1.6 kg, 1.9 kg including battery |  |
| 1.1.3 | Mass (with protection) | 2.6 kg including battery |  |
| 1.1.4 | Display | 8-inch touch screen TFT-Colour LCD |  |
| 1.1.5 | Interface | USB 1.1, Type A × 1 (memory), Type B × 1 (USB mass storage) |  |
| 1.1.6 | Data Storage | Internal memory: Not less than1 GB (50,000 traces), External memory (USB): up to 32 GB |  |
| 1.1.7 | Power Supply | 12 V(dc), 100 V(ac) to 240 V(ac), Allowable input voltage range: 90 V to 264 V, 50 Hz/60 Hz |  |
| 1.1.8 | Battery | Type: Lithium-ion Operating Time: 12 hours, Telcordia GR-196-CORE Recharge Time: <5 hours (power off) |  |
| 1.1.9 | Power Saving Functions | Backlight off: Disable/1 to 99 minutes Auto shutdown: Disable/1 to 99 minutes |  |
| 1.1.10 | Power Consumption | 20W max (recharging), 4W standard (low backlight, sweep stopped) |  |
| 1.1.11 | Vertical Scale | 0.13, 0.33, 0.65, 1.3, 3.25, 6.5, 13 dB/div |  |
| 1.1.12 | IOR Setting | 1.300000 to 1.699999 (0.000001 steps) |  |
| 1.1.13 | Units | km, m, kft, ft, mi |  |
| 1.1.14 | Languages | User selectable (English a must) |  |
| 1.1.15 | Sampling Points∗2 | Normal: 5001, High density: 20001 or 25001, Very high density: 100,001 or 150,001 |  |
| 1.1.16 | Sampling Resolution | 0.05m to 60m |  |
| 1.1.17 | Reflectance Accuracy | Single mode: ±2 dB, multimode: ±4 dB |  |
| 1.1.18 | Distance Accuracy | 14- 15- ±1 m ±3 × measurement distance × 10–5 ± marker resolution (excluding IOR uncertainty) |  |
| 1.1.19 | Distance Range | Single mode: 0.5 to 300 km Multimode: 0.5 to 100 km |  |
| 1.1.20 | Testing Modes | 1-Fibre Visualizer: Provides end/break location, end to end loss, fibre length, easy graphical summary, PDF report, PDF viewer 2-Standard OTDR: User selectable automatic or manual set-up 3-Construction OTDR: Automated, multi-wavelength testing 4-Light source: Stabilized Light source (CW, 270 Hz, 1 kHz, 2 kHz output) 5-Loss test set: Power meter and Light source 6- Connector Video Inspection Probe 7-Visual fault locator (optional): Visible red light for fibre identification and troubleshooting |  |
| 1.1.21 | Fibre Event Analysis | A- Auto or manual operation, displayed in table format B- User defined PASS/FAIL thresholds: - Reflective and non-reflective events: 0.01 to 9.99 dB (0.01 dB steps) - Reflectance: –70.0 to –20.0 dB (0.1 dB steps) - Fibre end/break: 1 to 99 dB (1 dB steps) C- Number of detected events: up to 99 D -Macro bend detection |  |
| 1.1.22 | OTDR Trace Format | Telcordia universal. SOR, issue 2 (SR-4731) |  |
| 1.1.23 | Other Functions |  |  |
| 1.1.24 | Real time sweep∗3 | 0.15 sec |  |
| 1.1.25 | Loss modes | 2-point loss, dB/km, 2-point LSA, splice loss, ORL |  |
| 1.1.26 | Averaging modes | Timed (1 to 3600 sec.) |  |
| 1.1.27 | Live fibre detect | Verifies presence of communication light in optical Fibre |  |
| 1.1.28 | Connection check | Automatic check of OTDR to FUT connection quality |  |
| 1.1.29 | Connectivity | Bluetooth, Wi-Fi and Ethernet |  |
| 1.1.30 | Environmental Conditions |  |  |
| 1.1.31 | Operating temperature and humidity | –10° to +50°C, <80% (non-condensing) |  |
| 1.1.32 | Storage temperature and humidity | –20° to +60°C, <80% (non-condensing) |  |
| 1.1.33 | Vibration | Conforming to MIL-T-28800E Class 3 |  |
| 1.1.34 | Dust proof | MIL-T-28800E (Dust Exposure) Class 2 |  |
| 1.1.35 | Drip proof | IP51 (IEC 60529), JIS C 0920 TYPE I |  |
| 1.1.36 | CE | EMC: EN61326-1, EN61000-3-2 LVD: EN61010-1 RoHS: EN50581 |  |

### TECHNICAL SCHEDULE FOR OPTICAL FIBRE FUSION SPLICING (OPTIC JOINING) MACHINE

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION | BIDDER’S GUARANTEED VALUES |
| --- | --- | --- | --- |
| 1.1 | OPTICAL FIBRE FUSION SPLICING (OPTIC FIBRE JOINING) MACHINE |  |  |
| 1.1.1 | Fibre alignment mode | Active core alignment |  |
| 1.1.2 | Applicable fibre - Fibre type | Single mode |  |
|  |  | Multi-mode |  |
| 1.1.3 | Applicable coating – sheath clamp | Coating diameter: 3000µm |  |
|  |  | Cleave length: 5mm – 16mm |  |
| 1.1.4 | Fibre splice performance – splice loss | ITU-T G.652: avg. 0.02 dB |  |
|  |  | ITU-T G.651: avg. 0.01 dB |  |
|  |  | ITU-T G.653: avg. 0.04 dB |  |
|  |  | ITU-T G.655: avg. 0.04 dB |  |
|  |  | ITU-T G.657: avg. 0.02 dB |  |
| 1.1.5 | Fibre splice performance – Splice time | SM FAST mode: avg. 7 – 9 sec |  |
|  |  | AUTO mode: avg. 14 – 16 sec |  |
| 1.1.6 | Sleeve type | Heat shrinkable sleeve |  |
|  | Sleeve length | Max. 66 mm |  |
|  | Sleeve diameter | Max. 6.0 mm before shrinking |  |
| 1.1.7 | Sleeve heat performance – Heat time | 60mm slim mode: avg. 9 -10sec |  |
|  |  | 60mm mode: avg. 13 – 15 sec |  |
| 1.1.8 | Fibre tensile test force | Approximately 2.0 N |  |
| 1.1.9 | Electrode life | 5000+ |  |
| 1.1.10 | Dimensions (W x D x H) | Within (170 x 173 x 150) mm |  |
| 1.1.11 | Weight | Within 2.8 kg (with battery) |  |
| 1.1.12 | Environmental Conditions - Temperature | Operate: -10°C - +50°C |  |
|  |  | Storage: -40°C - +80°C |  |
|  | Environmental Conditions - Humidity | Operate: 0% - 95% RH non-condensing |  |
|  |  | Storage: 0% - 95% RH non-condensing |  |
| 1.1.13 | AC adaptor - Input | AC 100 to 240V, 50/60Hz max. 1.5 A |  |
| 1.1.14 | Battery type | Rechargeable lithium-ion |  |
|  | Battery output | Approx. DC 14.4V/6,380 mAh |  |
|  | Battery capacity | Approx. 300 splice & heat cycles |  |
|  | Battery Temperature | Recharge: 0°C - 40°C |  |
|  |  | Storage: -20°C - +30°C |  |
|  | Battery life | Approx. 500 recharge cycles |  |
| 1.1.15 | Display - LC monitor | TFT 5 inches with touch screen |  |
|  | Display - Magnification | 200 to 300x |  |
| 1.1.16 | Illumination – V-grooves | LED lamp |  |
| 1.1.17 | Interface - PC | USB2.0 Mini B type |  |
|  | Interface- External LED lamp | USB2.0 A type, approx. DC 5V, 500mA |  |
|  | Interface – Ribbon stripper | Mini DIN 6 pin, DC 12V, max. 1A |  |
|  | Interface - Wireless | Bluetooth 4.1 LE |  |
| 1.1.18 | Data storage – Splice mode | 100 splice modes |  |
|  | Data storage – Heat mode | 30 heat modes |  |
|  | Data storage – Splice result | 20000 splices |  |
|  | Data storage – Slice image | 100 images |  |
| 1.1.19 | Screw hole for tripod | ¼ -20UNC |  |
| 1.1.20 | Other features – Automatic functions | Splice mode select by fibre type analysis |  |
|  |  | Discharge power calibration |  |
|  |  | Wind protector: open/close |  |
|  |  | Sheath clamp: open |  |
|  |  | Heater lid: open/close |  |
|  |  | Heater clamp: open/close |  |
|  | Reference guide | Video and PDF file store in splicer |  |
|  | Sheath clamp | Easy sleeve positioning clamp |  |
|  | Electrode | Replaceable without tool |  |
| 1.1.21 | Cleaver/Stripper/Alcohol Dispenser | Set/Lot |  |

### TECHNICAL SCHEDULE FOR FOX615 MULTIPLEXER

| ITEM | FEATURE | ZESCO MINIMUM SPECIFICATION | BIDDER’S GUARANTEED VALUES |
| --- | --- | --- | --- |
| 1.1 | FOX615 MULTIPLEXER EQUIPMENT |  |  |
| 1.1.1 | Equipment type | Multiplexer |  |
| 1.1.2 | Equipment Supply Voltage | -48VDC to -54VDC |  |
| 1.1.3 | Operation Mode | Add - Drop |  |
|  | Transmission Capacity | 2.5G |  |
| 1.1.4 | Local/Remote Management | Open for integration, managing and monitoring on ABB FOX MAN & FOXCST |  |
| 1.1.5 | Reliability design | Supports 1+1 protection of main control, clock, and power) |  |
| 1.1.6 | Protection Switching | Automatic |  |
| 1.1.7 | Transmission module | Laser |  |
| 1.1.8 | STM-16 transmission | Optical – 2.5 Gbps |  |
| 1.1.9 | STM- 1 transmission | Optical - 155 Mbps |  |
| 1.1.10 | Fast Ethernet interface | Electrical/Optical - 10/100 Mbps |  |
| 1.1.11 | E1 port | 2 Mbps - 125Ω interface |  |
| 1.1.12 | Fibre/Patch Cord Type | SM/MM – Single/Multi Mode |  |
| 1.1.13 | Operating wavelength | 1310 and 1550 nm |  |
| 1.1.14 | Transmission media | SFP – LC Type |  |
| 1.1.15 | Operation configuration | Terminal and Add-Drop |  |
| 1.1.16 | Services Supported | Differential Protection |  |
|  |  | Distance Protection |  |
|  |  | Telephony |  |
|  |  | EoS |  |

### SCHEDULE FOR OPTIC FIBRE CABLE

Approach Cable Attributes:

| Item | Attribute | Minimum Requirement | Bidders Specifications |
| --- | --- | --- | --- |
| 1 | Cable Type | ITU-T G.652D |  |
| 2 | Max Cable length | 5000m |  |
| 3 | Cable weight | 240 ± 10 Kg/Km |  |
| 4 | Fibre count (Cores) | 48 |  |
| 5 | Mode | Single Mode |  |
| 6 | Buffer Type | Loose Tube |  |
| 7 | Buffer Material | Polybutylene Terephthalate (PBT) |  |
| 8 | Strength Member | Central Glass Reinforced plastic |  |
| 9 | Tube Filling compound | Thixotropic jelly |  |
| 10 | Flooding Compound | Water blocking jelly |  |
| 11 | Inner Sheath | LLDPE (Linear Low Density Poly-Ethylene) |  |
| 12 | UV Outer Jacket | HDPE (high density polyethylene) |  |
| 13 | Overall Diameter | 17 ± 0.5 mm |  |
| 14 | Tensile Strength | 33 KN |  |
| 15 | Minimum bend radius during installation | 300 mm |  |
| 16 | Cable life span | 30 years |  |
| 17 | Operating temperature | -40 to 70˚C |  |
| 18 | Storage temperature | -50 to 70˚C |  |
| 19 | Installation temperature | -30 to 70˚C |  |

### OPGW Cable Characteristics

Cable Structure

Sub-tube (Fibres)

AS Wire

AA Wire

Sub-tube (Fibres)

AS Wire

AA Wire

| Name | Number | Diameter |
| --- | --- | --- |
| Structure Details |  | 40% AS Wire | 1 | 3.0 mm |
|  | Layer 1 | 40% AS Wire | 5 | 3.0 mm |
|  |  | Sub-tube (Fibres) | 1 (48 fibres inside) | 3.0 mm |
|  | Layer 2 | AA Wire (LHA1) | 12 | mm |

### OPGW Cable Mechanical/Electrical characteristics

| Item | Attribute | Minimum Requirement | Bidders Specifications |
| --- | --- | --- | --- |
| 1 | Standards | IEEE 1138, IEC 60794-4 |  |
| 2 | Stranding Direction of outer layer | Right-hand |  |
| 3 | Fibre Count | 48 |  |
| 4 | Cable outer diameter | 15 mm |  |
| 5 | Supporting Cross Section | 127 mm2 |  |
| 6 | Section of AS wire | 42 mm2 |  |
| 7 | Section of AA wire | 84 mm2 |  |
| 8 | Mass | 450 kg/km |  |
| 9 | Rated Tensile Strength (RTS) | 50 kN |  |
| 10 | Maximum Allowable Tension (40% of RTS) | 159 N/mm2 |  |
| 11 | Everyday Stress (20%RTS) | 79 N/mm2 |  |
| 12 | Strain Margin Stress (70%RTS) | 279 N/mm2 |  |
| 13 | Modulus of Elasticity | 80 GPa |  |
| 14 | Thermal Elongation Coefficient | 19 x 10-6/oC |  |
| 15 | Calculated DC Resistance at 20oC | 0.3 Ω/km |  |
| 16 | Short Circuit Current (1 sec, 40 - 180oC) | 11 kA |  |
| 17 | Short Circuit Current Capacity (40 - 180oC) | 124 kA2.s |  |
| 18 | OPGW minimum bend radius | 300 mm |  |
| 19 | Fibre Strand minimum bend radius | 30 mm |  |
| 20 | Ratio between pull and weight | 11 |  |
| 21 | Installation Temperature | -10 to +50 oC |  |
| 22 | Transportation Temperature | -40 to +80 oC |  |
| 23 | Operation Temperature | -40 to +80 oC |  |

### OPGW/Approach cables Optical Characteristics

| Attribute | Detail | Minimum Required Value | Bidders Specifications |
| --- | --- | --- | --- |
| Mode field diameter | Wavelength | 1310 nm |  |
|  | Range of nominal values | 8.6-9.5 μm |  |
|  | Tolerance | ±0.6 μm |  |
| Cladding diameter | Nominal | 125.0 μm |  |
|  | Tolerance | ±1 μm |  |
| Core concentricity error | Maximum | 0.6 μm |  |
| Cladding non-circularity | Maximum | 1.0% |  |
| Cable cut-off wavelength | Maximum | 1260 nm |  |
| Macro-bend loss | Radius | 30 mm |  |
|  | Number of turns | 100 |  |
|  | Maximum at 1625 nm | 0.1 dB |  |
| Proof stress | Minimum | 0.69 GPa |  |
| Chromatic dispersion coefficient | λ0min | 1300 nm |  |
|  | λ0max | 1324 nm |  |
|  | S0max | 0.1 ps/nm2 × km |  |
| Cable attributes |  |  |  |
| Attenuation coefficient | Maximum from 1310 nm to 1625 nm | 0.4 dB/km |  |
|  | Maximum at 1383 nm ±3 nm | 0.4 dB/km |  |
|  | Maximum at 1550 nm | 0.3 dB/km |  |
| PMD coefficient | M | 20 cables |  |
|  | Q | 0.01% |  |
|  | Maximum PMDQ | 0.20 ps/ km1/2 |  |

NORMATIVE REFERENCE

Optical Characteristics

ITU-T G.652D

IEEE 1138-P1222

Mechanical Characteristics of the Fibre Cores

IEC 793

EIA/TIA 455

Mechanical Characteristics of the Cable

IEEE 1138-P1222

EIA 455

IEC 794

Color Coding

EIA/TIA 598 B

Sub-tube (Fibres)

AS Wire

AA Wire

Sub-tube (Fibres)

AS Wire

AA Wire

PARTICULAR TECHNICAL SPECIFICATIONS: CIVIL WORKS AND STEEL STUCTURE

SECTION VII CONTENT

7 PARTICULAR TECHNICAL SPECIFICATIONS: CIVIL WORKS AND STEEL STRUCTURES	451

7.1 Preamble	451

7.2 General	451

7.2.1 Location of the Works	451

7.2.2 Type of Works	451

7.2.3 Site Visit	453

7.2.4 Drawings	453

7.2.5 Use of Site	453

7.2.6 Plan of Operations and Temporary Works	453

7.2.7 Contractor's Office and Accommodation.	454

7.2.8 Site Office and Laboratory for the Project Manager	454

7.2.9 Maintenance of Office and Laboratory for the Project Manager	454

7.2.10 Survey Instruments and Chainmen	455

7.2.11 Telephone	455

7.2.12 Surface Water Control at Site	455

7.2.13 Liaison with Police and Other Officials	456

7.2.14 Explosives and Blasting	456

7.2.15 Works Executed by the Employer or by Other Contractors	456

7.2.16 Water Supplies for the Works	457

7.2.17 Water Supplies for the Employer	457

7.2.18 Haul and Overhaul	458

7.2.19 Approval of Finished Works	458

7.2.20 Preservation of Trees	458

7.2.21 Survey Beacons	458

7.2.22 Basic Survey and Setting Out	459

7.3 Earthworks	459

7.3.1 Bush Clearing	459

7.3.2 Removal of Topsoil	459

7.3.3 Road Bed Preparation	459

7.3.4 Classification of Materials	460

7.3.5 Order of Work	460

7.3.6 Fill Material	461

7.3.7 Spoil Material	461

7.3.8 Expansive Material	461

7.3.9 Surplus Material	461

7.3.10 Formation, Sub-grade and Pavement	461

7.3.11 Side Drains	462

7.3.12 Excavation in "Rock"	462

7.3.13 Setting Out and Preparation for Earthworks	463

7.3.14 Construction of Earthworks to Formation	463

7.3.15 Unsuitable Material Information	464

7.3.16 Spreading and Compaction of Embankment and Fills	464

7.3.17 Ant Hills	465

7.3.18 Drainage of Works	465

7.3.19 Sub-grade Layer	465

7.3.20 Tolerances	466

7.3.21 Protection of Embankment Slopes	466

7.3.22 Grassing of Slopes	466

7.3.23 Borrow Pits	467

7.3.24 Soil Sterilisation	467

7.4 Materials for the Works	467

7.4.1 General	467

7.4.2 Concrete Pipes	468

7.4.3 Porous Concrete Pipes	468

7.4.4 Cast Iron Manhole Covers and Gratings	468

7.4.5 Filter Backfill for Sub-soil Drains.	468

7.4.6 Stone for Pitching	468

7.4.7 Clay and Cement Bricks	469

7.4.8 Stone for Platform Surfacing	469

7.4.9 Gravel Sub-base Material	469

7.4.10 Crushed Stone Base Course	469

7.4.11 Precast Concrete Kerbs	470

7.4.12 Surface Dressing Chipping for Roads	471

7.4.13 Bitumen and Tars	471

7.5 Drainage and Storm Water	472

7.5.1 Setting Out of Sub-soil and Storm Water Trenches	472

7.5.2 Excavation and Backfilling of Sub-soil Drains	472

7.5.3 Excavation and Backfilling of Piped Storm Water Drains	472

7.5.4 Other Services	473

7.5.5 Explosives and Blasting	473

7.5.6 Classification of Excavation	473

7.5.7 Pipe Culverts	474

7.5.8 Stone Pitching	475

7.5.9 Outlet and Other Drainage Works	475

7.5.10 Control Building and Other Buildings	476

7.6 Road Pavements and Surfacing	476

7.6.1 Preparations	476

7.6.2 Alignment and Level Control	476

7.6.3 Thickness and Surface Tolerances	477

7.6.4 Gravel Pits	477

7.6.5 Sub-base and Wearing Course	478

7.6.6 Base Course	478

7.6.7 Laying and Compacting Pavement Layers	478

7.6.8 Joints Between New and Previous Work	479

7.6.9 Heating of Bitumen	479

7.6.10 Construction Limitation	480

7.6.11 Preparation of Surface for Prime Coat	480

7.6.12 Spraying of Prime Coat	481

7.6.13 Curing of Prime Coat	482

7.6.14 Binders for Surface Dressing	482

7.6.15 Chippings	482

7.6.16 Preparation for Surface Dressing	483

7.6.17 Surface Dressing	483

7.6.18 Control of Traffic and Sweeping	484

7.6.19 Kerb Stone	485

7.6.20 Surfacing of Platforms	485

7.7 Fencing	485

7.7.1 Fencing	485

7.7.2 Dimensions	486

7.7.3 Materials	487

7.7.4 Installation	487

7.8 Concrete and Building Works	488

7.8.1 General	488

7.8.2 Earthworks	489

7.8.3 Concrete, Formwork and Reinforcement	491

7.8.4 Brickwork Specifications	497

7.8.5 Plaster and Floor Coverings	499

7.8.6 Carpentry and Joinery	502

7.8.7 Glazing and Painting	503

7.8.8 Steelwork for Buildings	506

7.8.9 Roofing, Moisture Protection and Water Proofing	509

7.8.10 Doors, Windows, and Louvres	513

7.8.11 Ironmongery and Hardware	515

7.8.12 Plumbing	517

7.8.13 Mechanical Services	523

7.8.14 Electrical Services	524

7.9 Specific Structures	529

7.9.1 General	529

7.9.2 Substation Area	529

7.10 Furnishing	531

7.10.1 General	531

7.10.2 Control Room Furnishing	531

7.10.3 Guard House Furnishing	531

7.11 Schedules for Civil Works	532

7.11.1 SCHEDULE 1.11.1	532

7.11.2 SCHEDULE 1.11.2	533

7.11.3 SCHEDULE 1.11.3	534

7.11.4 SCHEDULE 1.11.4	536

7.11.5 SCHEDULE 1.11.5	537

7.11.6 SCHEDULE 1.11.6	538

7.11.7 SCHEDULE 1.11.7	539

# PARTICULAR TECHNICAL SPECIFICATIONS: CIVIL WORKS AND STEEL STRUCTURES

## Preamble

The Civil Works Specification covers the substation civil works, which form part of the supply by the substation Contractor. The specification including schedules (except Bill of Quantities) for civil works are made as a separate chapter for practical reasons in case the substation Contractor wishes to sub-contract these works. The specifications are primarily valid for new and existing substation works.

## General

### Location of the Works

The locations of the sites are as described under the relevant clauses in scope of works.

### Type of Works

The civil works to be constructed include the following:

- The contractor shall construct at Kitwe, Kalulushi, Chambishi, Chingola, Chililabombwe and Mufulira substation platforms, access roads, cable tranches and relevant foundations and gantry structures as described in the scope of works and supply.

- The contractor shall construct at new substation a control building at Kitwe, Kalulushi, Chambishi, Chingola, Chililabombwe and Mufulira substations. Each control building shall comprise a Control room, AC/DC room, Battery room, Three (03) offices, Communication room, Storeroom, two toilets, two bathrooms and a kitchen. As a requirement, the building will have a roof concrete slab which will be covered by a double pitched false roof in IT4 sheets, 1.5 hours fire resistant ceiling type. Cable trenches in the control building shall be covered by ribbed/checkered plates, windows shall be dressed in burglar bars, floor finishes in ceramic tiles, and wall finishes in “Plascon, Home Pride Type” paint, all to be approved by the Project Manager. The contractor shall also construct two high cost and four medium cost houses. The designs are as attached.

- The contractor shall carry out Earthworks to platform formation level of    substation platform which will be raised to not more than 1m, and to be compacted as per relevant clauses in the scope of works.

- The contractor shall provide both platform subsoil and surface stormwater drainage, including spoon drains and gully traps for substation area and any adjacent building and roads.

- The contractor shall also supply and fix a wire fence and two gates   all-round the substation as required in the relevant clauses specified herein,

- The contractor shall construct a guard house, complete with a toilet, septic tank, soak away and sewer network at the entrance to the substations.

- The contractor shall construct in Chingola (at the site to be approved by the Project Manager), two medium-cost houses

- The contractor shall site and drill one (01) borehole complete with wiring, controls and pumps fittings, pipes, 10,000litres tanks and tank stands, one at each substation location. The boreholes shall be tested as specified in clause 1.2.17 of these specifications.

- The contractor shall construct an access road covering not more than 2.5km to and within the substation area in bitumen standard finish as per specifications in the scope of works. This access road shall connect the substation to nearby main trunk road.

- The contractor shall carry out landscaping works and plant approved type grass between the wire fence and boundary wall, including re-vegetating all surrounding areas outside the substation where vegetative matter was disturbed during works.

- The contractor shall carry out any other works necessary for full completeness to the specified standard and to the satisfaction of and approval by the Project Manager.

### Site Visit

The Contractor (or Bidder) shall visit the substation sites to evaluate ground conditions prior to submission of Bid. The bidder is advised to evaluate the existence of anthills, trees and shrubs, nature of soil and terrain, accessibility to site, and alternative modalities for provision of power supply. Appropriate technical solutions and other costs shall be included in the prices for civil works.

The Contractor must complete all the civil works in time to provide a clean and complete site for the mechanical and electrical erection works.

The Contractor shall supply and stockpile on site, as soon as possible after commencement of the Contract, for later use, all materials necessary for the works.  The requirement also applies to the crush stone for the 150 mm platform finishing layer which will be laid after the mechanical and electrical erection has been completed.

### Drawings

The drawings issued with these documents are for tendering purposes only.  Drawings for this project shall be made by the Contractor or his consultant and be to the approval of the Project Manager.

### Use of Site

The Contractor will restrict his activities to within the Sites.  Access for others to work on the site concurrently with the civil works shall be maintained as far as possible.  Where it is necessary for persons on foot or in vehicles, including other Contractors, to cross the site whilst work is in progress, the Contractor shall provide warning signs on either side of the Work and flagmen if necessary to guide such persons safely across the Site.  The cost of maintaining access for others and assisting the passage of others across the Site shall be deemed to be covered by and included in the rates entered by the Contractor in the Bill of Quantities.

### Plan of Operations and Temporary Works

The Contractor shall before commence work on Site, submit to the Project Manager a fully detailed programme showing the order of procedure and method by which he proposes to carry out the construction and completion of the Civil Engineering Works, and particulars of the organisation and staff proposed to direct and administer the performance of the Works.

The information to be supplied to the Project Manager shall include drawings showing the general arrangements of his temporary offices, camps, storage sheds, buildings and access roads, and details of constructional plant and temporary works proposed.

### Contractor's Office and Accommodation.

Adjacent to the site space will be allocated for the Contractor's offices, accommodation, storage, and workshops.  The Contractor may fence this area for his own security for the duration of the Contract, but any such fence erected together with all buildings, plant and materials shall be removed, all holes filled in and the site left in a tidy and level condition upon completion of the Contract.

### Site Office and Laboratory for the Project Manager

The site office and laboratory for the Project/site Manager shall be a 2-roomed building 6 m long and 4 m wide constructed with timber outer walls and shall be provided with the following furniture:

- 2 No. 4 drawer tables

- 5 No. chairs

- 1 No. 2 drawer lockable steel/timber cabinet

- 1 No. Concrete work bench 3m x 0.9m

- 1 Sink with a cold-water supply

The buildings and the furniture shall remain the property of the Contractor who shall remove and tidy up the Sites after completion of the Contract.  However, the Project Manager shall also be allowed to use these facilities for the duration of the building, erection, and commissioning of electrical works.

### Maintenance of Office and Laboratory for the Project Manager

The Contractor shall keep all of the buildings provided by him in a satisfactory and fully habitable condition, and he shall maintain and repair all services and all furniture and equipment.  He shall provide for collection of refuse, and he shall pay all charges in connection with the provision of lights and water.

The Contractor shall insure the offices and laboratories together with all of the contents therein, whether or not provided by the Contractor, against loss or damage by accident, fire or theft for the duration of the Contract.

This Clause shall also apply for the duration of the erection of electrical works.

### Survey Instruments and Chainmen

The Contractor shall make available for use by the Project Manager throughout the duration of the Civil Works the following survey equipment in first class condition:

- 1 No. level plus tripod

- 2 No. 30m steel band and refill

- 2 No. tape repair kit

- 2 No. 3m tape with locking device

- 2 No. metric staff with level bubble

The equipment shall be used by the Project Manager only on the actual substation site. In addition, the Contractor will provide all necessary skilled labour, poles, pegs, templates, profiles, and all other requisites for checking the setting out and for measurement of the works. The equipment will remain the property of the Contractor and he shall maintain the equipment in first class order and carry out such repairs as are necessary. The cost of providing the survey equipment and attendance upon the Project Manager shall be included in the rates.

### Telephone

The Contractor shall arrange for the installation of a telephone in the offices and shall allow the Project Manager free use of this telephone to communicate for professional reasons within Zambia and manufacturers’ locations.  A radio link shall be substituted if a telephone cannot be arranged.

### Surface Water Control at Site

The Contractor shall keep the whole of the Works free from water and he will be deemed to have included in his rates in the Bill of Quantities for all pumping, shoring, temporary drains, sumps and other measures and provisions necessary for such purposes and for clearing away and making good to the satisfaction of the Project Manager damage caused thereby.

The Contractor shall keep all existing drainage channels clear and shall not obstruct the passage of water to or way from any such drainage channels.

### Liaison with Police and Other Officials

Contractor shall keep in close contact with the Police and other officials of the area concerned regarding their requirements in the control of workmen, movement of traffic, or other matter and shall provide all assistance and facilities which may be required by such officials in the execution of their duties.

### Explosives and Blasting

The Contractor shall use explosives for blasting in connection with the work only at such times and places and in such a manner as the Project Manager may approve, but such approval shall not relieve the Contractor from his responsibility for injury, loss, inconvenience and annoyance to persons, the Work and adjoining structures, roads, places and things and injury or damage to animals and property consequent on the use of such explosives.  The Contractor shall be entirely liable for any accident which shall occur and shall save the Employer and the Project Manager harmless and indemnified from all claims arising from such use of explosives.

The Contractor shall keep in his office at the Site copies of Laws applying to the transport, storage and use of explosives and shall also submit to the Project Manager a copy of any instructions or notices which the Contractor may issue to his staff or workmen or post about the site in compliance with such Laws.

The Contractor shall submit to the Project Manager details of the explosives which he proposes to use and of his proposals for the transport and storage of explosives.

### Works Executed by the Employer or by Other Contractors

The Employer reserves the right to execute on the site, works not included under this Contract and to employ for this purpose either his own employees or other contractors.

The Contractor shall ensure that neither his own operations nor trespass by his own employees shall interfere with the operations of the Employer or his contractors employed on such works and the same obligations shall be imposed on the Employer or his contractors in respect of work being executed under the Contract.

The Contractor shall provide unhindered access to all parts of the site to the Employer, authorised representatives of the Project Manager and of public bodies and corporations, and to contractors employed by the Employer, and he shall make available to such authorised persons the use of all temporary access tracks in or about the site.

Where works are being carried out concurrently in one area careful co-ordination of operations will be required so that interference can be minimised.  The Project Manager shall have the power to regulate and rearrange the order of execution of the Works under this Contract to achieve the best co-ordination practicable.  The Contractor's programme shall take into consideration all information on co-ordination available at the time of its preparation and it shall be flexible enough to allow for subsequent changes that may become necessary.  The rates tendered for the Works shall include the costs of complying with the requirements of this Clause.

### Water Supplies for the Works

The Contractor shall make his own arrangements for the supply of portable water for his staff on site and water for the Works.

The Contractor must make all arrangements including the supply of pumps and motors, labour and the like to abstract water and must pay royalty to the owners.  These costs shall be included in the rates.

If the Contractor fails to obtain permission to utilise existing water sources, he may have to drill boreholes near the sites at suitable locations.

The Contractor shall obtain the Project Manager prior approval before utilising any water source for the Works.

### Water Supplies for the Employer

If there is no already existing water supply, a borehole shall be provided to ensure water supply to the sub-station when in operation, unless connection to public water works is more economical.

The Contractor shall arrange for the drilling of a borehole at the sub-station location and the work shall include siting, drilling, lining and test pumping for 72 hours continuously.  The borehole shall be equipped with a 10 000-litre water tank on a 6 m, or higher, if necessary, stand, an electrically operated submersible pump including wiring, controls and fittings and all pipe works.

If possible, the borehole should be drilled and tested in the early stages of the Contract so that they may provide water for construction, if the supply is adequate.  In which case the Contractor should provide his own temporary pumping arrangements as required and replace them on completion with the permanent submersible pump.

See also under “Plumbing” in this Specification.

### Haul and Overhaul

Haul and overhaul from sources of stone, gravel, water and all other materials shall be included in the prices for Civil Works in the Bill of Quantities.

### Approval of Finished Works

The Contractor shall obtain the approval of the Project Manager for each section and each stage of construction.  Approval of any section of any stage will not be given, and the Contractor shall not proceed with any subsequent stage, until all tests required by the Project Manager have been carried out, and the results have shown that the section complies with the Specification.  Any works rejected by the Project Manager as not complying with the Specification shall be replaced by the Contractor at his own expense.

### Preservation of Trees

No tree shall be removed without prior permission of the Project Manager who will limit the removal of trees to the minimum necessary to accommodate the permanent Works.

### Survey Beacons

During the progress of the Works, the Contractor shall not remove, damage, alter or destroy in any way any beacons or survey beacons. Should the Contractor consider that any survey beacon will be interfered with by the Works, he will notify the Project Manager, who, if he considers necessary, will plan for the removal and replacement of the beacon.

If the Contractor removes or disturbs a beacon without the prior permission of the Project Manager, he shall be liable for the full cost of its replacement together with the full cost of re-establishing the data relevant to it.

### Basic Survey and Setting Out

The sites will be surveyed in detail by the Contractor, and the exact locations shall be agreed with the Project Manager.

The details of beacons and benchmarks shall be provided in the site survey drawings.

The Works shall be located on the drawings and the Contractor shall appoint a suitably qualified Surveyor to set out the Works from the beacons and shall plot cross sections at 20 m intervals and submit to the Project Manager for approval.

No separate payment will be made for any work in connection with the setting out of the Works, nor any other Works required by the Contractor to ensure the accurate location and construction of the Works.

## Earthworks

### Bush Clearing

The areas of the platform, access road, and borrow pit shall be cleared of all trees, vegetation, and roots.  These shall be neatly stockpiled within 300 m of the site at locations agreed with the Project Manager and shall remain the property of the landowner.

### Removal of Topsoil

The topsoil, if any, within the areas of platform and access road shall be stripped to an approximate depth of 200 mm and stockpiled at locations agreed with the Project Manager for later use on embankment slopes.

Overburden in the borrow pit shall also be stripped to a depth specified by the Project Manager and stockpiled for later use in rehabilitation.

### Road Bed Preparation

The 'road bed' is that part of the ground uncovered by clearing the site, completion of cuts, excavation and removal of unsuitable material as required, on which the platform and road structure rest.  The road bed must be scarified to a depth of 150 mm, water added as considered necessary, and compacted with a minimum of four (4) passes of a 50 tonne single axle pneumatic super compactor.  If the road bed is rock no preparation is necessary.

### Classification of Materials

Materials excavated and either placed in the Works for the formation of the platform and roads, or carted to spoil will be categorised as follows:

Rock: "Rock" shall include all material which requires blasting for its removal or cannot be extracted by ripping with a single tine heavy duty ripper of at least 5 tonne mass towed by a crawler tractor in good condition with a net available flywheel power rating of not less than one hundred and thirty-five kW continuous according to BS 649 and with a minimum bare tractor mass of 15 tonne. Individual boulders greater than 0.2 m3 in volume shall be included in this class when their nature and size are such that they cannot be removed without recourse to blasting.

Hard Material: "Hard Material" or "Decomposed Rock" shall include all material such as consolidated gravels, decomposed or stratified rock, stones or boulders less than 0.2 m3 in volume which cannot be classified as "Rock" but which requires additional processing, such as ripping or breaking down by compressor tools before normal loading processes may be employed.

Common: “Common” Material shall be all material not defined as Rock or Hard Rock.

### Order of Work

The construction of cuttings, side drains and embankments shall proceed in a methodical and orderly manner.  It shall be solely the Contractor's responsibility to arrange his methods and programme of work to ensure that the earthworks are carried out by the most efficient and economical method possible with the type of plant employed on the Works.

All trimming of cuttings, and embankments, drains and shoulders to the specified slopes and shapes, shall be carried out concurrently with the earthworks that are being carried out at that particular site and level.

### Fill Material

"Fill-material" shall mean material deposited in accordance with these specifications from any of the classes specified to build up an earthworks construction to formation level as shown on the approved drawings or as ordered by the Project Manager.  The CBR of fill for the platforms shall not be less than 5% at 91% Mod AASHTO density (4 day-soaked test) and for road sub-grade, 9%.  The Contractor shall obtain the fill material from a source approved by the Project Manager.

### Spoil Material

"Spoil-material" shall mean material excavated in accordance with these specifications from any of the classes specified, and which, being obtained from the excavation of side drains, cuttings or below the road, embankment is unsuitable for the requirements of the Works.  Spoil material shall be removed from the Site to a spoil tip which should be within 300 m of the boundary of the site in a neat and tidy manner and shall be approved by the Project Manager.

### Expansive Material

When expansive material (black cotton, etc.) is encountered, it shall be removed to a depth 600 mm below the formation or the existing ground level, whichever is greater.  Material removed shall be stockpiled for later use in slope protection or spoiled to a tip as instructed by the Project Manager.

### Surplus Material

"Surplus-material" shall mean material excavated in accordance with these specifications from any of the classes specified and which is temporarily surplus to the fill requirements and shall be carted to a designated stockpile for re-use later elsewhere in the Works, or to an approved spoil tip.

### Formation, Sub-grade and Pavement

The "Formation" shall be the top surface of the earthworks in its final shape after completion.

The "Subgrade" of the road and platform shall be the top 150 mm of the fill in embankment, or of the existing ground in cut, lying immediately below the "Formation".

The "Pavement" shall be the whole construction in the road or paved areas made to support the traffic above the subgrade, comprising surfacing and base layers.

### Side Drains

Where side drains are required they shall be shaped by excavating the lines, slopes and widths shown on the approved drawings and finished off so that the formation levels and camber or super-elevation of the formation, level and crossfall of the shoulders, and shape and invert levels of the side drains are everywhere in accordance with the approved drawings.

Any excess depth or width excavated from the side drains shall be backfilled and made good to the satisfaction of the Project Manager at the Contractor's expense.

All other types of drains are specified separately in this Specification.

### Excavation in "Rock"

Excavation Level

Unless otherwise directed, the formation of the platform can be founded on rock.  However, for roads, rock shall be excavated to an average level 150 mm below the formation and in no place less than 100 mm below the formation.

Backfilling for Surfaces

Any excess excavation in rock below the formation shall be backfilled and compacted as for embankment and fills, see below.  Excess excavation in the invert of drains shall not be backfilled, but the rock surfaces shall be trimmed, and all loose particles removed, to allow free drainage of water.

Excess Excavation of Slopes

Where side slopes are over-excavated no backfilling will be required but the slopes shall be trimmed to a neat shape and safe angle as is acceptable to the Project Manager.  The sloping sides of all cuttings shall be cleared of all rock fragments which move when prised with a crowbar.

Hard Material

The provisions of this Clause do not apply to hard and common materials, which materials shall be excavated to the lines and levels shown on the approved drawings or as instructed, within the permitted tolerances.

### Setting Out and Preparation for Earthworks

The Contractor shall carry out a careful evaluation of costs and timing when deciding on platform formation.  In case of rock at the platform site it must be considered if filling up with borrow materials is a better solution than extensive blasting of rock.  The extent of blasting for foundations, cable trenches and drains must be considered.

The Contractor shall set out the earthworks and the tops of cuttings and toes of embankments at intervals 10m. Reference pegs shall be provided clear of the earthworks and at right angles to the centre lines, from which the centre lines and levels can be re-established at any time.

After road bed preparation, but before the construction of any earthworks in the fills, the levels of the existing ground shall be agreed between the Contractor and the Project Manager.  If the Contractor fails to take the requisite levels, then the ground levels shown on the approved drawings or determined by the Project Manager shall be taken as correct.

### Construction of Earthworks to Formation

All earthworks up to formation shall be formed and completed to the correct lines, slopes, widths, and levels shown on the approved drawings and with the subgrade parallel to and at the correct depth below the profile, camber, crossfall or super-elevation shown for the finished level, unless otherwise directed by the Project Manager.

Embankments and fills shall be constructed only of suitable material obtained from the excavation of cuttings.  If the Contractor encounters material which he considers unsuitable for earthworks, then he shall forthwith inform the Project Manager, who shall instruct the method of use or disposal of such material.  If insufficient material can be obtained from the cuttings, additional material may be borrowed from approved borrow pits.

The Project Manager may direct that certain soils be excluded from certain layers and other soils set apart or obtained from borrow and used only for these layers, in which case the Contractor shall comply with the Project Manager’s directions and shall allow in his rates for such selection of materials.

### Unsuitable Material Information

Where, in the opinion of the Project Manager, unsuitable material occurs in cuttings, the Contractor shall excavate it to the depths and widths directed and replace it with selected fill material to form an improved formation.

### Spreading and Compaction of Embankment and Fills

Embankments and fills shall be compacted in layers not exceeding a compacted thickness of 150 mm, provided that the minimum relative density specified is achieved throughout the layer when compacted.  The contractor shall obtain the Project Manager’s approval of the previous layer before the next layer is spread.  If the Contractor wishes to continue placing fill before density test results are available, he may do so entirely at his own risk and, should tests fail, then the Contractor must remove both the layer being tested and those placed above it, all at his own expense.

Unless otherwise specified, embankments and fills shall be compacted to a minimum relative dry density of 91% Mod AASHTO.

Embankments shall be constructed as far as is reasonable in layers parallel to the formation and to the full width corresponding to the height at which the work is being carried out from time to time.  In no circumstances may a narrow portion of the embankment be constructed first and material "side-tipped" to make up the specified width.

Density tests must be taken on every layer at a frequency of one for every 1000 m² of area.  The specified density is a minimum so the Contractor must aim to achieve a higher density than the minimum specified.

### Ant Hills

Where an anthill occurs within the limits of earthworks, all that portion of the anthill which is up to 2 m below formation level shall be removed.  The cavity formed by the excavation of the anthill shall be poisoned with an approved pesticide and be backfilled with approved material in layers not exceeding 150 mm and compacted as described above.

### Drainage of Works

All cuttings, embankments and borrow pits shall be kept free of standing water and drained during the whole of the construction.

Should water accumulate on any part of the earthworks, either during construction or after construction, until the end of the maintenance period, giving rise to soaking or eroding conditions in the earthworks, the Project Manager may order the Contractor to remove and replace at the Contractor's expense any material which has been so affected.

All drains shall be maintained throughout the Contract in proper working order.

The Contractor must allow in his rates for draining the earthworks satisfactorily at all stages during the construction and arrange his methods and order of working accordingly.

### Sub-grade Layer

The subgrade of roads, in both cuttings and embankments shall be compacted to 93% Mod AASHTO dry density or as otherwise specified.  The subgrade of the Platform shall be compacted to 91% Mod AASHTO dry density.  The maximum compacted thickness which shall be laid processed and compacted at one time shall be 150 mm.  The maximum dimension of any particle in the layer shall not exceed 100 mm.

The layer shall be scarified, and water shall be mixed in, or the material allowed to dry out to the correct moisture content, and the layer shall then be compacted to the specified dry density, or as otherwise directed.  The most suitable moisture content for compaction will be usually in the range of +1/2% to -2% Optimum Moisture Content.

During this process the final surface of the subgrade layer shall be graded to level, parallel to the crossfall or camber and profile shown upon the approved drawings or directed by the Project Manager and to the tolerances specified below.  Density tests must be taken at a frequency of one for every 250 m² of area.

### Tolerances

The following tolerances will be permitted in the finish of the formation to roads and platform:

1. 	The level of the formation should be within +/- 100 mm of that specified.

2.  	On the final trimmed slope of earthworks, a variation of + or - one fifth of the specified slope will be allowed.

3.	The tolerances permitted in the overall width of the bottom of cuttings shall be plus or minus 150 mm in the distance between centre lines and the toe of cuttings slopes, and plus 150 mm in the case of embankments.

### Protection of Embankment Slopes

Any topsoil and expansive material removed from the Works shall be placed on embankment slopes as directed by the Project Manager.  The slopes shall be trimmed to form a gradient not less than 1 on 5 unless otherwise directed.  Slopes in rock without a topsoil cover may be steeper.

### Grassing of Slopes

The surface of embankment slopes, after placing of topsoil, if any, shall be planted with grass sprigs at approximately 250 mm centres.  Unless instructed otherwise by the Project Manager, the type of grass shall be indigenous, low growing or runner grass.  Alternatively, the surface may be turfed.  While planting, the area shall be irrigated for as long as necessary to ensure that the grass is properly established and has completely covered the ground.  Grass should only be planted in the rainy season.

### Borrow Pits

Where it is necessary to borrow material for construction, suitable pits shall be provided by the Contractor to the approval of the Project Manager.

All borrow pits must be carefully cross sectioned before and after excavation to determine the quality of earth excavated.

After removal of material for use, the area must be rehabilitated by the Contractor so that it will not prove a hazard to man or beast or a source of erosion.  The sides of the excavation must first be sloped and then any previously stockpiled topsoil spread as far as possible.

At some borrow pit locations, further cleaning and fencing etc., may be required.

### Soil Sterilisation

To stop the growth of vegetation and incidence of ants, the Contractor shall apply an approved herbicide before any spreading of stone over the platform area. Insecticide to be used around Control Building.

## Materials for the Works

### General

All materials shall comply with the appropriate standard specification unless otherwise required hereinafter.

The Contractor shall before placing any order for materials or manufactured articles for incorporation in the Civil Works, submit for the approval of the Project Manager the names of the firms from whom he proposes to obtain such materials, etc., together with a list of the materials and manufactured articles giving the origin, quality, weight, strength, description, etc., which he proposes that the firms should supply.  No materials or manufactured articles shall be ordered or obtained from any firm of which the Project Manager shall not have previously approved.

All materials shall be delivered to the site a sufficient period before they are required for use in the Works to enable the Project Manager to take such samples as he may wish for testing and approval.  Any materials condemned as unsuitable for Works shall be removed from the Site at the Contractor's expense.

The Contractor may propose alternative materials to those specified, provided that they are of equivalent quality and, subject to the Project Manager’s approval such materials may be used in the Works.

### Concrete Pipes

Precast concrete non-pressure pipes for the culverts and storm water drainage shall comply with CAS A17.  The pipes shall have ogee joints.

### Porous Concrete Pipes

Porous concrete pipes for use in sub soil drains shall comply with CAS A17.

### Cast Iron Manhole Covers and Gratings

Cast iron manhole covers and frames and gratings shall comply with SABS 558 1973 or BS 497 and the duty shall be medium weight 100 kg.

### Filter Backfill for Sub-soil Drains.

This shall be graded crushed stone as for platform surfacing.

### Stone for Pitching

Stone for pitching to drains, inlets and outlets of culverts, to embankments and around structures shall consist of sound un-decomposed rock.

The stone as dressed shall be roughly cubical in shape with minimum dimensions of 150 mm x 150 mm x 150 mm for a nominal thickness of 150 mm pitching or 225 mm x 225 mm x 150 mm for a nominal thickness of 225 mm pitching.

Hard stone boulders may be used for grouted pitching only but in this case the size shall be 225 mm minimum diameter for a nominal thickness of 150 mm pitching and 300 mm diameter for a nominal thickness of 225 mm pitching.

### Clay and Cement Bricks

Clay bricks shall comply with CAS 211 or BS 3921 and cement bricks shall comply with CAS A41 or BS 6073.

### Stone for Platform Surfacing

The stone shall be hard and durable crushed rock with a maximum particle size of 62.5 mm and not more than 15% shall pass a 9.5 mm sieve.

The stone layer to be spread uniformly over the finished surface of the platform shall have a thickness of 100 mm.

### Gravel Sub-base Material

Gravel for the road sub-base layer shall be natural gravel obtained from a proven source and shall comply with the following requirements:

1.	CBR at 95% Mod AASHTO density and after 4-day soak	Min  30

2	Plastic Index							         Max. 12

3.	Plasticity product (If x Ip)					       Max. 200

4.	Maximum particle size (mm)				         Max. 80

### Crushed Stone Base Course

Material for road base to support the bituminous surfacing shall be crushed rock complying with the following requirements:

1.	CBR at 97% Mod AASHTO density and after 4-day soak         Min 80

2.	Plasticity Index 							 Max. 6

3.	Liquid limit								Max. 25

4.	Coarseness Index							50-70

5.	Fineness Index								5-15

In addition, the grading shall be within and approximately parallel to the following envelope:

British Standard			Percent passing

sieve size (mm)			by weight (%)

37.5					100

19.0					80-100

9.5					55-80

4.75					40-64

2.36					30-50

1.18					22-40

0.60					15-30

0.30					10-23

0.150					 8-19

0.075					 5-15

Equivalent road gravel, produced by a recognised Quarry which has been successfully used as Base 1 elsewhere, may be utilised with the approval of the Project Manager.

### Precast Concrete Kerbs

Precast concrete kerbs shall be in accordance with CAS 104 and the dimensions shall be 1 000 mm x 300 mm x 100 mm at the base with a chamfer to 60 mm, over the top 150 mm.

### Surface Dressing Chipping for Roads

1.	General

All chippings shall consist of tough durable crushed stone cubical in shape and free from visible dust and harmful materials such as loam, clay, salt, lime, organic matter and other deletions constituents.

The rock from which the chippings are to be produced shall comply with the following:

Aggregate crushing value:		         Not greater than 22%

Los Angeles Abrasion value:		Not greater than 28%

Sodium Sulphate Soundness test:	Loss on 20 cycles to be not more than 20%

2.	Gradings

Chippings for surface treatment work shall comply with CAS 232 with - "Single Sized Crusher Stone for Roads".  The following nominal sizes of chippings shall be used:

First seal	-	13.2 mm + 6.7 mm

Second seal	-	 6.7 mm + 1.18 mm

### Bitumen and Tars

Before any bitumen, bitumen emulsion or tar is delivered to the site the Contractor shall provide the Project Manager with a certificate from the manufacturer that the material to be supplied complies in all respects with the Specification.

The types of bitumens required will be as follows:

Prime Coat: MC 30 or 70 or RC 30 or 70 cut back bitumen conforming to CAS 145 or T.P. 7 Tar conforming to CAS 105.

Surface Dressing:150/200 Penetration straight run bitumen conforming to CAS 144.

With special approval:60% Cationic rapid setting bitumen emulsion diluted 1:1 with water.

## Drainage and Storm Water

### Setting Out of Sub-soil and Storm Water Trenches

The Contractor shall be responsible for setting out from approved drawings.

Prior to excavating a section of pipeline, sight rails shall be erected at each end and at each change in grade and direction with a maximum distance between profiles of 50 metres.

Site rails and boning rods shall be of substantial construction and shall be painted black and white in such a manner as to indicate clearly the lines and levels to be worked to.

### Excavation and Backfilling of Sub-soil Drains

Drains are to be formed by cutting a trench, lining it with a double thickness of black shade cloth and backfilling with a suitable filter material surrounding a porous concrete pipe.  The drains shall have a minimum of 600 mm depth from platform formation and a gradient of 1 in 100.  The internal diameter of the porous pipes shall be 225 mm and the backfill filter material shall consist of crushed stone, as for platform surfacing.

The stone backfill should be placed around the pipe in the trench and compacted in layers so as to ensure that no settlement will occur later in the section of finished platform directly above the trench.  The discharge ends of all subsoil drains must be carefully protected to avoid blockage and they should be suitably marked.

### Excavation and Backfilling of Piped Storm Water Drains

The piped drains are to be formed by cutting a trench, laying a 300 mm internal diameter concrete pipe and backfilling with a suitable material.  The drains shall have a minimum of 650 mm depth from platform formation and a gradient of 1 in 100.  The backfill material shall have the following grading:

Sieve to BS			Amount Passing

20 mm				100%

10 mm			Not less than 85%

5 mm				Not more than 20%

2.36 mm			Not more than 5%

A 150 mm thick layer of backfill material shall be laid and compacted thoroughly before placing the pipe in the trench.  The material shall also be placed and compacted around the pipe for the full width of the trench and shall extend to a level 150 mm above the top of the pipe and compacted to a density not less than 91% of Mod AASHTO density.  The rest of the trench shall be backfilled to the same standard with approved material from excavation or other works.

### Other Services

Where trenches pass near or across other services, the Contractor shall take every precaution against damaging such services.  These services shall be properly supported in the trench until backfilling is complete and the backfilling shall be thoroughly compacted under and around such services.

### Explosives and Blasting

Blasting to be carried out on sections of the Works shall be restricted to such hours and conditions as prescribed by Zambian laws and regulations.

### Classification of Excavation

In pipe trenches the excavation will be classified as follows:

1.	Excavation in 'rock' is defined as:

a)	un-decomposed rock occurring in bulk or banks or ledges, the practicable excavation of which requires explosives or drilling, wedging, and splitting.

b)	un-decomposed boulders each exceeding 0.20 m3 in volume.

2.	Excavation in 'hard', which will be held to be material other than 'rock', the economically practicable excavation of which necessitates the use of mechanical breakers, or which will reduce the rate of excavation of a back-acting excavator having a power of at least 0.1 kW per millimetre width of bucket to one third or less of that achieved by the same excavator in soft excavation at a similar depth.

Laterite, ironpan and cemented gravels will generally fall into this category.

3.	Excavation in 'common', which will be held to be all other material not falling into the categories of 'rock' or 'hard' and will include all loose, decomposed boulders less than 0.20 m3 in volume.

Excavation costs shall be included in the quoted civil works prices.

### Pipe Culverts

#### Preparation of Foundation

The construction of pipe culverts shall be carried out to the lines and levels shown on approved drawings. In order that the foundation material shall be undisturbed, the last 100 mm depth of excavation shall be carried out by hand.  The excavated surface shall be kept clean and free from standing water.  Before placing the concrete, the surface shall be lightly compacted.

Excavation in rock shall be carried out to the approved levels and dimensions unless otherwise directed by the Project Manager.

#### Forms

The Contractor will be required to form vertical surfaces to the concrete by means of timber forms. Wrot formwork shall be used for the exposed faces and shall be adequately supported to prevent movement during concreting.  Unwrot butt-jointed timber may be used for the unexposed faces.  The top surface of the forms shall be set accurately to the required levels or slopes.

#### Concrete

Grade 20 concrete shall be used throughout for drainage purposes.

### Stone Pitching

Where shown on the approved drawings or were directed by the Project Manager stone pitching shall be used to form apron slabs and banks at culvert inlets and outlets, as lining to drains and slopes.

All areas to be pitched shall first be thoroughly cleaned and compacted to a sufficient extent to ensure that no subsequent settlement shall occur.  At culvert inlets and outlets, the level of the pitching shall be the same as the culvert or apron inverts.

The pitching stones shall be laid with their longest dimensions perpendicular to the slope and shall be rammed into the under-surface until firmly bedded and a uniform surface true to line and grade is obtained.  Pitching stones shall be firmly butted up against adjacent pitching stones.

Where grouted stone pitching is called for, the stone shall be laid as prescribed, the surface thoroughly wetted and the spaces between the stones filled with cement mortar composed of one part of cement to three parts of approved river sand.  The mortar shall be worked into the pitching so as to ensure that all spaces or voids between the stones are completely filled with mortar.  The grouted pitching shall then be cured by keeping it continuously covered with wet sacking, or other approved wet cover, for the period of not less than four days from the time the mortar was applied.

### Outlet and Other Drainage Works

Where directed by the Project Manager, channels shall be excavated as outlets from culverts, to straighten or extend water courses, improve entries to culverts, form cut-off drains, divert water and the like.  These channels shall be excavated to the sizes, shapes, levels and dimensions shown on the approved drawings or directed by the Project Manager.

Material from such excavation shall be carted to spoil or stockpile or used elsewhere in the Works as instructed by the Project Manager.  In some cases, the material shall be deposited adjacent to the sides of the excavation in which case the material shall be deposited in such a manner and location that it will not obstruct the flow of water along the channel or subsequently be washed back into the channel and it shall be trimmed to a neat and tidy shape to the approval of the Project Manager.

Where channels are excavated in erodible soils, the Project Manager may direct that bolsters are constructed to form a cascade.  Concrete Grade 20 shall be used.

Catchpits, kerb inlets and junction boxes shall also be constructed to the sizes, shapes and levels shown in the approved drawings or as instructed by the Project Manager.

### Control Building and Other Buildings

The level of the control building shall be so that rainwater can not enter the building.

Cable trenches inside the building shall be built in such a way that water from outside trenches, drains or rainwater cannot enter into the indoor trenches.

## Road Pavements and Surfacing

### Preparations

Prior to the construction of each pavement layer, the previous shall be thoroughly cleaned of all foreign substances.  Any ruts or soft spots which occur or any deviation from the specified tolerances or degree of compaction shall be corrected by scarifying, removing and/or adding approved material, relaying and re-compacting the unsatisfactory areas to the required density and to the required lines and levels.  Should any damage occur to a pavement layer prior to the construction of the next layer, it shall be rectified to the satisfaction of the Project Manager at the expense of the Contractor.

### Alignment and Level Control

Stakes, boards, and boning rods of substantial construction shall be furnished, set and maintained by the Contractor, in order that the works will conform to the lines and levels shown on the approved drawings.  The stakes shall be set at intervals not exceeding 20 metres in lines parallel with the centre lines and not more than 15 metres apart.  Stakes, boards, and boning rods shall be painted black and white in such a manner as to clearly indicate the lines and levels to be worked to for each layer or pavement.

### Thickness and Surface Tolerances

The thickness of each pavement layer shall be such that the depths from the required finished surface levels of the pavement to the surface of each pavement layer shall nowhere be less than the depths shown on the approved drawings.  The surfaces of each layer other than the final layer may be lower than the required surface within the tolerances stated below, provided that any such deficiency shall be made good at the Contractor's expense by increasing the thickness of the course above the surface in question.

Each layer of pavement shall be finished to a surface profile parallel to the finished surface of the pavement shown on the approved drawings within the level tolerances shown below:

Layer				Variation Permitted

mm		mm

Sub-base			+5		-20

Basecourse			+5		-10

The finished surface of the Basecourse shall be such that when tested with a straight edge 3 metres long placed in any position and direction, there shall not be any gap greater that 10 mm between the bottom of the straight edge and the surface.  In addition to this requirement there shall not be any deflection exceeding 20 mm from a straight line between any tow points 30 m apart.  Neither of these requirements shall apply across road crowns.  These smoothness tolerances apply to straight profiles and equivalent smoothness tolerances shall be applied to vertical curves.

### Gravel Pits

The gravel pits for wearing course and sub-base materials shall be located by the commencement of the Contract.

### Sub-base and Wearing Course

Natural gravel sub-base and wearing course material for internal and access roads respectively shall comply with the requirements specified under “Materials for the Works”, and they must be compacted to achieve, as a minimum, density of 95% of the modified AASHTO density.  The frequency of density tests will be one for every 250 m2 of layer area.

After the completion of Second Stage Works, the gravel wearing course of the access road, shall be re-shaped, replaced of any gravel loss and re-compacted as directed by the Project Manager.

### Base Course

Graded crushed stone for base in internal roads shall comply with the requirements specified under “Materials for the Works” and it must compacted to achieve, as a minimum the density of 97% of the Modified AASHTO density.  The frequency of density tests will be one for every 250 m2 of layer area.

The Contractor shall supply and stockpile at site, the required quantity of crushed stone for later use, as soon as possible after the commencement of the Contract.

### Laying and Compacting Pavement Layers

The pavement material shall be deposited in such quantity and spread in a uniform layer across the full width of the area, so that the final compacted thickness is everywhere not less than shown upon the approved drawings or ordered by the Project Manager.

The uncompacted thickness of the layer shall be such that the thickness after compaction shall not exceed the specified thickness.  The material shall be thoroughly mixed to a uniform consistency and large material shall be broken down so that the grading complies with the Specification.  Large stones or boulders which cannot be broken down to the required size shall be removed to an approved tip.

The spread material shall be brought uniformly to within a range of 90 percent to 110 percent of the Optimum Moisture Content, as previously determined for the material, by sprinkling with water and/or mixing as required.

Compaction shall be carried out by such method and using such plant as the Project Manager may approve until the specified minimum dry density is achieved.  The Project Manager may disapprove any methods of compaction or items of compaction plant which in his opinion are detrimental to the work.

Additional water shall be applied to the materials during compaction in amounts such as are required to maintain the moisture content within the specified limits.  Any base course finished with a surface level above the required surface level shall be planed down to the correct level scarified re-compacted and finished as specified.

If at any time after compaction the base course dries out sufficiently to lose apparent cohesion, or is damaged by rain it shall be scarified, aerated and/or watered, re-compacted and finished as specified above.

The surface of the material shall, on completion of compaction, be well closed, free from movement under the compaction plant and free from compaction planes, ridges, cracks or loose material.  All loose, segregated or otherwise defective areas shall be dug out and made good with new material to the full thickness of the layer and re-compacted all at the Contractor's expense.

### Joints Between New and Previous Work

The forming of construction joints and the protection of previously completed works shall be carried out so as to produce a uniformly compacted and homogenous layer free from ridges or other surface irregularities.

Full width working without longitudinal joints is required.  When forming a transverse joint at least 5 m length of the previously laid work shall be incorporated into the new layer.

### Heating of Bitumen

Bitumen shall be heated such that the temperatures at the time of spraying are within the limits given in the table below in approved boilers or bulk storage containers equipped with adequate pumps and accurate thermometers.

SPRAYING TEMPERATURES

Material							Temperature deg. C

Min		Max.

Straight run bitumen grade 150-200 penetration        165		200

M.C.30, R.C.30						35		 60

M.C.70, R.C.70						60		 85

Bitumen Emulsions						15		 70

No bitumen shall be heated above the maximum temperature recommended by the Supplier and any that is accidentally over-heated shall be removed from the Site and disposed of by the Contractor at his own expense.

No bitumen shall be heated in a boiler for which the thermometer is broken or inaccurate.

### Construction Limitation

No bitumenization will be permitted when the road is wet or when the surface moisture is such as to prevent even coverage by the binder.  Work may not proceed when the temperature is less than 15°C unless specifically approved by the Project Manager.

### Preparation of Surface for Prime Coat

The surface of the layer shall be thoroughly swept, and all loose and foreign material removed.  All loose material shall be swept well clear of the layer to expose the full width of the layer.

The surface of the layer shall be checked for line, camber and level and the surface corrected made good as necessary and approved by the Project Manager before any bitumen prime is added.

Where required by the Project Manager immediately prior to the application of prime the surface of the layer shall be lightly sprayed with water but not saturated.

### Spraying of Prime Coat

1.	General

Immediately the area to be primed has been prepared and approved by the Project Manager the prime shall be sprayed on to it.

2.	Amount and Type of Prime

The amount and type of prime shall be as approved by the Project Manager.

The rate of spray will depend upon the texture and density of the surface but will usually be in the range of 0.75 l/m2 to 1.0 l/m2.  The quantities used must give complete coverage of the surface.

Should the Contractor find that when using the rate of spray approved by the Project Manager the coverage is inadequate or there is run-off he shall immediately inform the Project Manager and amend the spray rates as directed by the latter.

3.	Method of Spraying

The edges of the area shall be marked out with a line of string or wire, pegged down at intervals not exceeding 15 m on straights or 7.5 m on curves.

Bitumen shall be sprayed from a pressure distributor and no hand spraying will be permitted except in small areas when approved by the Project Manager or to make good a defective area left by a blocked nozzle.

The nozzles shall be tested prior to each days’ spraying by discharging on to metal sheets, or into purpose made troughs.  The testing shall not take place on the road and any bitumen spilt on the ground shall be cleaned off.  The metal sheets or troughs shall be cleaned at the end of each day’s work.

When commencing and stopping spraying sheets of building paper or similar approved material at least 2 m wide shall be spread across the full width to be sprayed to give a clean sharp edge.

During spraying all kerbs, road furniture, culvert head-walls, tree boles and the like which are liable to be disfigured by splashing of bitumen shall be protected and any such feature which is accidentally marred by bitumen shall be cleaned off with a suitable solvent or made good at the Contractor's expense.

When, during spraying, a nozzle becomes blocked or develops a defect, the spraying shall be immediately stopped, any area incompletely sprayed shall be made good with a hand spray and the machine repaired before spraying is commenced.

### Curing of Prime Coat

The prime coat shall be allowed to dry out before anything is allowed to pass over the surface.  Where the prime puddles on the surface, it shall be blinded with sand or quarry dust until the free bitumen is absorbed.  Pneumatic-tyred vehicles shall not run over primed surfaces for at least 7 days.

### Binders for Surface Dressing

The type of binder and the rate of spray shall be as approved by the Project Manager.

The quantity of binder required will depend upon the shape and size of chippings and the nature and absorbency of the surface.

The rate of spray will generally be between 0.8 l/m2 and 1.4 l/m2 for each seal coat to give a total application of 2 l/m2.  The Project Manager may from time to time direct the Contractor to vary the rates of application and the Contractor shall allow in his prices for doing so.

### Chippings

Chippings should be supplied from an approved commercial quarry.  The Contractor shall deliver to the Project Manager’s laboratory at least 28 days before he intends to commence surfacing samples of the chippings that he proposes to use.

The rate of application shall be as approved by the Project Manager and will depend upon the size and shape of the chippings.  The Project Manager may from time to time direct the Contractor to vary the rates of application, and the Contractor shall allow in his prices for doing so.  The approximate rates of application shall be 9 m3 and 7 m3 for 1000 m2 of Tack Coat and Seal Coat, respectively.

### Preparation for Surface Dressing

The previously primed surface shall be swept clean with brooms or other approved method, and the debris deposited well clear of the surface to be sprayed.

Any defects of the surface shall be made good as directed by the Project Manager and no binder shall be applied until the surface has been approved by the Project Manager.

### Surface Dressing

The surface dressing shall be a double seal application.

1.	First Seal

The binder for surface dressing shall be sprayed as specified for the prime and at the rate approved by the Project Manager.

Immediately after the bitumen has been sprayed the 13 mm chippings shall be applied by means of an approved mechanical spreader at the rate approved by the Project Manager.

Should it become apparent that the supply of stone is about to fail, the bitumen spraying shall be immediately stopped and not recommenced until an adequate supply of chippings is assured.

Directly the chippings have been spread they shall be initially rolled so that the whole area receives at least one pass within ten minutes of the bitumen being sprayed.

Immediately after the initial rolling, any area which is deficient in chippings shall be made good by hand spreading.  Brooming of the material to effect re-distribution of chippings will not be permitted.

The rolling shall re-commence at the edges, working inwards to the centre of the road.  The number of passes of the roller shall be to the approval of the Project Manager.

A certain amount of crushing under the roller is permissible but should any general shattering occur the Project Manager may direct that the rolling shall cease regardless of the number of passes completed.

After the bitumen has attained sufficient viscosity to retain the chippings the entire surface shall receive at least one pass of a drag broom or be hand brushed to remove any surplus chippings, and any deficient areas shall be made good with additional chippings.

When the Project Manager is satisfied that full coverage has been obtained, rolling shall recommence and shall continue for two further passes, or as directed by the Project Manager.

No rollers or construction equipment shall be permitted to park on the completed work.

2.	Second Seal

Before applying a further coat of binder, the surface shall be rolled with one pass of a steel wheeled roller to form a flat surface.

The second application of bituminous binder shall now be applied as for the first seal and at a rate approved by the Project Manager within the specified range.  The operation shall be followed immediately by a second application of chippings of the 7 mm size spread in accordance with the manner approved by the Project Manager.

The rolling re-distribution and brooming operations specified for the first layer shall then be carried out.

Two additional passes on previously completed sections shall be given later by a pneumatic tyred roller in the heat of the day (termed "Back-rolling") as may be necessary.

### Control of Traffic and Sweeping

The road shall not be opened to work traffic until the bitumen has attained sufficient viscosity to retain the chippings and not earlier than 24 hours in the case of the first application of chippings.

Unless otherwise directed by the Project Manager the road shall not be opened to other than work traffic before the application of the full number of specified coats.

After traffic has been permitted to run on a surface dressing for a period of at least a fortnight all loose material shall be swept to the side of the road collected up and disposed of.  No windrows of loose chippings shall be allowed to accumulate at the sides of the road.

### Kerb Stone

Kerb stones shall be provided at the edges of roads as shown on the approved drawings.

Kerbs shall be laid on a cement (C20) bed of 100 mm minimum thickness and the joints between the kerb blocks shall be buttered with a 5 : 1 sand/cement mortar finished flush with the surface of the blocks.  In order to obtain a smooth alignment along curves, 300 mm long kerb stones shall be used instead of 1 000 mm.

Kerb inlets shall be provided along kerb line at intervals as shown on the approved drawings, to facilitate drainage of surface run-off from the road.

### Surfacing of Platforms

The stone for surfacing of platform shall comply with the requirements specified under “Materials for the Works” and it must be uniformly spread to a thickness of 100 mm over the full uncovered formation of the platform.

The Contractor shall supply and stockpile at site, the required quantity of stone for later use, as soon as possible after the commencement of the Contract.

Before laying and spreading the 100 mm layer of stone on the platform, the Contractor shall remove any growth of vegetation, re-compact, trim and sterilise the platform surface before laying the stone, so that the formation shall comply with the requirements specified under “Earthworks”, if so directed by the Project Manager.

## Fencing

### Fencing

The Contractor shall construct fencing along the perimeter of sub-stations, including gates where necessary and shall comply with the requirements of the following Clauses. The contractor shall also construct a 2.5mmsq diamond wire mesh on 113mm diameter round poles around the peripherals of the ZESCO plot on which the substation shall be constructed.

### Dimensions

Height of fence:			2 300 mm

Height of chain link fabric: 		2 000 mm

Barbed wire:		3 wires above fabric, height of 300 mm, on supporting arms facing outwards from Site at 450 angle.

Maximum distance between posts: 3000 mm, except where interrupted by gate.

Terminal posts: including end, corner and straining posts; 89 mm outside diameter 114 mm outside diameter at gates.

Embedment lengths of terminal posts:

-	Corner and straining posts		1 100 mm

-	End posts				1 200 mm

-	Gate posts				1 400 mm

Tension bars and bands: locate at terminal posts to fix fabric, bottom wire and barbed wire.

Top rail: "extra-strong" pipe, 43 mm outside diameter.

Braces: "extra-strong" pipe, 43 mm outside diameter for attaching end and gate posts to adjoining posts.  Use two braces at corner and restraining posts.

Gate width: free distance between 2 gate posts, 1 500 mm for single gate, 5 000 mm double gates.

Double gates: one leaf for normal traffic, other leaf to remain closed by means of drop bolt locking into centre rest, inoperable from exterior.

Gates:  able to open in either direction to 900.

Gate hardware: three hinges, latch with padlock accessible from either side of gate, latch catch.

Top of posts and uprights: weatherproof tops.

Ground beam: 100x200 mm concrete beam along the fence at ground level.

### Materials

Fabric: ASTM A 392, 2 000 mm high, 3.8 mm diameter (No. 9 gauge) steel wire, 50 mm diamond pattern, twisted and barbed finish at top, knuckled wires at bottom, zinc coated.

Pipes: ASTM A 120, steel pile, hot-dipped zinc coated after welding, diameter and weight size as shown on drawings, unthreaded ends, free from burrs.

Fence fittings: ASTM F 626, hot-dipped zinc coated according to ASTM A 123.

Barbed wire: ASTM A 121, 2.51 mm diameter wire in strand (No.12-1/2 gauge), 2 strands with 4-point barbs spaced at 125 mm, Class 3 zinc coating.

Bottom wires: 5 mm (No. 6 gauge) steel wire, 500 g/m2 zinc coating.  This shall be surrounded by a concrete beam (C20) as shown on the drawings.

Fence fittings: ASTM F 626, steel tension bars and bands, nuts and bolts, weather proof tops of commercial Aluminium alloy, malleable cast iron, or rolled or pressed steel, cast iron and steel fittings hot-dipped galvanized with 500 g/m2 according to ASTM A123.

Concrete: 20MPA at 28 days

### Installation

Install fencing and gates according to ASTM F 567 unless otherwise indicated, and to approved drawings and this Specification.

Level ground surface so that space between finished ground surface elevation and bottom of fabric does not exceed 50 mm.

The ground beam shall be cast at the bottom of the fence extending 100 mm below ground level.  The bottom 50 mm of the fence fabric shall be encased in the ground beam.

Plumb and align posts to within 10 mm.

Install posts of a gate at same elevation regardless of difference in ground level.

Set posts in concrete footings in form of truncated cone, according to ASTM F 567, and as follows:

|  | ORDINARY SOIL |  | SOLID ROCK |  |
| --- | --- | --- | --- | --- |
| FOUNDATIONS | LINE POSTS & CENTRE REST | TERMINAL POSTS | LINE POSTS | TERMINAL |
| Depth | 1,000 mm | 1,600 mm | 300 mm | 500 mm |
| Diameter at top | 250 mm | 300 mm | 150 mm | 150 mm |
| Diameter at bottom | 350 mm | 400 mm | 150 mm | 150 mm |

Make joints in fabric at terminal posts.

Fasten as follows:

1.	Every 450 mm along top rail, braces and bottom wire.

2.	Every 300 mm on line posts.

Secure barbed wire to terminal and gate posts with tension bands, and to gate uprights with hooks.

Install bottom wire in middle of last line of mesh.

## Concrete and Building Works

### General

This chapter applies to all building works for control building, toilet building, support structures and transformer foundations, cable trenches and other concrete or building structures.

The transformer foundations shall be built with oil catchment pit.

Typical cable trenches and foundations are illustrated on the attached drawings.

The control building and toilet building shall be built to a design and with materials to the approval of the Project Manager and in accordance with the specifications.  The Contractor shall design the buildings taking into account the requirements listed under Scope of Works and allow for space for future extensions, all to approval.  Water shall not enter into the building or the indoor cable trenches.  Metal sheet roofing, if any, shall be properly earthed.

All technical rooms or rooms for apparatus shall be constructed to the requirements of fire cells.  Doors shall be class A30.

### Earthworks

#### Excavation

Excavation for concrete foundations shall be carried out in strict accordance with the requirements of the Project Manager and to fit in with the programme of construction.

#### Shoring and Timbering of Excavation

The Contractor shall be entirely responsible for the safety of all excavations, for the prevention of injury to workmen and for the stability of the faces of the excavation.

The adjacent road surfaces must remain trafficable, and cracking or cave-ins must be avoided.  All shoring and timbering shall be done to the approval of the Project Manager, who may order such shoring or timbering to be strengthened or altered if he considers this necessary in the interests of the work or to safeguard against accidents to workmen or cave-ins. The following categories of shoring shall apply:

Open timber shoring:

This shall consist of vertical boards of not less than 225 mm width and not greater centres than 1.6 metres on both sides of the trench.  Held in place by wallings which shall be strutted apart.

Intermediate boards may be used and must be firmly wedged in position against the wallings.

Close timber shoring:

When ordered by the Project Manager or dictated by the ground condition close timber shoring shall be timber boards in contact to give a complete support to the sides of the trench.  The boards shall be supported by wales and strutted as required.

#### Dewatering

The whole Works shall be constructed in the dry and the Contractor shall be held responsible for keeping all excavations free from water, whatever the source or cause may be, and shall properly deal with and dispose of water by use of sufficient temporary works, plant and appliances so as to ensure that the whole Works is executed in a satisfactory dry and safe manner.

#### Excavation to be Approved.

In no case shall broken stone for under drainage or concrete be placed in an excavation until the surface on which such materials are to be placed has been approved by the Project Manager.

The Contractor shall advise the Project Manager whenever the bottom of any excavation is ready for inspection or whenever it is necessary to cover up the work.  In default of such notice the foundation shall on the order of the Project Manager be uncovered by the Contractor and reinstated without extra charge.

#### Disposal of Excavated Material

All material excavated under this Contract shall be disposed of as agreed with the Project Manager. Selected material required for back-filling shall be removed to a tip found by the Contractor and the Contractor shall be responsible for ensuring that the required amount of spoil is set aside.

#### Other Services

Where trenches pass near or across other services, the Contractor shall take every precaution against damaging such services.  These services shall be properly supported in the trench until back-filling is complete and the back-filling shall be thoroughly compacted under and around such services.

#### Backfilling

Back-filling shall be carried out either with selected spoil as set aside, or with imported selected spoil, or with crusher run, or where specified, with gravel of 38 mm nominal size to B.S.C.P. 2006 Table 4.

No backfilling shall be done until all the formwork has been removed together with pieces of timber, cement bags, vegetation and or other rubbish.

All back-filling shall be compacted in layers not exceeding 150 mm thick and shall be sprayed with water to bring the moisture content to the optimum for dense compaction.

Compaction shall be such as to achieve a minimum of 91% H.C.E density up to 300 mm below pavement level, and a minimum of 98% above this level up to the underside of the pavement.  Compaction is to be tested by a Testing Laboratory.

#### Payments, Excavation and Backfilling

All costs for execution of excavation and backfilling shall be included in the prices stated in the Bill of Quantities.  Additional works, if any, ordered during the cause of the project will be paid for at daywork rates.

### Concrete, Formwork and Reinforcement

#### General

For execution of concrete works BS 8110 Parts 1, 2 and 3, Structural Use of Concrete, shall apply.

#### Materials

1.	Aggregates	a)	Shall conform to CAS 233 or BS 882.

b)	Shall be heaped separately on hard, self-draining surfaces.

c)	Normal size of coarse aggregate shall be 20 mm.

2.	Water

Shall be fit to drink and conform to BS 3148.

3.	Reinforcement Steel

Shall conform to the following standards: BS 4449, BS 4461, BS 4482, BS 4483, SABS 	CKS 158.

4.	Cement

shall		a)	Conform to CAS A46, BS 12 or ZS 000.

b)	Be either normal portland or P.C. 15.

c)	Be used within 6 weeks of manufacture.

d)	Be stored in a manner to exclude any moisture.

e)	Be stored in a manner to ensure use of the earliest consignment.

f)	Different types of cement from different manufacturers shall not be mixed for a single cast or structural element.

g)	If concrete is to be exposed Item 4.f to apply for whole project.

Additives shall not be used.

#### Prior to Concreting

1.	Design Mixes

Not less than 2 weeks before the start of concrete work, the Contractor shall submit to the Project Manager for his approval a statement of proposed mix proportions for the various grades required in the project.  (Note: the grade is the characteristic strength or the cube strength below which not more than 5 % of the result may be expected to fall when tested at 28 days).  The grades required shall be as per approved design and drawings.

The statement shall include proportions of cement, fine and coarse aggregate, and water, the maximum and minimum slump and the target strength for each grade.

A certificate by recognised laboratory that the proposed mix will meet the requirements must accompany the statement.

The proportions stated may not later be altered without the written approval of the Project Manager.

Cost of mix designs to be borne by the Contractor.

2.	Formwork

Formwork shall be sufficient to leave the concrete finishes specified on approved drawings and to be within the tolerances specified below and to provide an acceptable surface for applied finishes, where required.

Line and Level		1 mm per metre not exceeding 5 mm

Pockets, Sleeves etc.	+/- 5 mm

Bases			+/- 50 mm

Where specified as wrot, or the concrete as off good shutter the surface shall be of formboard or wrot smooth timber of not less than 200 mm widths, to impart a smooth finish free of projections, voids, etc.. The type of ties to be used shall be such that the required finish is achieved and does not become marred by subsequent corrosion.  Ties to be set out to definite pattern to the Project Manager’s approval.  Rubbing down may be required, subject to the Project Manager’s approval.

3.	Reinforcement

Shall not be heated or rebent without the Project Manager’s permission.

Shall be free from any material likely to impair bond or initiate corrosion.

Shall be bent and fixed according to the bending schedules approved by the Project Manager

Shall be tied with soft iron wire.

Shall be supported to maintain the following minimum cover during concreting.

a)	The greater of the diameter of the bar or 40 mm for external unplastered face.

b)	The greater diameter of the bar or 15 mm for internal face.

Shall be inspected by the Project Manager.

NOTE:	Holding down bolts shall be supplied to the drawings and schedules approved by the Project Manager.

4.	Construction Joints

Shall be avoided if possible, but if inevitable shall be pre-planned in consultation with the Project Manager and temporary stop ends inserted.  Before placing of concrete against a construction joint, the formed face shall be hacked down to expose the coarse aggregate, kept continuously wet for 24 hours.  Vertical faces should be covered with cement/water slurry and horizontal faces should be covered with 15 mm layer of cement/sand grout.  New concrete should then be placed immediately.

5.	Camber

To formwork as per approval on drawings shall not be at the expense of the overall depth of the concrete.

6.	Weather

Concrete shall not be placed if temperatures above 30 degrees Celsius or below 0 degrees Celsius are expected

#### During and after Concreting

1.	Batching

shall

a)      Be by mass in accurately calibrated scales or be volume in soundly constructed gauge boxes making due allowance for bulking of the fine aggregate.

b)	Be in proportion to whole sacks of cement.

2.	Mixing

shall

a)	Be in a machine in good condition, large enough to carry Q	the whole mix, controlled by a competent experienced operator.

b)	Be for sufficient time to ensure complete mixing of the ingredients.

3.	Placing

shall

a)	Be under the control of a competent, experienced overseer.

b)	Be in a manner to prevent separation of the ingredients.

c)	Be a continuous process until the pour is complete.

4.	Compaction

a)	Shall be by immersion (poker) vibrator in the hands of experienced                            operators.

b)	Concrete shall not be moved by vibrator.

c)	Shall be sufficient to remove all air pockets and honeycombing and to ensure complete dense concrete cover to all reinforcement.

5.	Testing

The Contractor shall make concrete cubes as directed by the Project Manager.  The Contractor shall arrange for transport to and testing at approved testing laboratory. During mixing of concrete for each section of the work and at such other times as directed by the Project Manager, 3 sets of test cubes, size 15x15x15 cm shall be taken, each set consisting of 6 cubes.  From each set 3 cubes shall be tested after 7 days and the remaining 3 cubes after 28 days.  The compressive strength of the cubes shall not be less than 20000 kN/m2 after 28 days.

6.	Curing

a)	Shall commence early on the morning following the placing of the concrete.

b)	Shall be effected by keeping the concrete in a permanently wet state.

c)	Membranes shall not be used.

d)	Shall continue for a minimum of seven (7) days or such longer time as may be required by the Project Manager.

7.	Stripping of Formwork

a)	To soffits shall not be struck until 7 days after placing of concrete (but see below for (props).

b)	To vertical faces shall not be struck until 14 days after placing concrete.

c)	Props to soffits shall not be struck until 14 days after placing concrete.

d)	Shall not be stripped without the Project Manager’s approval who has the power to vary the above items.

8.	Patching

a)	To defective work shall not be undertaken before the item has been shown to the Project Manager.

b)	Is a sign of poor workmanship.  The Project Manager shall have the right to reject the complete element if an unreasonable amount of patching must be done, or if patching will spoil the appearance of the finished concrete.

9.	Records

Are to be kept by the Contractor, showing date and time of each concrete pour, the weather conditions, the temperature, the number of the cubes which represent the concrete, the slump and any other items which the Contractor and/or the Project Manager consider relevant.  These records are to be made available for inspection by the Project Manager when required.

### Brickwork Specifications

#### Bricks

All bricks are to be the best of their respective kinds, hard, square, sound, free from any cracks or defects and even in size. All bricks are to be obtained from an approved manufacturer.  Clay bricks or cement bricks may be used.

#### Cement

The cement is to be as described under Concrete.

#### Sand

The sand is to be clean, sharp, fine grain material free from impurities.

#### Water

The water is to be potable and free from deleterious materials.

#### Mortar

Approved gauge boxes are to be used for measuring all ingredients.  The ingredients are to be mixed dry on an approved mixing platform until they are thoroughly incorporated, and then water may be added slowly afterwards.  Care must be taken that no foreign matter is mixed in with the mortar.

#### Cement Mortar

The cement mortar is to be mixed in the proportions of 1 Cement, 4 Sand, and thoroughly incorporated with a sufficiency of water.  Any cement mortar which has been left for more than one hour shall not be used in the Works.

#### Brickwork Generally

The brickwork unless otherwise specified is to be built in English Bond.  Half brick walls are to be built in Stretcher Bond.  All courses are to be built to a fixed standard level throughout, and true to line.  All angles and perpends unless otherwise shown are to be plumb and properly raked back where required.

Brickwork is to be in whole bricks as far as possible, bats and closures only being used where necessary for bond.  No portion of brickwork shall be carried up more than 1,2 m above adjoining work.

All mortar joints are not to exceed 13 mm, or less than 10 mm in thickness.  Gauge rods must be set up and used continuously.

All brickwork is to be set out and built strictly in accordance with dimensions, thickness and heights shown on the drawings.

All face brickwork is to be protected in an approved manner before any work is carried out above or near the facings.  Remove protection and clean down facings on completion.

#### Damp Proofing

Damp proof course is to be three ply Malthoid, or other equal and approved material, laid under all superstructure walls.  It is to extend the full width of the walls, overlapping at all ends and angles, and stepped if necessary.  Damp proof course is to be laid under all window cills and tucked up under window section and under the eaves beam.

#### Joints Raked

Joints of brickwork internally are to be raked out as work proceeds to form a key for all plaster work.

#### Building in Door Frames

Door frames are to be built into brickwork truly vertical and square with six ties per frame.  Cement mortar is to be packed around brickwork built into back of frames.  Temporary props to be provided.

#### Building in Windows

Windows are to be built into brickwork truly vertical square with six ties per frame.  Windows over 1.00 m wide are to be provided with additional head and cill ties.  Temporary props to be provided.

#### Building in Roof Ties

Galvanised hoop iron ties are to be 15 s.w.g. by 25 mm wide built 0.750 m into external wall at 1.0 m maximum centres.

#### Brick on Edge Cills

Bricks on edge are to be set on a slight slope and projecting a minimum of 25 mm beyond wall face.  The bricks are to be bedded and pointed in 1:4 cement mortar.

### Plaster and Floor Coverings

#### Materials

Cement and water to be as described under brickwork.  The sand to be screened through a sieve of 10 to 15 and meshes to 1 cm and to be washed if directed.

#### Mixing

All materials for mixing are to be used in proper gauge boxes and they are to be strike measured and not tamped down in boxes.  Proper non-absorbent stages are to be used for mixing and storing mortar.  No foreign matter must be mixed with the mortar.

The materials are to be mixed dry before adding water through a fine hose spray.  No cement mortar which has taken its initial set will be allowed to be used.

#### Plaster Thickness

Unless otherwise specified all wall plasters should not be less than 13 mm thick and not more than 19 mm thick.

#### Cement Plaster

Cement plaster for external use to be composed of one part cement to four parts sand and for internal use to be one part cement to five parts sand.

#### Rhinoset Plaster

To be used in strict accordance with the manufacturer's printed instructions and steel trowelled to a hard, true and glass like surface.

#### Form Key

Rake out joints and roughen if necessary to form key for plaster.

For concrete surfaces, hack and apply 1:1 cement sand slush to form key.  Continuously wet for 7 days and then apply plaster.

All brickwork and concrete works shall be brushed down to remove dust and any other loose material.

#### Wetting

All internal and external brick or concrete surfaces are to be wetted well before plastering.All cement plaster must be kept wet for at least 7 days.

#### Repairing Defects

All defective plaster, cracks, hollows, etc., are to be cut out to a rectangular shape, the edges undercut to form a dovetail key and to be made good to finish flush with the edge of the surrounding plasterwork.

All patches shall be to the approval of the Project Manager and if the defects cannot be made good satisfactorily then the whole surface is to be removed and re-plastered at the Contractor's expense.

#### Granolithic Floor

Preparation of bases

Clean all bases thoroughly to remove all dirt, dust, rust and oil.  Hack and expose as much coarse aggregate as possible.  Wet base for 24 hours before laying finish and remove surplus water.  Brush neat cement slurry onto surface 20 minutes before laying finish.

Materials

Use approved, clean, washed granite chippings or other approved stone graded in size from 7 mm down with not more than 20% fine material passing 200 micron mesh sieve.  Mix to comprise 1 part Portland Cement, 2 parts coarse aggregate and 1 part river sand by volume.  Use smallest quantity of mixing water needed to give adequate mouldability.  Lay to a finished smooth surface of 40 mm and finish off with a steel trowel.  Continuously wet finished surface for 7 days.

#### Wall Tiling

Ensure that the base to receive tiles is level, dry and clean with no loose and friable areas or surface dusting.  Prepare and use adhesive to manufacturer's recommendations to form a bed not more than 3 mm thick.  Lay tiles dry and tamp well down to ensure a proper bond with base and a level surface.  Grout up joint with approved white cement.

### Carpentry and Joinery

#### Timber

To be best quality procurable, free from sap, white wood, shakes, large, loose or dead knots, waney edges and other defects.  Timber to be sawn to hold the full specified sizes and die square.

Timber and timber products to be guaranteed free from borer and beetle infestation of any kind.  Any defects traceable to such infestation shall be rectified by the Contractor at his own expense, including any timber adjacent to the affected parts.  This guarantee shall be valid for a period of two years from date of handling over the works.

Timber to be well seasoned and kiln dried to a moisture content not less than 10% or more than 12%.

#### Softwood

Softwood for carpentry to be selected straight grained timber in accordance with relevant SABS or equivalent standard.

Laminates are not to exceed 25 mm thickness and are to be finger jointed.

#### Hardwood

Hardwood to be best quality selected wrot straight grained kiln dried of the type specified.  Submit sample 600 x 150 x 38 mm for approval.

#### Structural Timber

Timber for non-structural framing, battens and brandering to be merchantable grade and shall conform to relevant SABS or equivalent standard.

Structural timber to be merchantable grade and shall conform to relevant SABS or equivalent standard.

Glued laminated timber shall conform to relevant SABS or equivalent standard.

#### Workmanship

All timber for carpentry work to be in as long lengths as possible and all laps and joints to be placed over points of support.  All wrot timber to be finished clean, smooth, and free from tool marks.

#### Nailing

All nails are to be of the best quality and of gauge, length and strength suitable for work.  They will be long enough to enter the second timber at least one half their entire length before punching.  Skew nailing will only be permitted in the framing.

#### Sizes

All sizes specified are nominal before dressing or shaping.  2.5 mm will be allowed off nominal (sawn) sizes for each wrot face.

### Glazing and Painting

#### Glass

All glass is to be of approved manufacture, free from bubbles, waveness, scratches or other imperfections and is to be well bedded, puttied and backputtied and secured with glazing pins or clips in steel sashes or with sprigs in wood sashes.

All glass shall be carefully cut to the required sizes so that all panes of figured or textured glass are uniform in appearance with the pattern parallel to the edges and wired glass shall be so cut that the wires are parallel to the edges.

#### Putty

Putty for glazing to steel sashes is to be of approved proprietary brand specially made for use with steel sashes and shall conform to relevant SABS or equivalent standard.  Best quality linseed oil putty shall conform to relevant SABS or equivalent standard to be used for wood sashes tinted as necessary when used for glazing to hardwood.  Rebates are to be thoroughly back puttied before glazing and all putty is to be carefully trimmed and cleaned off so that back putty finishes level with the top of sections internally, external putty covers sight lines exactly and finished straight and true.  Rough surfaces to putty will not be allowed and any defective putty shall be cut out and replaced at the Contractor's expense.

Rebates of wood sashes are to be given one coat of priming immediately before glazing.

#### Mirrors

Glass mirrors are to be of approved thickness and glass quality, silvered on back, with protective sealing coat and arrised edges, unless otherwise described.

#### Generally

All cracked, broken or defective glass shall be replaced.  All glass shall be left thoroughly clean and perfect at completion.

#### Materials for Decoration

All paints, primers, varnishes, emulsions, stopping, etc., to be of approved manufacture.

The Contractor is to use proprietary ready mixed paints obtained from an approved supplier.

When a coat of proprietary paint is applied, the manufacturer's priming and previous coats suitable for the particular type are to be used.

All materials must be brought on to the site in unopened tins, and no dilution or adulteration will be permitted, unless approved by the Project Manager.

#### Emulsion Paint

Emulsion paint shall be PVA (Polyvinyl Acetate) alkali-resisting formulated with high washability and capable of resisting a 8 000 scrub test.  The first coat to be specially formulated base coat for direct application to the specified surface.

#### Fillers

Higher grade cellulose fillers are to be used internally and premixed filler to be used externally.

#### High Gloss Paints

Primers

Primers for application to bare metal to be red oxide primer for iron and steel.  For galvanised metal to be an approved zinc chromate or galvanised iron primer.  For application on wood or plaster etc., to be an approved alkali primer.

Finish enamels

Finish enamels to be synthetic enamel high-capacity paint with high coverage and high gloss finish unless otherwise described.

#### Workmanship

All surfaces are to be free from moisture, dust, grease and dirt and rubbed down smooth according to approved practice.

All plaster to be free from efflorescence and treated with one coat of petrifying liquid, approved sealer or alkali primer if required.  Hardwall plaster to be glass papered before decorating.

Rectifying defects to decorated surfaces due to dampness, efflorescence, chemical reaction, etc., will be to the Contractor's account, as these surfaces must be checked, and the appropriate precautions taken before applying the decoration.

Metalwork must be scraped free of rust, primed as described and finished as later specified.

Galvanised sheet iron, pipes, etc., are to be cleaned down to remove manufacturer's ammoniated dichromat protective covering, primed as described and finished as later specified.

Coated pipes are to be cleaned down, stopped and primed with one coat of aluminium primer and finished as later specified.

All knots in woodwork to be treated to prevent bleeding.  Large or loose knots to be cut out and be replaced with sound wood or cut back and filled.  Small knots to be treated with two thin coats of Shellac in methylated spirits.  Woodwork to be glass papered to a smooth surface with all sharp arises removed, all cracks, crevices, holes, etc., to be scraped out, primed as described and stopped with hard stopping, faced up and rubbed down to an even surface and finished as later specified.

All metal and woodwork to have the number of coats in addition to the priming coat as is necessary for good finish to the approval of the Project Manager.

Every coat of paint must be a good covering coat and must dry hard and be well rubbed down to a smooth surface before the next coat is applied, otherwise the Contractor will be required to apply extra coats at his own expense.

Each coat of paint to be of a distinctive colour: sample colours are to be prepared for the final coat which is to be an approved colour scheme and must not be applied without the permission of the Project Manager.  After undercoats are on, the painter shall check all work and grain fill as necessary with filler as described.

NOTE:

1.	All paints are to be obtained from an approved manufacturer and used in strict accordance with their instructions.  Their representative may check the paints being used and the method of application and advise accordingly.

2.	This section of the work to be carried out by an approved firm of decorators who must allow for the very best finish possible and of the highest quality obtainable.

3.	Provisions shall be made for the removal and refitting of all beads, fittings, fastenings, ironmongery, etc., removed for decoration purposes to be carried out by skilled tradesmen of the appropriate trade.

### Steelwork for Buildings

#### General

This clause applies to steel structures carrying the control building roof and other steel structures or parts in the building, if any.

Steel structures shall be designed at least for minimum dead and imposed loads as defined in BS 6399, Part 1, 1984, for wind loads according to CP 3:  Chapter V: Part 2, for loads due to equipment, assembly and erection and for combinations thereof.  The design loads from wind shall take into account the Zambian conditions.

#### Workmanship

Unless otherwise specified all steel work shall comply with the following requirements:

-All work shall be finished straight, smooth and free from all defects and imperfections and shall be to the sizes shown on the approved drawings.

-All steelwork shall be rigidly fixed in place as shown on the approved drawings using proper size of bolts, anchor bolts and locks.

#### Steel Cutting

Cutting of steel parts shall be done mainly mechanically.  Oxygen burning may be used with the permission of the Project Manager.  All cut parts and sections shall be ground even and filed smooth with rounded edges.

#### Steel Welding

All welding materials, plant, equipment, procedures and types of welds shall comply with BS 5135 and BS 4360.

Filler materials for welding shall be as required for the type(s) of steel to be welded.  The welding work of the structures shall be performed by qualified welders.

The welds shall be continuous, uniform in size throughout their full length, free of non-metallic inclusions, porosity, weld-bead cracking, weld bead craters, piping, undercutting and heat-affected zone cracking.

When not mentioned on drawings welds shall inspected over the entire length of the joint face.

#### Manufacture

Lifting links when required for handling, transportation or assembly shall be in accordance with manufacturer’s instructions. Weight shall be clearly marked when piece weight exceeds 1000 kg.

No permanent deformations in the members caused by lifting, transportation or storage shall be permitted.

Parts shall be clearly marked to assure assembly in proper positions.

Shop-made parts shall be inspected and accepted by the Project Manager prior to transport to the site.

#### Finishes

Prior to treatment the steel surface shall be cleaned of dirt and grease, and the heavier layers of rust shall be removed by chipping.

A thorough blast cleaning of the steel surface shall be done prior to coating.  All mill scale, rust and foreign matter shall be removed.  Finally, the surface shall be cleaned with a vacuum cleaner, clean dry compressed air or a clean brush.

It shall then be greyish in colour and correspond in appearance to preparation “second quality” as specified in BS 4232.

Finishing of steel members shall be as specified under Glazing and Painting.

During erection or otherwise damaged already painted steel surface shall be prepared as follows prior to recoating:

Thorough scraping and wire-brushing - machine brushing - grinding - etc.  The treatment shall remove loose mill scale, rust and foreign matter.  Finally, the surface shall be cleaned with a vacuum cleaner, clean dry compressed air or a clean brush.  It should then have a faint metallic sheen.

#### Non-Structural Metalwork

1.	This clause applies to all ferrous and non-ferrous non-structural metalwork unless this is separately specified under a different section.  Steel plates to cover indoor cable trenches and cable carriers belong to this category.

All metal components are to be supplied by approved manufacturers, the drawings of which shall be submitted to the Project Manager for approval.

Cold rolled sections shall comply with BS 2994.  All steel surfaces shall be finished as specified under Glazing and Painting.  Any defects occurring during delivery, welding or other handling are to be reinstated to their original condition at the Contractor’s expense before the actual painting work may commence.  Galvanising of steelwork shall be carried out according to BS 729.  Sizes of non-ferrous bars shall be according to BS 6722:1986.

2.	Materials for the installation of miscellaneous metal work items which will be exposed to view, only materials which are smooth and free from surface blemishes including pitting seam marks, roller marks, rolled trade names and roughness shall be used. Such blemishes shall be removed by grinding or by welding and grinding, prior to cleaning, treating and application of surface finishes including zinc coatings.

3.	Workmanship

Materials of the size and thickness required to produce adequate strength and durability in the finished item for its intended use shall be applied.  Work shall be carried out to approved dimensions and details of fabrication and finishing.

Where manufacturer’s instructions exist regarding workmanship etc., these shall be strictly complied with.

### Roofing, Moisture Protection and Water Proofing

#### With Bituminous Materials

1.	General

The waterproofing work, design, materials and workmanship are to be generally carried out to the recommendations of CP 144: Part 3:1970.

2.	Materials

The waterproofing shall consist of an approved, waterproofing agent and two layers of bituminous roofing felt conforming to BS 747:1977.

All other miscellaneous materials such as primers, fillers, sealers, adhesives, angles fillets and other accessories as recommended by the manufacturer shall be provided.

The waterproofing materials shall be subject to the Project Manager’s approval.

3.	Workmanship

Installation of the waterproofing shall be in accordance with the relevant requirements of CP 144: Part 3 and shall be performed in accordance with the manufacturer’s written instructions.

4.	Surface Preparation

The waterproofing shall be laid to a regular surface free from sharp protrusions and hollows.  Surface improvements shall be as directed by the Project Manager, at the expense of the Contractor.

5.	General Details

Adjacent rolls of the waterproofing membrane shall be provided with a 75 mm overlap to ensure complete adhesion between both layers.

All joints shall be well rolled until complete waterproofing is obtained.

All angles and corners, external and internal, shall be reinforced with an extra strip of 300 mm wide waterproofing membrane.

External corners where possible shall be trowelled to provide a 25 mm x 25 mm minimum splay.

Internal angles between slab and walls shall be provided with a 40 mm x 40 mm waterproofing fillet to facilitate dressing the membrane at these points.

Where the waterproofing membrane is to terminate at an upstand, a chase should be provided of dimensions 25 mm x 25 mm.  The waterproofing membrane shall be dressed into the chase and pointed with mastic prior to backfilling.

On the horizontal and vertical areas where subsequent processes may cause damage, the waterproofing membrane shall be protected with one layer of close butted protection board fixed to the waterproofing membrane with the adhesive recommended by the manufacturer.

Before covering, inspect to ensure no damage.  Any damaged areas should be patched with the waterproofing membrane and well rolled to provide continuous membrane.

6.	Protection of Waterproofing Membrane

The waterproofing shall be protected against UV-radiation ageing using a screed or other protective layer immediately after installation.  The protection shall be non-combustible.

#### With Corrugated Asbestos-Cement Sheets

1.	General

The waterproofing, work, design, materials and workmanship shall be carried out to the recommendations of BS 5247: Part 14:1975.

2.	Waterproofing Materials

The waterproofing shall consist of approved corrugated asbestos-cement sheets.  All other miscellaneous materials such as ridge cappings, flashing pieces, bird proofing pieces, soaker flanges, fixing and other accessories as recommended by the manufacturer shall be provided.

The waterproofing materials shall be to the Project Manager’s approval.

3.	Workmanship

Installation of the waterproofing shall be in accordance with the relevant requirements of BS 5247: Part 14 and shall be performed in accordance with the manufacturer’s written instructions.

4.	Base Preparations

The waterproofing shall be laid to timber or steel purlins not less than 50 mm wide. The purlin spacing shall not exceed the maximum purlin spacing recommended by the manufacturer.

5.	General Details

Corrugated asbestos-cement sheetings are designed for a side overlap and the corners shall be mitred for correct lay.  Sheets shall never be laid staggered to avoid mitring.  The sheets shall be cut with a saw, breaking off corners for mitring is not permitted.

Care shall be taken to fix the sheets correctly to the purlings. They shall be fixed through the crown of the second corrugation from the side lap.  Only the bottom row along the eaves shall be fixed on each side of the vertical lap and on all other rows one screw purlin is sufficient.

The sheets shall be laid smooth side up and it is important that a square start is made.

Galvanised drive screws for fixing to timber purlins and galvanised hookbolts for fixing to steel angle purlins shall be used.  The fixings shall be provided with either galvanised diamond washers or lead cupped washer with diamond felt washers or round felt washers, holes for fixing shall be 0.8 mm larger than the fixing.  Nuts or hookbolts shall not be over tightened.

6.	Precautions

Roof ladders or crawl boards shall be used to ensure safety and to avoid possible damage to the sheets, under no circumstances shall anyone walk between two purlins.  Materials shall not be loaded onto the roof.

Many asbestos based materials are subject to regulations in different parts of the world, which require precautions to be taken to ensure that they will be without risk to health when properly used.  Users shall observe those regulations, if applicable.

#### Metal Sheet Roofing

Shall be installed in accordance with manufacturer’s recommendation and to the approval of the Project Manager.  All necessary materials, tools and work shall be provided by the Contractor.

### Doors, Windows, and Louvres

#### General description

Doors, windows and louvres shall be factory assembled, and shall be of a standard type unless conditions on site dictate otherwise.

The shop drawings of all doors, windows and louvres shall be submitted to the Project Manager for approval.

Door, window and louvre frames and thresholds shall be of the same material as the relevant doors e.g. metal for metal structured doors and timber for timber framed doors.

Doors, windows and louvres shall be constructed in accordance with the published specification of the manufacturer and shall be within the following deviations or tolerances.

Dimensions:			 1,5 mm

Cup or bow - in width		2

- in length		4

- at diagonals		5

Twist of corner points

from vertical plane		6 mm

Squareness of top or bottom

for 500 mm	0,75 mm

Ironmongery is specified in separate Clause in this specification.  The same applies to glazing.

If special ironmongery is required for nonstandard or special doors, windows or louvres these shall be as recommended and prescribed by the manufacturer.

The Contractor is fully responsible for replacement of damaged doors, windows and louvres and also for the final cleaning.

The doors, windows and louvres may be local made, but if unavailable locally they shall generally be according to relevant SABS or other equivalent Standard.

The installation of doors, windows and louvres shall be in accordance with the manufacturer’s written instructions.

#### Doors

1.	Steel Doors

General requirements of steel plate and cold rolled section and finishes are described elsewhere in this specification.  All doors and frames shall generally be of welded construction, without any disposition of metal.  Edge joints shall be face welded and given a smooth rounded finish.

Double doors and frames shall be standard pressed steel substation doors, with pressed steel louvred panel fitted with flyscreen.

Single utility doors and frames shall be standard pressed steel utility doors with double skin.

Transportation and storage of the doors shall be done in such a way that damage do not occur.

2.	Wooden Doors

Door frame, leave and architraves shall be made of wood according to CP 151, Part 2 and have painted finish as described under Glazing and Painting.

Door frame shall be of solid timber and properly fixed.

All joints between frame and jamb shall be caulked with mineral wool or other suitable material.  Holes made during the fixing of the frame shall be subsequently filled with plastic plugs.

Architraves shall be of softwood.  Rebated door leaf shall be constructed with a frame of timber and cover of solid fibre board with hardboard facing.

Threshold shall be of hardwood.

#### Windows

The windows and frames shall be standard steel windows.  The windows to be opened shall be fitted with flyscreen, all the windows shall be fitted with burglar bars.

#### Louvres

The louvres shall be standard pressed steel units to the approval of the Project Manager.  They shall be fitted with flyscreen.

### Ironmongery and Hardware

#### General Requirements

All ironmongery shall be of high quality, to the approval of the Project Manager.  Standard sets shall be used for situations that can be regarded as domestic (washrooms, minor technical rooms, and other such areas that are provided with household type doors).  Samples shall be submitted to the Project Manager prior to approval.

The hardware for special doors shall be according to the door manufacturer unless otherwise stated and approved by the Project Manager.

The British Standards are for guidance only with reference to the quality and standards that are sought in this contract.

Ironmongery and hardware generally shall be according to BS 4951:1973 or relevant SABS.

All ironmongery and hardware shall be assembled and fixed in accordance with the manufacturer’s written instructions.  Fastening with a matching finish shall be used.  After ironmongery has been fixed in place all moving parts shall be checked and adjusted to ensure correct functioning, lubricating if necessary.

#### Products

1.	Hinges

Hinge types for the steel doors and gates shall be as recommended by the door manufacturer.  Hinges for wooden doors shall be lift off type and of chromium plated mazak.  Hinges shall comply with BS 1227: Part 1A:1967.

2.	Lever Handles

Lever handles shall be fitted to the specified lock types.  Only one-type of lever handle shall be used which shall be of chromium-plated mazak.

3.	Bow Handles

All double doors shall be provided with bow handles on both sides of the door plate.  The length of bow handles shall be to approval.  Material shall be of chromium plated mazak.

4.	Barrel Bolts

On the metal double doors, barrel bolts shall be installed.

5.	Door Stops

Doors shall have door stops of approved material.

Doorstop shall be plunger type holder with rubber shoe, screwed to the door leaf.

6.	Prescribed Ironmongery and Hardware for Special Doors

Where special ironmongery is required for nonstandard or otherwise specially ordered doors, these shall be as recommended and prescribed by the manufacturer of the door.

7.	Locks

Locks shall comply with BS 5872:1980.  Doors except gates, toilets and shower room doors, shall be provided and fitted with cylinder locks.

The double steel substation doors shall be provided with padlocks.

The locking system shall be based on the principal of a master and sub-master key system.

The Contractor shall submit the locking and lock schedule to the Project Manager for approval.

The locking mechanism shall be based upon a rotating retainer disc and cylinder drum system which shall be the same for all the different individual locks.  The lock type shall possess many different individual locks and many different opening permutations.

Keys shall be of nickel silver and shall be produced to fine tolerances.  Together with the previously stated 3 keys per lock, the Contractor shall also provide a key cabinet for the building.  The Contractor shall furnish the Project Manager with information on how to obtain duplicate keys.

All such locks shall have thumb turn knobs on the reverse face of the door.

Toilet doors shall be provided with a standard cylinder lock with lever handle.  Such locks shall be openable from the outside with a purpose made key, and from the inside by thumb turn.

These types given are only operating types and the types recommended by the Contractor for the approval by the Project Manager shall be suitable for the door types (suitable for metal doors, wooden doors etc.).  All samples of the locks and the locking schedules shall be to approval by the Project Manager.

8.	Fittings for Windows

The fittings for windows shall be the window manufacturer’s standard type and shall be to approval by the Project Manager.

### Plumbing

#### Regulations

All plumbing and drainage work shall be executed strictly in accordance with the Local Authority's By-Laws and Regulations.

#### Licensed Plumbers and Drainlayers

Only licensed Plumbers and Drainlayers shall be employed to carry out any plumbing and drainage works.

#### Sheet Iron

All sheet iron to be of approved brand, galvanised and of the thickness specified and shall conform to BS 2989.  Galvanised iron nails shall be used for galvanised sheet iron where required.

#### Flashing

Flashing, etc., shall be properly lapped at angles and passings.  Dress flashing 38 mm into grooves and 6 mm up at back and wedge with rolled wedges.  No screws or nails are to penetrate gutters or flashings.  Provision to be made for expansion and contraction under changes of temperature.

#### Eaves Gutters and Rainwater Pipes in Sheet Iron

Eaves gutters and rainwater pipes shall be formed to sizes and shapes specified.  The rainwater pipes shall have close welted and soldered seams, and the joints between lengths are to be riveted and soldered.  All joints in the straight length and at angles, stop ends, etc., are to be riveted and soldered.  Sizes of gutters are to be effective sizes.

The eaves gutters shall be fixed to falls to outlets on 6 x 25 mm mild steel gutter brackets bent to suit the profile of gutter and twice holed for and screwed to woodwork or bolted to steel at not exceeding 1.00 metre centres.  Alternatively, approved fascia brackets may be used.

Rainwater pipes shall be fixed to walls with 4 x 38 mild steel straps in two section, bent around pipe with the ends bent to form flanges 25 mm long holed for and bolted together with and including two 19 x 6 mm gutter bolts with locknuts and one section of the strap riveted to and including 4 mm thick mild steel anchor 33 mm wide and 230 mm girth with end split and flanged for and built or cut and pinned to brickwork or concrete in cement mortar at not exceeding 1.50 metre centres.

#### Asbestos Cement Pipes

Asbestos cement pipes and fittings shall conform to relevant SABS or BS standards and are to be laid in strict accordance with the manufacturer's written instructions.

#### Plastic Pipes

Plastic pipes and fittings shall conform to relevant SABS or BS standards and be fixed including brackets in strict accordance with the manufacturer's written instructions.

#### Cast Iron Pipes

Cast iron pipes and fittings shall conform to BS 416.  Heavy-duty cast-iron pipes and fittings shall conform BS 1130.  All pipes and fittings are to be coated with an approved preservative.  Pipes are to be jointed with gaskin and caulked with molten lead.

#### Steel Pipes

Steel pipes and fittings shall conform to relevant SABS and BS 143 and be galvanised.  Pipes are to be jointed with hemp and red lead.  Medium quality pipes are to be used, unless otherwise specified.  Fix to roof timbers with stout galvanised clips and to walls with galvanised hinged holderbats with brass pins at not exceeding one metre centres, built into walls with cement mortar.  Sling pipes to soffits on 6 x 32 mm mild steel strip fixed around pipes with 6 mm galvanised bolts with ends split and fanged and cut pinned to concrete soffit.

#### Copper Pipes and Fittings

Copper pipes shall conform to BS 659; BS 1306 and BS 1386 shall be solid drawn seamless supplied in straight random lengths, round clean, smooth, free from internal or external grooving, other defects and deleterious film.

All copper pipes carrying hot water are to be supported so as to allow free movement for expansion and contraction, particularly at the end of long runs where a change of direction takes place.  Fix tubing to walls with brass hinged holderbats with pins at not exceeding one metre centres built into wall with cement mortar.  Fix to soffits as described for steel pipes.

Fittings and couplings etc., for use with copper pipes shall be of the manipulative compression joint type, or other approved type.  All fittings, etc., are to be made from suitable corrosion resistant copper alloy, sound and clean, without flaws or laminations and full bore throughout.  All fittings and their component parts shall be capable of withstanding an internal hydraulic pressure of 2.20 MPa without showing signs of leakage or other defects.

#### Sizes of Pipes

The sizes of pipes, traps, etc., are the nominal bore except for PVC which shall be the external diameter.

#### Traps

Traps shall be brass, copper, polythene or cast iron as specified.  Generally, traps to shower trays, baths, lavatory basins, drinking water fountains and domestic sinks shall be tubular copper to BS 1184, of the same size as the waste outlet of the fitment, and shall have tails to suit the waste pipe to which they connect.

#### Stainless Steel

Stainless steel to be the austenitic type and shall comply with BS 970 EN58 series, and unless otherwise described, to 0.9 mm thick in 18/8 quantity and shall be entirely nonmagnetic.

#### Brassware

Brassware is to be of the best quality and equal to the samples approved.

All stop valves, bib taps, hose union bib taps and pillar taps shall comply with BS 1010 or SABS 226 and shall have washer plates so secured as to lift with the spindle.

Cold water taps shall in every case be fixed at the right hand side of sanitary fittings.

All ball valves shall comply with BS 1212 and shall be of sizes and for the pressure indicated or specified.  The loose orifice seats shall be of nylon for sizes 15 and 20 mm and bronze for sizes 25, 40 and 50 mm.  Ball valves shall be supplied and fixed complete with copper floats to BS 1968 or with plastic floats not less robust and having a lifting effect not less than a BS 1968 copper float for the same duty.

#### Technical Requirements of Equipment

1.	Flow Meters

In case of municipal supply the pipeline shall be equipped with a closing valve and flow meters before the cold water storage tank.  The flow meter shall be suitable for waterworks purposes and be a rotary vane type.  The meters shall be calibrated to cubic meters within the range of 2 % when tested at maximal flow.  Working pressure is the same as for pipes.

2.	Water Storage Tank and Domestic Cold Water Pipes

The size of the cold water storage tank shall be 0.5 m3 and the material shall be stainless steel.  Incoming water pipe shall be equipped with a float valve which close the water flow when the water reach high level in the tank.  The tank needs a vent pipe size of 50 mm.  Material of domestic cold water pipes is PVC pressure pipe joined together by solvent welding.  The storage tank and piping shall be capable of withstanding a safe working pressure of 60 m head of water.  All PVC joints shall comply with BS 4346.  Distance between to pipe supports shall not be more than 1.0 m.

3.	Pressuration pump and valves etc. of type to be approved shall be installed if necessary and required by the Project Manager.

4.	Sanitary Sewer

Material for sanitary sewers shall be unplasticized PVC soil quality and shall comply with BS 4660.  Each main sewer shall be equipped with a vent pipe out (nominal size 75 mm) to protect water traps to be emptied.  Cleanouts shall be installed by horizontal run each 20 m, by change of size, direction or elevation of more than 45 deg.  Every vent pipe shall have cleanout above the slab floor lewel.  If cleanouts are located outside the building or below the slab floor, there shall be manholes.  The manholes shall be provided with cast iron frames and covers confirming to BS 497 iron steps spaced 300 mm apart in accordance with BS 1247.  Horizontal pipes shall be installed with minimum slope of 2 % and maximum of 20 %.

Septic tank shall be divided in three chambers made of concrete.  Each chamber shall have maintenance openings as normal manholes and a vent pipe.  The wastewater from the septic tank shall be emptied by tank car.  Overflow from septic tank shall be disposed of in a way acceptable to local authorities.  The whole installation of sewage plant shall comply with the local statutory regulations including minimum distances from the buildings.

5.	Water Closets and Sinks

Water closets shall be floor mounted of vitreous china with full circle seat and lid with vacuum breaker.  The water cistern shall be of 6 dm3 capacity with internal overflow and float valve made of brass and with rubber sealings.  Nominal size of sewer outlet is 100 mmn.  Water trap is needed.  Sinks shall be wall mounted by steel hanger and made of vitreous china.  Sinks shall be equipped with cold water tap, bottom plug and water trap.  Size of the sewer is 32 mm above and 75 mm below the floor.

6.	Pipe Sleeves

Steel or plastic sleeves through walls for mechanical services shall be provided..  All pipe sleeves, types and installation, shall be to the approval of the Project Manager.

#### Excavation, etc.

Excavate bottom of drain trenches to an even fall and lay 75 mm cement concrete (Grade 10-20 mm stone) bed under pipe and support each length of drain pipe with stoolings of cement concrete (Grade 10-20 mm stone) behind each collar and haunch up half way around external diameter of the pipe.

#### Generally

No holes are to be cut through reinforced concrete work unless approved.  Where possible sleeves are to be cast into concrete.  Where drainpipes pass through walls, etc., they must be arched over to prevent any loads being transmitted from the structure.  Rainwater shall be prevented from entering the building.

#### Testing and Cleaning

All sheet metalwork shall be carefully and efficiently inspected and tested on completion and left perfectly watertight.

All defective work shall be taken out and replaced with new work at the Contractor's expense.

At completion of plumbing and drainage installations, clean down and flush pipes, traps, etc., wash sanitary fittings and test the whole to the satisfaction of the Local Authority and the Project Manager including making good and re-testing until found perfect.  The Contractor must provide all necessary equipment to carry out any tests required.

### Mechanical Services

#### General

This clause covers the requirements of design, delivery, installation, and testing of mechanical services.

#### Ventilation

For control rooms and switch gear rooms the outside air has to be filtered and overpressure has to be kept.  For that purpose, there has to be a make-up air fan with fine filter.  If this fan serves different fire zones each supply air duct needs a fire protection damper.

Battery rooms shall be equipped with exhaust fan and the air change should be calculated to 3-times the room volume per hour.  Supply air comes through wall grilles with coarse filter.

Ventilation may be based on natural draft with grilles in front doors and back walls.  Where the Contractor can document that this is sufficient.

Air conditions units shall be installed where necessary and be to the approval of the Project Manager.

1.	Fans

Material of fans shall be hot dip galvanized steel.  Belt drive shall have totally enclosed guard.  Electrical motor shall be mounted on slide rails for convenient adjustment of the belt tension.  Total efficiency of the fans shall be minimum 0.7.

2.	Filters

Fine filter of cartridge type shall be used, with efficiency of EU 8.  Maximum pressure drop shall be 300 Pa.  As coarse filter standard plan filter with an efficiency of EU 3 shall be used.  Maximum pressure drop shall be 100 Pa.

All filters shall be equipped with manometers.  Filter casing shall be made of hot dip galvanized steel.

3.	Ducts

Material of ducts shall be hot dip galvanized steel plate and shall be manufactured according to DW/142 “Specification for sheet metal sheet ductwork”.  Low duct pressure class shall be used.  Distance between supports of ducts shall be 2 meters.  Every branch needs a damper for regulation of air rates.  Fire dampers shall be to approval.

4.	Outdoor Grilles

Outdoor grilles shall be made of aluminium with horizontal lamella plates and mosquito screens.  Velocity through face area is for natural ventilation 1.0 m/s and for mechanical ventilation 3.0 m/s.

5.	Testing of Ventilation

All fans shall be tested to demonstrate compliance with requirements of the specifications.  Capacities of air rates shall be checked.

#### Fire Fighting

1.	Extinguishers

For switch gear rooms and control rooms portable CO2-extinguisher shall be provided, and for guard room etc. portable dry powder extinguisher.  Fire extinguishers shall be to the approval of the Project Manager.

2.	Fire Alarm

Fire alarm of approved type shall be provided and installed.

### Electrical Services

#### General Requirements

This clause covers the requirements of quality, materials, methods and measures for the design, supply and installation of electrical services in the control building and other buildings.

The low voltage AC auxiliary supply for building services shall be 50 Hz 400/231 V, 3-phase 4-wire + earth system with neutral directly earthed and with a separate PE-conductor (TN-S system).

#### Design Criteria

The electrical systems shall be designed to meet the Regulations for Electrical Installations (IEE Wiring Regulations) 15th Edition and Central African Standard Safety Code for Electrical Wiring of Premises 1964.

1.	Minimum size of wires for:

-	Lighting circuits		sq.mm.		1.5 Cu

-	Socket outlet circuits	sq.mm.		2.5 Cu

-	Telephone circuits		sq.mm.		0.6 Cu

2.	Protection classes:

-	Control and relayrooms,

Guard houses, Corridors,

Offices, Storerooms etc.			IP 20

-	Battery Rooms				IP 67

-	Exteriors					IP 23

3.	Minimum maintained in-service illumination levels:

-	Control and relayrooms,

Offices, Workshops		1x400

-	Auxiliaries, Battery rooms	1x200

-	Other rooms		1x150

-	Emergency Lighting		1x30

4.	Lighting uniformity factor			2

5.	Lighting:

There shall be at least two external lighting fixtures in each side of the Control building and one fixture over the building main entrances.

230V, 10A lighting circuits shall be installed directly from 230 V LVAC Distribution boards or separate lighting panel boards.  Panel boards shall be fed through LVAC Distribution boards.  Panel boards and their power supply cables shall be supplied under Civil works, but LVAC Distribution boards are part of Electrical works.

6.	Receptacles:

Socket outlet circuits 400/231 V shall be installed directly from LVAC Distribution board except in guard house, if any, where receptacles are fed through the lighting panel.

230 V single phase duplex receptacles shall be provided along the indoor surface of the walls of the buildings at every 5 metres of wall length.

400 V three phase single receptacles shall be provided where operationally required, but at least 2 per any operational room.

230 V single phase duplex receptacles and 400 V three phase single receptacles shall be provided along the outdoor surface of the walls, where operationally required, but at least one receptacle of each type as decided at the design stage.

#### Switches and Outlets

Flush mounting switches and outlets with separate earthing terminal shall conform to British Standard 13A, 3 square pin type.

Surface mounting switches and outlets shall conform to IEC 83 with conduit entry threads according to IEC 423 for weatherproof installations.

Lighting switches shall have minimum breaking capacity of 10 A at 230 VAC for loads with power factors of 0.5.

Outlet boxes shall be cast iron or galvanized sheet steel.

#### Lighting Fixtures

Control rooms, offices, guard houses (if any) and corridors shall be provided with lighting fixtures of 2x40 W fluorescent type with prismatic lens.  In the Control rooms they shall be low brightness type.  Workshops and storerooms shall be provided with lighting fixtures of 2x40 W. industrial type.

Exterior fixtures shall be of cast ferrous alloy type with glass prismatic lenses.

Battery room fixtures shall be incandescent type fixtures.

The 40 W fluorescent tubes shall be rapid start type and shall have a minimum operation lifetime of 10.000 hours.  The rapid start ballast shall be of high-power factor, 90 per cent or more.  They shall be equipped with a built-in non-resetting thermal protection near the core and coils.

The sound rating shall be “A”.  The ballast shall operate in ambient temperature conditions of 45 deg. C.

Emergency lighting shall be connected to the 110 V dc panels to be provided under the Electrical Works.  Emergency lighting fixtures shall be located over the exit doors to correspond to approximately 20 per cent of the total lighting.  Guard house (if any) will not be provided with emergency lighting.

Lamp holders for tungsten filament lamps shall be Bayonet Cap for 230 V for Primary lighting and Edison Screw for 100 V for Emergency lighting.

#### Telephones

Normal telephones (PABX-system) shall be installed in the controlrooms and guardhouses.

Telephone sets shall be flushmounted in lockable metalboxes.  The number, model and final location is subject to Project Manager’s approval.

#### Conduits

Conduits for building lighting, socket outlets and telephone circuits shall confirm to IEC 423.

Conduit accessories and junction boxes shall be of galvanized steel.

Conduits for damp and high humidity areas shall be galvanized.

#### Installations

The electrical system shall be installed to meet the requirements for Electrical (IEE Wiring Regulations) 15th Edition, Central African Standard Safety Code for the Wiring of Premises 1964, and good engineering practice.

Separate conduits and cables shall be provided for following the services:

- AC primary lighting

- AC power and socket outlets

- power for air conditioners

- telephone circuits

- dc emergensy circuits.

#### Earthing

Earthing system must be designed for maximum acceptable step and touch voltages of 65 V.

Building earthing systems shall be connected to substation earth with at least two earth connectors.

At cable termination points, metal sheats and armouring shall be bonded solidly.

The following parts of electrical installations shall be bonded to earth conductor:

-	Metal parts (other than current carrying parts) including conduits, distribution boards,

mechanical items, etc.

-	Earth terminal of socket outlets

-	Metal part of lighting fixtures and outlet boxes.

#### Testing

The following test shall be carried out by the Contractor at completion of electrical installation:

-	Phase rotation tests of complete installation.

-         	 Insulation tests on main cables at 1000 V, between conductors and sheets.  Minimum allowable insulation resistance is 10 megohms.

-	Insulation test to ground of all circuits with fuse links in phase and switches “on”.  Minimum allowable resistance value is 10 megohm.

-	Insulation test between conductors with lamps and current consuming apparatus removed and switches “on”.  Minimum allowable resistance value is 1 megohm.  Minimum allowable test voltage for insulation test is twice the normal voltage of supply, provided that only mV circuits are not exceeded 500 V rms.

-	Verification of polarity to ensure that fuses and single pole devices are connected to phase conductor and that outer contacts of Edison Screw lamp holders are connected to neutral conductor.

-	Continuity tests to verify continuity of conductors in every circuit.

-          Earth- loop impedance test taken at farthest point of installation to verify that current protective devices operate under earth fault conditions.

## Specific Structures

### General

This clause covers the specific requirements for design, delivery, workmanship of structures concerning substation, switchyard etc.

### Substation Area

#### Ground Network

The switchyard area shall be provided with a earthing network of copper wires.  For the wires trenches 1m deep shall be dug or a 1m thick layer of soil shall be removed depending on the prevailing circumstances.

After the installation of the wires the trenches shall be filled with suitable soil fill.  The filling shall be levelled and compacted.

#### Landscaping

Prior to the completion of major works on each substation the Contractor shall carry out landscaping of the total substation area.

The whole switchyard reaching app. one meter outside the fence shall be levelled and covered with an even layer of crushed rock as specified under “Materials for the Works”.

See also under “Earthworks”.

#### Foundations for Substation Equipment

All foundations for substation equipment (such as disconnectors, circuit breakers, post insulators, current transformers, voltage transformers, surge arresters, cable-ends etc) shall be designed and built so that they can withstand all loads without damage, distortion, or settlement.  Also the loads during the erection of equipment shall be taken into account.

The foundations shall be of type slab and chimney.  The following ground conditions shall apply:

- soil foundation

- rock foundation for hard rock

- rock foundation for weathered rock

The upper surface of concrete foundations shall come up at least 30 cm above the surface of substation.

The safety factors for foundations against overturning and uplift shall be at least 2.5.

Reinforced concrete structures shall be designed according to British Standard BS 8110:1985.

#### Cable Trenches

The cable trenches with prefabricated covers shall be made of reinforced concrete grade C25.  The thickness of bottom and walls shall be approximately 150 mm.

Trench covers of the standard type shall be designed to withstand 4 tonnes wheel load.  Where trenches are crossing internal roads, special covers shall be designed to withstand loads from heavy transports such as transformers.  See dwg.no. ZT-210.

The trenches shall have a longitudinal sloping of 2 % and drain holes at the bottom every 20 m in distance, either connected to sufficient sub soil drains or soak-away pits of min. 0,5 m3 volume at each drain point.  The soak-aways shall be filled with crushed stones as for the platform cover.  See also “Drainage and Stormwater” in this specification.

The trenches shall be laid on a well compacted gravel bed of 15 cm thickness.      The cable trenches shall be provided with steel cable supports, see dwg. ZT-210.

#### Oil Catchment Pit, Transformer Foundation

The catchment pit for transformer foundations shall be equipped with open grid steel flooring of sufficient strength to carry a 200 mm layer of stone chip.  A pump (electrical) for emptying the catchment pit shall be provided, including spares and accessories.  Ref. dwg.no. ZT-220.

The foundation shall be equipped with sufficient anchors, internal and/or external as necessary, for attachment of pulling equipment for positioning the transformer.

## Furnishing

### General

Furnishing shall be provided by the Contractor.  Size and type of furniture’s are subject to Project Manager’s approval. Only approved furniture shall be accepted.

### Control Room Furnishing

All new control rooms shall be provided with the following furnitures:

- pcs of office desks. Size 1220x610x760H.

- pcs office chairs.

- 2 pcs of stationary cupboard complete with 4 adjustable shelves.

- Lock system on the right-hand door.  Size 1930x915x475D.

- Adequately sized air conditioners

### Guard House Furnishing

All new guard houses shall be provided with the following furnitures:

- 1 pc of office desk.  Size 1220x610x760H.

- 2 pcs of simple metal armchairs.

- 1 pc of metal stationary cupboard complete with 4 adjustable shelves.

- Lock system on the right-hand door.  Size 1830x915x475D.

Toilet in Guard house shall be provided with soap dispenser, towel dispenser, toilet soap holder and mirror.

Toilet in Guard house shall be provided with soap dispenser, towel dispenser, toilet soap holder and mirror.

## Schedules for Civil Works

The following information schedules pertaining to civil works shall be filled in by the Bidders:

### SCHEDULE 1.11.1

BIDDERS EXPERIENCE

Civil Works of similar nature carried out by the Bidder

| ITEM | CLIENT | PROJECT | CONTRACT SUM | YEAR COMPLETED |
| --- | --- | --- | --- | --- |

NOTE:	The Schedule shall be filled in and submitted with the Bid.

Date:  _________________________	Bidder's Signature:  ___________________

### SCHEDULE 1.11.2

MAJOR ITEMS OF CONSTRUCTIONAL PLANT AND EQUIPMENT TO BE USED FOR THIS PROJECT

| ITEM NO. | DESCRIPTION (Type of Machine/Equipment) | NO. OF EACH | YEAR OF MANUFACTURE | ESTIMATED VALUE | CAPACITY |
| --- | --- | --- | --- | --- | --- |

Date:  ______________________________________	Bidder’s Signature _________________________________________

### SCHEDULE 1.11.3

PERSONNEL TO WORK ON THIS PROJECT

| DESIGNATION | NAME | Summary of Qualification, Experience and Present Occupation |
| --- | --- | --- |
| Key Personnel, Headquarters |  |  |
| Managing Director |  |  |
| Technical Director |  |  |
| Chief Engineer |  |  |
| Project Manager (intended for this project) |  |  |
| Other key personnel and experts to be employed at site: |  |  |
| a) Site Engineer/Manager |  |  |
| b) Foreman |  |  |
| c) Foreman |  |  |
| d) |  |  |
| e) |  |  |
| f) |  |  |
| Designer, or alternatively Civil Works Consultant |  |  |

The Bidder shall list management/key personnel responsible for the project, his own and subcontractor’s personnel, together with their qualifications, experience, and positions.  CVs shall be enclosed with the Bid.

Date:  __________________	Bidder’s Signature: __________________________

### SCHEDULE 1.11.4

SUB-CONTRACTORS

| Item | Type or Section of Works | Approximate Value | Name and Address of Sub-Contractor |
| --- | --- | --- | --- |

NOTE:	The Bidder shall enter in this Schedule the type or sections of works to be sub-contracted, and the identity of the Sub-contractors.  The Bidder, if awarded the Contract, shall remain entirely and solely responsible for the satisfactory completion of works carried out by the Sub-contractors.

Date:  _______________________	Bidder’s Signature:  ____________________

### SCHEDULE 1.11.5

SUB-CONTRACTORS' EXPERIENCE

Works of similar nature carried out by the Sub-Contractors

| Item | Client | Project | Year completed |
| --- | --- | --- | --- |

NOTE:	The Schedule shall be filled in and submitted with the Bid.

Date:  _____________________	Bidder’s Signature:  ______________________

### SCHEDULE 1.11.6

CERTIFICATE OF VISIT TO SUBSTATION SITES

THIS IS TO CERTIFY THAT I, ..........................................................................

Representative of .......................................................................................

Visited ………………………………………………………………………………………. sites on ............................................................................................................. (Date)

in the company of the Employer/the Project Manager, Mr. ................................................................................

I have carefully examined the Site and the local conditions including accessibility of necessary materials to carry out the works and have made myself familiar with the provisions of the Contract Documents.   I have made myself familiar with the local conditions likely to influence the work and cost thereof.

I FURTHER CERTIFY, and I am satisfied with the description of the work and explanations given by the Employer/Project Manager, and that I understand the work to be done.

SIGNED ..................................................

DATE	.......................................…….......

CONTRACTOR ..........................................…………........

DATE	..................................................

EMPLOYER/PROJECT MANAGER

### SCHEDULE 1.11.7

DATES FOR COMPLETION OF CIVIL WORKS

The Schedule shall be completed by the Bidder. The entered times are to be binding on the Contractor.

All periods in weeks shall show the commencement and completion for each item.

| Period in Weeks after Award of Contract for: | Weeks |
| --- | --- |
| 1. Submission of Design |  |
| 2. Approval of Design (Submission + 4 weeks provided that the design submitted is basically of acceptable standard) |  |
| 3. Earthworks for access road and platform |  |
| 4. Gantry and apparatus foundations |  |
| 5. Transformer foundations |  |
| 6. Cable trenches, earthing and drains |  |
| 7. Control building |  |
| 8. Toilet building |  |
| 9. Fencing |  |
| 10.Completion of roads including surfacing |  |
| 11.Spreading of stone layer on platform surface |  |
| 12.Other |  |
| 13.Overall completion |  |

Date:  _____________________	Bidder’s Signature:  _____________________

STEEL STUCTURE       SPECIFICATIONS

SECTION VIII CONTENT

8 PARTICULAR TECHNICAL SPECIFICATIONS: STEEL STRUCTURES SPECIFICATIONS	547

8.1 General	547

8.1.1 Location of the Works	547

8.1.2 Type of Works	547

8.1.3 Sequence of Supply	547

8.1.4 Drawings	547

8.1.5 Quality of Materials and Work	548

8.1.6 Design and General Particulars	549

8.1.7 Manufacture	550

8.2 Steel Structure Design Criteria	553

8.2.1 General	553

8.2.2 Loads on Structures	553

8.2.3 Design Temperatures	555

8.2.4 Safety Factors	556

8.2.5 Electrical Clearances	556

8.2.6 Phase Spacing	556

8.2.7 Shield Angle	556

8.2.8 Steel Structures, main dimensions	557

8.3 Design Requirements	557

8.3.1 Steel Characteristics	557

8.3.2 Members	557

8.3.3 Bolted Connections	558

8.3.4 Bolts, Nuts and Washers	558

8.4 Detailing Requirements	559

8.4.1 Member Thickness	559

8.4.2 Splices	559

8.4.3 Attachment of Insulator Strings	559

8.4.4 Miscellaneous	559

8.4.5 Ladders and Steps	560

8.5 Manufacturing Requirements	560

8.5.1 Technical Documents	560

8.5.2 Quality Assurance Program (QAP)	560

8.5.3 Manufacturing Tolerances	561

8.5.4 Manufacturing	561

8.5.5 Welding	562

8.5.6 Numbering of Parts	562

8.5.7 Galvanising	563

8.5.8 Packing, Storing and Transport	563

8.5.9 Test Program	564

8.6 Schedules for Steel Structures	565

8.6.1 SCHEDULE 2.6.1	566

8.6.2 SCHEDULE 2.6.2	567

8.6.3 SCHEDULE 2.6.3	569

8.6.4 SCHEDULE 2.6.4	570

8.6.5 SCHEDULE 2.6.5	571

8.6.6 SCHEDULE 2.6.6	572

8.6.7 SCHEDULE 2.6.7	574

8.6.8 SCHEDULE 2.6.8	576

8.6.9 SCHEDULE 2.6.9	577

# PARTICULAR TECHNICAL SPECIFICATIONS: STEEL STRUCTURES SPECIFICATIONS

## General

### Location of the Works

The location of the sites is as described under the relevant clauses in Scope of Work elsewhere in these Bidding Documents.

### Type of Works

The Works covered by this part of the Specifications include the following:

-	Design of all gantries (consisting of pylons and girders) and steel support structures necessary for the substations

-	Manufacture of steel structures

-	Galvanizing of steel structures

-       Timely delivery of steel structures to site including transport, handling, on/off loading and storage

-	All works for erection of steel structures

-	Any other works necessary for full compliance to plans and drawings approved by the Project Manager.

### Sequence of Supply

The sequence of supply of steel structures to site shall be determined by considering when the various structures actually are needed from the point of view of the overall project programme.  The Contractor shall be responsible for correct coordination.

### Drawings

Any drawings issued with these tender documents are for tendering purposes only.

Drawings for the project shall be made by the Contractor or his consultant and be to the approval of the Project Manager.

### Quality of Materials and Work

#### Quality of Materials

All materials supplied under this Contract shall be new and of the best quality and of the class most suitable for working under the conditions specified and shall withstand the variations of temperature and atmospheric conditions arising under working conditions without distortion or deterioration or the setting up of undue stresses in any part, and without affecting the strength and suitability of the various parts for the work which they have to perform.

#### Workmanship

All work, methods of work and workmanship, whether fully specified herein or not, shall be of the highest order in all respects, the generally accepted requirements and commonly recognised good practice for first-class work of the nature are to be adhered to.  All work shall be to the satisfaction and approval of the Project Manager.

#### Contractor's Quality Assurance Procedures

The Contractor shall submit for approval a programme of quality control and inspection procedure to assure that the product during manufacture and on completion complies with the specified requirements.  The programme will be considered adequate when it provides for the detection and removal of non-conforming materials during manufacture or processing where the material characteristics can be observed or measured.  The programme shall relate the quality control and inspection activities to the production cycle.  In support of the quality control and inspection programme the Contractor shall provide details of quality control and inspection facilities, together with the inspection and manufacturing control procedures available for use in the execution of the Contract.  In addition, where required by the Project Manager, the Contractor shall submit for approval well in advance of commencement of manufacture, details of fabrication processes including welding and methods of non-destructive testing.  The Contractor shall retain responsibility for quality control and inspection activities made by his sub-contractors and shall indicate on the programme which items are to be sub-contracted.

### Design and General Particulars

#### Design and Standardisation

All design carried out by the Contractor shall comply with these Specifications and shall consider all requirements of the works.  The Contractor shall be entirely responsible for all design carried out by him.  All design calculations shall be subject to the approval of the Project Manager.

The steel structures shall be designed to ensure satisfactory operation in which continuity of service is the first consideration and to facilitate inspection and repairs.  All structures supplied shall also be designed to ensure satisfactory operation under the atmospheric conditions prevailing at the Site, and under such variations of load as may be met with under the prevailing working conditions.

Except where otherwise specified or implied, the structures shall comply with the latest applicable Standards of the British Standards Institution, hereinafter referred to as BS, or to technically equivalent National standards.

Copies of any Standards proposed in substitution for BS must be submitted with the Bid accompanied where required by English translations of the appropriate sections.

#### Interchangeability of Parts

Corresponding parts of all materials shall be made to gauge and shall be interchangeable.  When required by the Project Manager the Contractor shall demonstrate this quality by inter-changing parts.

#### Drawings, Samples and Patterns

Drawings to be submitted with the Bid and drawings to be submitted for approval by the successful Bidder are specified in the Schedules.  The Contractor shall also submit any further drawings, or copies of drawings, samples and patterns at his own expense, as may be reasonably required by the Project Manager during the design, manufacture and erection of steel structures.

The Contractor shall prepare and submit to the Project Manager for approval dimensioned general and detailed design drawings of all the structures.  Drawings already submitted by the Contractor and approved by the Project Manager, and such drawings as shall be thereafter submitted by the Contractor and approved by the Project Manager shall not be departed from without permission by the Project Manager in writing.

All dimensions marked in SI units on drawings are to be considered correct, although measurements by scale may differ therefrom.

Approval of drawings shall not relieve the Contractor of his obligations to supply the structures in accordance with the Specification.

The Contractor is responsible for any errors that may appear in the approved documents.  He shall as soon as an error has been detected, deliver the corrected documents to the Project Manager for re-approval.

All legends and notes on drawings provided by the Contractor shall be in the English language in addition, if necessary, to that of the country of origin.

All drawings shall be dimensioned in millimetres (or meters) and drawn to one of the preferred scales quoted in Table 7 of BS Publication PD 6031 and on paper of the appropriate size from the International Series of A Sizes.

The dispatching of drawings and other documents to the Project Manager shall be effected by the most expeditious way of transport.

#### Guarantees and General Particulars

The steel structures shall comply with the general particulars and guarantees stated in the Schedules in this Chapter.

The Contractor shall be responsible for any discrepancies, errors or omissions in the particulars and guarantees, whether such particulars and guarantees have been approved by the Project Manager or not.

### Manufacture

#### Places of Manufacture, Sub-Contractors and Dates for Completion

The manufacturer's identity and places of manufacture, testing and inspection before shipment for the various structures shall be specified in the Schedules in this chapter and shall not be departed from without the agreement of the Project Manager.

Completion of steel structures shall be in time so as not to cause delays of the overall substation construction and erection works.

The actual dates of readiness for despatch of, and the dates for completion of the various portions of the structures shall be communicated to the Project Manager in good time.

As soon as practicable after entering into the Contract, the Contractor shall, having obtained the Project Manager’s consent in accordance with the Conditions of Contract, enter into the Sub-contracts he considers necessary for the satisfactory completion of the support structures.

All Sub-contractors and Sub-suppliers of components and materials shall be subject to the approval of the Project Manager.  Information shall be given on each Sub-order sufficient to identify the material or equipment to which the sub-order relates.

#### Work Plans and Progress Reports

Programmes and progress reports shall be provided by the Contractor in a form approved by the Project Manager.

#### Inspection and Testing

All materials used for the steel structures are subject to inspection by the Project Manager and it is the Contractor's responsibility to advise the Project Manager when equipment and materials are available for inspection, at least 2 1/2 weeks in advance.

The Contractor shall under the Contract carry out the tests as in the opinion of the Project Manager are necessary to determine that the structures comply with the conditions of this Specification.

All materials used shall also be subjected to and shall withstand satisfactorily such routine tests as are customary in the manufacture of the types of structures included in this project.

All tests shall be carried out to the satisfaction of the Project Manager and, if required, in his presence.

If testing is decided on, a test programme shall be submitted to the Project Manager for approval at least 1 month ahead of the commencement of testing.

Measuring apparatus shall be approved by the Project Manager and if required shall be calibrated at the expense of the Contractor at an approved laboratory.

The Contractor shall be responsible for the proper testing of the completed materials supplied by a Sub-contractor to the same extent as if the materials were completed or supplied by the Contractor himself.

The Contractor shall supply to the Project Manager suitable test pieces of all materials as required. If requested by the Project Manager test specimens shall be independently tested at the expense of the Contractor by an independent testing authority selected by the Project Manager.

#### Submission of Drawings

After award of Contract, the Contractor shall submit, within two months, copies of drawings and calculations to the Project Manager in triplicate for examination and approval of which one set will be returned with comments or approval.  Manufacture may start prior to complete approval of any structure but at the Contractor's own risk.

#### Spares

Any spare materials shall comply with the requirements of this Specification including compliance with the specified tests and interchangeability.

#### Packing and Transportation

All materials shall be carefully packed for transport by sea, rail and road, and in such a manner that the packing provides adequate protection against all climatic conditions experienced in transit and storage at site during the construction period.

## Steel Structure Design Criteria

### General

The structures shall be designed to provide at least the minimum phase and earth clearances, also under conditions of swing and sag.

Where typical layouts of the switchgear are shown on drawings attached to this Specification, structures shall be of the approximate general proportions given on these drawings.

All structures shall be designed to fit the actual equipment and apparatus which they shall support.

The rigidity of the structures shall be such that the alignment of the apparatus which they carry shall not be disturbed by the loads to which the structures are subjected.  Lattice girders shall be fabricated with a camber to compensate for the horizontal deflections.

Busbar dead end structures shall be designed so as to be suitable for future busbar extension.

### Loads on Structures

The assumed maximum simultaneous working loadings on the structures shall be as follows:

#### Wind Loadings

To be assumed working on the whole projected area of all conductors, insulators and apparatus carried on the structures.  For lattice steel structures the loadings shall be assumed working on 1.5 times the projected area of members on one face.  The wind load to be applied in the design shall be 765 N/m² on all surfaces, including cylindrical objects.

#### Vertical Loadings

The dead weights of all conductors, insulators and apparatus carried by the structures and of the structures themselves.  All steel members shall be designed to carry the weight of a man with a tool kit, i.e. 1.5 kN applied in the middle of members that are horizontal or slopes ±30° from horizontal.

The weight of actual conductors, insulators and apparatus to be installed, must be obtained from relevant suppliers, and/or the designers of the substation.  Dead weights need not be increased by the factor of safety in design calculations.

#### Conductor Tensions

Tension in conductors (and earthwires) acting on busbar gantries and other structures shall be in accordance with the tensions given by the substation designers.

#### Line Gantries

Transmission lines are terminated on special towers outside the substation fence.  The slack spans from terminal towers to line gantries will cause forces acting upon the line gantries as shown in the table below.

The transversal force in the design allows for an angle ±30° from perpendicular to the line gantry.

A vertical angle of ±20° is also allowed for.

Mechanical loads on line gantries, caused by slack spans from terminal towers:

ALL LOADS IN NEWTONS PER PHASE

|  | TYPE OF INCOMING LINE |  |  |  |
| --- | --- | --- | --- | --- |
| TYPE OF FORCES | 330 kV LINE |  |  |  |
|  | Conductors 2 x ACSR- BISON or equivalent | Earthwire GSW 19x2.64 |  |  |
| Longitudinally | 13,000 | 4,000 |  |  |
| Vertically | 5,000 | 1,000 |  |  |
| Transversal | 7,500 | 2,300 |  |  |

### Design Temperatures

The structures shall be designed for the following temperatures:

Minimum ambient temp.		-1°C

Maximum ambient temp.		+45°C

Minimum conductor temp.		-1°C

Maximum conductor temp.		+65°C

### Safety Factors

The safety factors to be used for design are:

| Item | Factor based on | Normal Load | Exceptional Load (Short-circuit load) |
| --- | --- | --- | --- |
| Steel structures | Yield point | 2.5 | 1.5 |
| Tubular busses | Yield point | 1.5 | 1.0 |
| Foundations against overturning or uprooting | - | 2.5 | 1.5 |

### Electrical Clearances

Electrical clearances are given under the specification for switchgear.

### Phase Spacing

The approximate phase spacing is shown on dwg.no. ZT-240.  See also specification for switchgear.

### Shield Angle

The shield angle of earthwires is given under the specification for switchgear.

### Steel Structures, main dimensions

See dwg.no. ZT-240.

## Design Requirements

### Steel Characteristics

All rolled steel sections, flats, plates and bolt and nut bars used shall consist of steel manufactured by the open hearth or other approved process.

The steel shall comply in quality and strength at least with structural steel St 37-2 according to DIN 17100 or to Grade 43A according to BS 4360.  If a steel of higher tensile grade is offered the appropriate Specification which details both mechanical and chemical properties shall be provided.  The steel shall be free from blisters, scales, laminations, or other defects.  Steel sections shall be chosen with a view to avoiding delays in obtaining material.

All bolts shall be made of one type of steel only.

The steel shall be of a quality that will not have its physical properties changed, not become embrittled by hot-dip galvanising.

### Members

Stresses in tension members shall be calculated from the net area after reduction for holes.  In case of a single angle member connected by one flange only, the net area shall be reduced by 10 %.  For connections with one bolt only, the net area shall be reduced with 30 %.  Allowable ultimate tensile stress is equal to the yield point Fy of the steel.

Redundant members supporting leg members or supporting other members shall be designed for a transverse load at each node point of minimum 1.7 % of the maximum load in the leg member or the other member respectively.

Allowable ultimate stress in tension and compression on extreme fibres is equal to the yield point Fy of the steel.

The ratio between unsupported length of a member and the relevant radius of gyration, slenderness ratio (L/r), shall not exceed:

#### Compression members		L/r

- Leg members		120

- Other members		200

- Redundant members	250

#### Tension members

### Bolted Connections

Bolts shall conform to the requirements of the next clause.

Bolted connections may have one bolt only.

Minimum bolt spacing is equal to two point five (2.5) times the bolt diameter.

The distance from the centre of a fastener hole to the end of any connected part shall not be less than two (2.0) times the bolt diameter minus five (5.0) mm and the distance to the adjacent edge shall not be less than one point five (1.5) times the bolt diameter.

The distance from the centre of a bolt to the face of the outstanding flange of an angle or other members shall be such as to permit the use of a socket wrench, in tightening the nut.

The bolt hole diameter shall be equal to the bolt diameter plus one point five (1.5) mm.

Allowable ultimate bearing stress for bolts as well as members is equal to one point zero (1.0) times the ultimate stress Fu of the steel.

Allowable ultimate shearing stress for bolts and members is equal to zero point six (0.6) times the ultimate stress Fu of the steel.

### Bolts, Nuts and Washers

Bolts shall be of Metric standard.  Connection bolts, step bolts and nuts shall conform relevant BS-EN standard or equivalent.  All bolts shall be of the same steel quality for the entire supply under this contract.

Bolts and nuts shall be of standard design.  Nuts shall be tapped after galvanizing and the threads of the nuts left bare and greased.  Washers shall be used under the nuts.  Bolt lengths shall be such as to ensure that bearing is upon the shank and not upon the thread of the bolt.  The threaded part shall end within the washer.  When installed, the bolt shall project through the nut not less than three (3) mm and not more than ten (10) mm.  Taper washers shall be used where required.

All bolts, nuts and washers shall be furnished 5 % more than the actual number required to compensate for normal field losses.

All bolts, nuts and washers shall be galvanised.

## Detailing Requirements

### Member Thickness

The material used for the gantry girders and pylons members shall not be less than 4 mm thick for members carrying calculated stress.

For small steel supports for apparatus the minimum thickness of lattice members may be 3 mm.

### Splices

Splices in all members shall be of the butt-splice or lap-splice type.

Splices of the main members shall be located immediately above horizontal members or diagonal brace connection.

### Attachment of Insulator Strings

Attachment points shall be design for fitting of shackles.  Additional service holes shall be provided in line (terminal) gantries.  Attachment points shall be designed so that eccentricities are avoided as far as possible.

### Miscellaneous

The design shall be such as to keep the number of different parts as small as possible and to facilitate transport, erection, and inspection.

Horizontal members shall be placed wherever possible so that the horizontal flange is on the top.  Pockets and depressions likely to hold water shall be avoided and, if not avoidable, shall be properly drained.

Tension members shall not be made of flats or rods.

Holes necessary for accommodating earthing counterpoise connections shall be provided on each leg of every support structure.  Holes for all required signs, step bolts etc. shall be provided on each structure as and when applicable.

### Ladders and Steps

On gantry structures one leg shall be provided with ladder of approved type.  Step bolts shall be provided for earthing masts (lightning towers).

## Manufacturing Requirements

### Technical Documents

Manufacture, supervision, and inspection shall be carried out in due order in accordance with the following documents:

1.	The Contract Agreement

2.	The approved drawings

3.	This technical specification

4.	Standards and specifications to be employed by the Contractor and approved by the Project Manager.

5.	The Contractors (or Sub-Contractors) Quality Assurance Program (QAP)

### Quality Assurance Program (QAP)

The manufacturer of the towers shall have a QAP which shall be subjected to the approval of the Project Manager.

### Manufacturing Tolerances

Manufacturing tolerances shall be in accordance with the specified and/or agreed standards.

### Manufacturing

#### Straightening and Bending

Straightening and bending of steel shall only be carried out in accordance with methods to be proposed by the Contractor and approved by the Project Manager.

Straightening and bending shall not cause any notches or other defects that would have a detrimental influence on the bearing capacity of the structure.  Straightening by local heating flame is allowed.  Stretching of the material by hammering is prohibited.

The straightening and bending of a finished welded or bolted structure requires the Project Manager’s consent in writing.  After the straightening and bending the structure shall be carefully examined.

#### Cutting

Cutting of parts shall be made so as not to cause any notches diminishing the strength or any detrimental stresses.  Cutting of section bars shall be made so that deformations are avoided.

#### Bolt Holes

Besides by drilling, bolt holes may be punched if the thickness of the material does not exceed 12 mm and the diameter of the hole is not inferior to the thickness of the material.

In other cases, the holes shall be either drilled or sub-punched and thereafter reamed or drilled.  The diameter of the die for sub-punching of holes shall be at least 2 mm smaller than the nominal diameter of the hole.

The punching shall be done by pressing, not by hitting; the punch shall fit closely to the die.  The holes shall be straight and smooth with a clean surface.  The outside dimensions of the material to be punched must not alter and the material not bend.  Burrs shall be removed. Incorrect holes may be neither partly nor wholly filled out by welding.

### Welding

#### Qualifications for Executing the Welding Work

The welding work on the structures, if employed, shall be performed with a labour management experienced in welding and with skilled welders.  The qualifications shall be testified by a certificate.

#### Execution of the Welding Work

The sequence of welding shall be such as to cause as small deformations and welding stresses as possible.

The welding shall be performed with equipment and in premises suitable for the      purpose.

Equipment shall be well suited to the type of weld to be performed so that the right quality shall be attained.

No gaps or hollows may appear in the welding into which acid may penetrate during the pickling procedure preceding galvanising.

The weld shall be ground flush to the surface in such places where the welding bulge prevents a perfect fitting of components together.

A high bulge or uneven weld surface may be levelled out by chiselling or grinding.

#### Filler Metals for Welding

Standard filler metals shall be used, and the strength class and quality shall be chosen to correspond to the base material.

### Numbering of Parts

All separate parts of structures shall be marked with the part identification number which consists of the following numbers:

-	Structure type number

-	The running number of the part in question.

The marking shall be stamped onto the part before hot dip galvanising using numbers not less than 12 mm high.  The marking shall be placed near one end in the same relative position on each part.  The marking shall be clearly visible after galvanising and be located on the outside of the structure and so that they also are visible after erection.

### Galvanising

All structure parts and components shall be hot dip galvanised in accordance with BS 729 or other appropriate standards.

-	The minimum coating mass on any individual component shall be 610 g/m².

-	Bolts, nuts and washers shall have a zinc coating not less than 305 g/m² (equal to 43 mm thickness) when galvanised according to BS 729.

The nut threads shall be cut after hot dip galvanising and thinly oiled in order to protect the threads during storage.

The zinc coating on bolt threads shall be so smooth and free from blisters, drops and projections that nuts can be screwed on with fingers.  It is prohibited to open bolt threads by cutting after hot dip galvanising.

Galvanising of steel counterpoise cable and other rods not exceeding 7 mm diameter shall be in accordance with BS 443 or other approved standard.

Galvanising defects shall be repaired as separately agreed upon with the Project Manager. Minor galvanising defects may, however, be patched by painting over with zinc powder paint. After galvanising, parts of a structure must not be welded, machined or bent.  The Contractor shall at his own expense open all bolt holes where zinc has stuck so that they conform with the aforementioned requirements.

The preparation for galvanising and the galvanising itself shall not adversely affect the mechanical properties of the coated material.

### Packing, Storing and Transport

It shall be the Contractors responsibility to pack, store and transport all the material so that their physical properties do not deteriorate.

Every delivery shall contain a complete material list, a copy of which shall be sent in advance to the Project Manager.

The costs for packing, storing, handling, transportation and customs and taxes shall be included in the tender price.

### Test Program

Before starting the manufacture, an inspection plan written by the Contractor showing the different inspection procedures shall be mutually agreed between the Contractor and the Project Manager.

The Contractor shall keep the Project Manager informed about the course of manufacture of materials and works, so that the inspection and testing can be informed in the presence of the Project Manager’s representative.

Before every inspection and test supervised by the Project Manager the Contractor shall satisfy himself that the work is in all respects in accordance with the Specification ready for inspection and testing.

Routine tests shall be performed in accordance with the relevant standards and according to instructions by the Project Manager.

Representative samples, selected at random, of all materials amongst lots ready for despatch, shall be subject to tests in order to verify their conformity with the Specification.

The tests shall be performed by the Contractor or his Sub-Contractors, and the costs are deemed to be included in relevant prices in the Bill of Quantity.

Full and complete testing of all components shall be carried out to the satisfaction of the Project Manager.

All test results shall be documented in test reports which shall be delivered in triplicate to the Project Manager within 2 weeks after the tests have been carried out.

#### Shop Assembly

One complete structure of each of the main structures (gantries) shall be manufactured for shop assembly and erected in the presence of the Project Manager if he so requires. The Project Manager will check the component parts for proper fit and ease of assembly.  Any defects shall be amended to the satisfaction of the Project Manager, before commencement of delivery.

#### Testing of Mechanical and Chemical Properties of Structure Members

Steel samples shall be taken at random amongst lots of completely galvanised structure members.  These samples shall be dimensioned and tested in accordance with DIN 17100 or BS 4360 or with other equivalent and approved standards.

#### Galvanisation Tests on Structure Members, Bolts and Nuts

The uniformity of the zinc coating on galvanised steel articles other than wires shall be tested as specified in VDE 0210/5.69, Part IV or BS 729 Part 1.

#### Welding Tests

Welding tests shall be carried out in accordance with approved standards and as directed by the Project Manager.

## Schedules for Steel Structures

The following information and guarantee schedules pertaining to steel structures shall be filled in by the Bidders.

### SCHEDULE 2.6.1

BIDDER’S EXPERIENCE

Works of similar nature carried out by the Bidder

| ITEM | CLIENT | TYPE OF SUPPLY | CONTRACT SUM | TONS OF STEEL | YEAR COMPLETED |
| --- | --- | --- | --- | --- | --- |

NOTE:	The Schedule shall be filled in and submitted with the Bid.

Date: ___________________     Bidder’s Signature:  ____________________

### SCHEDULE 2.6.2

KEY PERSONNEL TO WORK ON THIS PROJECT

| Designation | Name | Summary of Qualifications, Experience and Present Occupation |
| --- | --- | --- |
| Key Personnel, Manufacturing: |  |  |
| Factory Manager |  |  |
| Deputy Factory Manger |  |  |
| Quality Assurance Manager |  |  |
| Supervising Engineers/ Production Managers |  |  |
| a) |  |  |
| b) |  |  |
| c) |  |  |
| d) |  |  |
| Key Personnel, Design: |  |  |
| Design Manager |  |  |
| Designer |  |  |
| Designer |  |  |
| Other Staff: |  |  |

NOTE:	The Bidder shall list in this Schedule the key personnel he will employ for design and manufacturing of structures to direct and execute the work, together with their qualifications, experience and positions held.

Date:  _____________________   Bidder’s Signature:  _____________________

### SCHEDULE 2.6.3

SUB-CONTRACTORS

|  | Type or Section of Works | Approximate Value | Name and Address of Sub-Contractor |
| --- | --- | --- | --- |

NOTE:	The Bidder shall enter in this Schedule the type or sections of works to be sub-contracted, and the identity of the Sub-contractors.  The Bidder, if awarded the Contract, shall remain entirely and solely responsible for the satisfactory completion of works carried out by the Sub-contractors.

Date:  _________________	Bidder’s Signature: ___________________________

### SCHEDULE 2.6.4

SUB-CONTRACTORS' EXPERIENCE

Works of similar nature carried out by the Sub-Contractors

| Item | Client | Project | Year completed |
| --- | --- | --- | --- |

NOTE:	The Schedule shall be filled in and submitted with the Bid.

Date:____________________ Bidder’s Signature:  _____________________

### SCHEDULE 2.6.5

MANUFACTURERS AND PLACES OF MANUFACTURE

| Item | Country of Origin of Raw Materials | Manufacturer's Identity | Place of Manufacture | Place of Testing and Inspection |
| --- | --- | --- | --- | --- |
| Structure design and calculation |  |  |  |  |
| Structure drawings |  |  |  |  |
| Steel profiles |  |  |  |  |
| Bolts and nuts |  |  |  |  |
| Fabrication of structures |  |  |  |  |
| Galvanising of structures |  |  |  |  |
| Zinc |  |  |  |  |
| Other Materials: |  |  |  |  |
| a) |  |  |  |  |
| b) |  |  |  |  |
| c) |  |  |  |  |
| d) |  |  |  |  |
| e) |  |  |  |  |

Date:  __________________	Bidder’s Signature:  __________________________

### SCHEDULE 2.6.6

DATES FOR COMPLETION OF MANUFACTURE

AND SUPPLY OF STEEL STRUCTURES

The Schedule shall be completed by the Bidder.  The entered times are to be binding on the Contractor.

All periods in weeks shall show the commencement and completion for each item.

| Period in Weeks after Award of Contract for: | Weeks |
| --- | --- |
| Design to be submitted for approval |  |
| a) Main gantries |  |
| b) Other support structures |  |
| Start of manufacturing |  |
| a) Main gantries |  |
| b) Other support structures |  |
| Completion of manufacturing |  |
| a) Main gantries |  |
| b) Other support structures |  |
| Delivery on Site |  |
| a) Main gantries |  |
| b) Other support structures |  |

Date:  ________________________	Bidder’s Signature:  _____________________

### SCHEDULE 2.6.7

GENERAL PARTICULARS AND GUARANTEES

| STEEL STRUCTURE DESIGN PARTICULARS | UNIT | GUARANTEE |
| --- | --- | --- |
| Quality of steel in structures: |  |  |
| Relevant standards |  |  |
| Mild steel |  |  |
| High tensile steel |  |  |
| Maximum yield stress |  |  |
| Mild steel | N/mm2 |  |
| High tensile steel | N/mm2 |  |
| Maximum elongation of breaking |  |  |
| Mild steel | % |  |
| High tensile steel | % |  |
| Modulus of elasticity |  |  |
| Mild steel | N/mm2 |  |
| High tensile steel | N/mm2 |  |
| Quality of steel in bolts and nuts: |  |  |
| Relevant standards |  |  |
| Minimum yield stress |  |  |
| Minimum breaking stress |  |  |
| Minimum ratios of slenderness assumed in design: |  |  |
| Main members |  | 120 |
| Stressed bracings |  | 200 |
| Unstressed bracings |  | 250 |
| Minimum thickness of material | mm |  |
| Minimum bolt diameter | mm | 12 |
| Minimum thickness of members for which holes drilled | mm |  |
| Maximum thickness of members for which holes punched | mm |  |
| Minimum zinc coating |  |  |
| For members | g/m2 |  |
| For bolts and nuts | g/m2 |  |
| Whether markings stamped before galvanising |  |  |

Date:  _______________	Bidder’s Signature:  _________________________

### SCHEDULE 2.6.8

QUALITY OF MATERIALS

| TYPE OF MATERIAL | STANDARD TO BE EMPLOYED |
| --- | --- |
| Steel structure members |  |
| Steel nuts and bolts |  |
| Steel washers |  |
| Galvanising |  |
| Others: |  |

Date:  _______________	Bidder’s Signature:  _________________________

### SCHEDULE 2.6.9

SAFETY FACTORS

| MINIMUM FACTORS OF SAFETY AT ASSUMED MAXIMUM SIMULTANEOUS WORKING LOADS | GUARANTEE |
| --- | --- |
| Steel structures and foundation steelwork based on elastic limit of tensioning members and on crippling strength of compression members. Normal Loading Condition Exceptional Loading Condition | 2.5 1.5 |

Date:  _______________	Bidder’s Signature:  ___

### 3.  ZESCO PROJECT MANAGEMENT

The bidder shall be required to provide for the cost of ZESCO project management as shown below:

Item 3.1	Staff Allowances for staff for the duration of the project. ZMW 1,100, ZMW 950 and ZMW 750 per day for five staff covering the duration of the project. Refer to Project management price schedules.

Item 3.2	Rent for one house in Kitwe and Chingola districts. Household furnishings and equipment (cooker, refrigerator, sofas, beds and beddings, curtains, television, satellite decoder and dish. Pots and pans, etc) for one rented house. The same one rented house shall also be used as an office by ZESCO site personnel. The contractor shall also furnish the office with the following:

- Office table

- Office chairs

- Shelves

- Desktop computer (loaded with Microsoft office) with LCD monitor

- Four Laptop computers with preloaded software

- LaserJet colour printer (medium duty)

- Medium duty photocopier

- Digital camera

- Fax machine

- Scanner machine

Item 3.3	For vehicles, refer to Project management price schedules

The contractor shall also be responsible for payment for the following:

- Telephone and internet initial connection charge

- Bills for telephone, internet, satellite television and water for the duration of the project.

- Security services, gardener and maid.

Item 3.4 	There shall be an environmental mitigation fund for compensation of affected people. Refer to price schedules

### 4.	ENVIRONMENTAL MANAGEMENT

The Contractor shall provide for awareness campaigns and monitoring of the environmental management mitigation plan.

Item 4.1	Constructions workers` awareness campaign

a) Conservation

b) Health

Item 4.2	Awareness for settlers, small holders and commercial farmers

a) Conservation

b) Health