BIDDING DOCUMENT

___________________________________

TENDER NO. ZESCO/002/2024

TENDER FOR ENGINEERING, PROCUREMENT AND CONSTRUCTION (EPC) WORKS OF COPPERBELT NETWORK REINFORCEMENT PROJECT (LOT A) - ZESCO/…/2023 - ZESCO LIMITED

ZESCO Limited

Stand Number 6949

Great East Road

P. O Box 33304

Lusaka, Zambia

Tel: 260 211 223971

Fax: 260 211 223971

Part 3: Employers Requirements: Transmission and Distribution Lines

JANUARY 2024

PART 3A: EMPLOYERS REQUIREMENTS: TRANSMISSION LINES	8

1.	SECTION -I SCOPE OF WORKS AND SUPPLY	1

1.1.	General	1

1.1.1.	Chingola District	1

1.1.1.1	Transmission Lines	1

1.1.2.	Chililabombwe District	2

1.1.2.1	Transmission Lines	2

1.1.3.	Kitwe District	2

1.1.3.1	Transmission Lines	2

1.1.4.	Kalulushi District	2

1.1.4.1	Transmission Lines	2

1.1.5.	Mufulira District	2

1.1.5.1	Transmission Lines	2

1.1.6.	Lufwanyama District	2

1.2.	Supply of Materials	3

1.3.	Conductors and earth wires	3

1.4.	Towers	3

1.5.	Foundation Materials	3

1.6.	Insulators and Fittings	3

1.7.	Survey and Design	4

1.8.	Geotechnical Investigations and line design	4

1.9.	Access and Bush Clearing	4

1.10.	Tower Design	4

1.11.	Polymer Insulators	5

1.12.	Drawings and Documentation	5

1.13.	Training	5

1.14.	Prices	6

1.15.	Timing	6

1.16.	Factory Acceptance Tests	7

2.	GENERAL TECHNICAL CONDITIONS	8

2.1.	Extent of Supply	8

2.2.	Marking	8

2.3.	Crossing of Obstacles	8

2.4.	Corrosion Protection	8

2.4.1.	General	8

2.4.2.	Surface Protection	9

2.4.3.	Painting	9

2.4.4.	Galvanising	9

2.4.5.	Bituminous Paint	10

2.5.	Structural Steel and Cast Iron	10

2.6.	Copper, Aluminium Alloys and Clad Steel	10

2.7.	Cement	10

2.8.	Erection	10

2.9.	Electrical Clearances, General	11

2.10.	Electrical Design of 330 kV and 132kV Lines	11

2.10.1.	Electrical Characteristics	11

2.10.2.	Conductor Clearance to Ground	11

2.10.3.	Phase Spacing	12

2.10.4.	Phase to Earth Clearance	12

2.10.5.	Shield Angle of Earth wire	13

2.10.6.	Phase Angle Transposition	13

2.11.	Mechanical Design	13

2.11.1.	Insulators and Fittings	13

2.11.2.	Conductors and Earth Wire	13

2.11.3.	Tower Design	14

3.	DATA AND REQUIREMENTS FOR PHASE CONDUCTORS AND EARTH WIRES	15

3.1.	Phase Conductors (ACSR)	15

3.2.	Aerial Earth-Wires	16

3.2.1.	Aluminium Clad Steel Wire (ACS)	16

3.2.2.	Fibre Optical Earth-wire (OPGW)	17

3.2.2.1.	Standards and Codes	17

3.2.2.2.	Quality Assurance	17

3.2.2.3.	Submittals	18

3.2.2.4.	Design	18

3.2.2.5.	Field and Acceptance Testing	21

3.3.	Supply	22

4.	DESIGN REQUIREMENTS, INSULATORS AND FITTINGS	24

4.1.	Insulators	24

4.1.1.	General	24

4.1.2.	Testing	27

4.2	Insulator Sets	27

4.3	Earth Wire Assemblies	29

4.4	Fittings	29

5. MATERIAL SPECIFICATIONS FOR STEEL TOWERS	40

5.1	General	40

5.2	Materials	40

5.3	Towers for 330 kV Line In – Line Out	40

5.4	Towers for 132kV Lines	44

5.5	Design Requirements	49

5.6	Detailing Requirements	51

5.8	Manufacturing Requirements	60

5.9	Packing, Storing and Transport	62

5.10	Testing	62

6. 	MATERIAL SPECIFICATIONS, FOUNDATIONS	64

6.1	General	64

6.2	Design Requirements	64

6.3	Soil Classification	65

6.4	Foundation Loadings	66

6.5	Foundation Types	66

6.6	Tower Leg Connection and Anchorage	68

6.7	Materials	69

7. 	EARTHING AND SOIL INVESTIGATIONS	70

7.1	General	70

7.2	Earthing Arrangements	70

7.3	Measurements and Tests	70

7.4	Counterpoise Wire	71

7.5	Connections	71

7.6     Scope of Works and Specifications for Soil Investigations	71

8.	CONSTRUCTION WORKS	79

8.1	330kV and 132kV Routes	79

8.2	Profile Survey	79

8.3	Wayleaves	79

8.4	Access for Construction	80

8.5	Plan and Profile Drawings	81

8.6	Tower Plotting and Design	82

8.7	Site Inspection, Tower Locations	83

8.8	Bush Clearing	84

8.9	Crossings	84

8.10	Material Transport and Handling	85

8.11	Soil Investigations	85

8.12	Installation of Foundations	87

8.13	Concrete Work	89

8.14	Rock Anchors	93

8.15	Foundations Located in Slopes	94

8.16	Time for Foundations to Set	94

8.17	Foundation Tolerances	95

8.18	Tower Earthing	95

8.19	Tower and Steel Erection Works	95

8.20	Installation of Insulators, Conductors and Earthwires	97

8.21	Plans and Schedules	103

9. 330kV TECHNICAL SCHEDULES	104

9.2 Suspension Insulators	108

9.3 Hardware and Fittings for Conductors - ACSR	112

9.4 Hardware and Fittings for Earthwire - OPGW and ACS	116

9.5 Conductors - ACSR	119

9.6 Foundation Design Particulars	121

9.7 Soil Foundation Classification	122

9.8 Quality of Materials	122

9.9 	Earthing Materials	123

9.10 Overhead Earthwires - ACS	125

9.11 	Overhead Earthwire – OPGW	128

9.12	Deviation from Specifications	131

9.13 	Minimum Factors of Safety at Assumed Maximum Simultaneous   Working Loads	132

9.14 Assumed Maximum Working Conditions	133

9.15 Line Conductor Data and Loads	135

9.16	Earth wire Data and Loads	137

9.17 	330KV Single and Double Tower Design Particulars	138

9.18 Particulars of Tension Towers	142

9.19	Particulars of Suspension Towers	144

9.20 	Insulator Sets	145

9.24 	Drawings, calculations and Information to be submitted with the Bid	147

9.25 	Drawings and Information to be submitted with the Bid	149

9.26 	Drawings and Information to be submitted after Award of Contract	150

9.27 	As Built Documentation To Be Submitted By The Contractor	154

10. 132KV TECHNICAL SCHEDULES	155

10.1 Preliminary Information – Insulators, Vibration dampers and Tower Monopoles	155

10.2 Technical Insulators, Vibration dampers and Tower Monopoles	157

10.3 Hardware and Fittings for Conductors - ACSR	163

10.4 Hardware and Fittings for Earthwire - OPGW and ACS	166

10.5 Conductors - ACSR	169

10.6 Foundation Design Particulars	172

10.7 Soil Foundation Classification	173

10.8 Quality Of Materials	174

10.9 Earthing Materials	175

10.10 Overhead Earthwires - ACS	176

10.11 Overhead Earth wire - OPGW	178

10.12	Deviation From Specifications	183

10.13	Minimum Factors Of Safety At Assumed Maximum Simultaneous Working Loads	185

10.14 Assumed Maximum Working Conditions	185

10.15 Earthwire Data and Loads	187

10.16 Tower Design Particulars	189

10.17 Tower Design Particulars	192

10.18 Particulars of Suspension and Tension Towers	194

10.19 Insulator Sets	196

10.19 132kV Cable Particulars	199

10.20 Drawings, calculations and Information to be submitted with the Bid.	200

10.21 Drawings and Information to be submitted with the Bid	202

10.22 Drawings, Calculations and Information to be submitted after Award of Contract	204

10.23 Drawings, Calculations, and Information to be submitted after Award of Contract	205

10.24 As Built Documentation to Be Submitted by The Contractor	207

PART 3B: EMPLOYERS REQUIREMENTS:  DISTRIBUTION LINES	209

WORKS REQUIREMENTS	210

1.	WORKS REQUIREMENTS	211

1.1.	Background	211

1.2.	General	211

1.3.	Extent of Supply	211

1.4.	Scope Of Works	211

1.4.1.	Chingola District	212

1.4.1.1.	33kV Distribution Lines	212

1.4.1.2.	11kV Distribution Power Evacuation	212

1.4.2.	Chililabombwe District	213

1.4.2.1.	33kV Distribution Lines	213

1.4.2.2.	11kV Distribution Power Evacuation	214

1.4.3.	Kitwe District	214

1.4.3.1.	33kV Distribution Lines	214

1.4.3.2.	11kV Distribution Power Evacuation	215

1.4.4.	Kalulushi District	216

1.4.4.1.	33kV Distribution Lines	216

1.4.4.2.	11kV Distribution Power Evacuation	217

1.4.5.	Mufulira District	218

1.4.5.1.	33kV Distribution Lines	218

1.4.5.2.	11kV Distribution Power Evacuation	218

1.4.6.	Lufwanyama District	219

1.4.6.1.	33kV Distribution Lines	219

1.5.	Project Milestones	219

TECHNICAL SPECIFICATIONS	220

2.	TECHNICAL SPECIFICATIONS	221

2.1.	Preamble	221

2.2.	General Technical Requirements	221

2.2.1.	Scope	221

2.2.2.	Definitions and Terminology	221

2.2.3.	DESIGN AND STANDARDISATION	222

2.2.3.1.	Galvanising	223

2.2.3.2.	Aluminium and Aluminium Alloys	224

2.2.3.3.	Marking and Nameplate Labels	224

2.2.3.4.	Nuts, Bolts and Washers	225

2.2.3.5.	Cleaning and Painting	226

2.2.3.6.	Insulating Oil and Gas	228

2.2.3.7.	Prevention of Acidity	228

2.2.3.8.	Fire Protection	228

2.2.3.9.	Locking Devices and Padlocks	228

2.2.3.10.	Tools	228

2.2.3.11.	Power Cable Termination	228

2.2.3.12.	Drawings	228

2.2.3.13.	Spare Parts	229

2.2.3.14.	Erection Marks	229

2.2.3.15.	Packing of Material	229

2.2.3.16.	Shipping Marks	231

2.2.3.17.	Tests	231

2.2.3.18.	Type tests	231

2.2.3.19.	Routine tests	232

2.2.3.20.	Acceptance tests	232

2.2.3.21.	Site tests	232

2.2.3.22.	Site Conditions	233

2.2.3.23.	Overhead Line Clearances	234

2.2.3.24.	Ground Clearance	235

2.3.	Particular Technical Requirements	236

2.3.1.	GENERAL DESIGN DATA	236

2.4.	11kV and 33kV Overhead Line	237

2.4.1.	Overhead Line and Earth Conductors	237

2.4.1.1.	Overhead Line Conductor	237

General	237

Joints	238

2.4.2.	ACSR Earth Conductors	239

2.4.2.1.	General	239

2.4.2.2.	Joints and Clamps	239

2.4.3.	OPTICAL OVERHEAD GROUND WIRE (OPGW) AND ACCESSORIES	239

2.4.3.1.	General	239

2.4.3.2.	Standards	239

2.4.3.3.	OPGW Characteristics	240

2.4.3.4.	Fabrication	241

2.4.3.5.	Tests	242

2.4.4.	SUPPORTS AND FOUNDATIONS	248

2.4.4.1.	Foundations, excavations and backfilling	248

2.4.5.	WOOD POLE SUPPORTS	253

2.4.6.	OVERHEAD LINE INSULATORS	256

2.4.7.	STAYS	258

2.4.8.	ALL DIELECTRIC SELF SUPPORTING (ADSS) CABLE	259

2.5.	Technical Schedules	263

2.5.1.	Preamble	263

2.5.2.	Technical Schedule List	263

2.5.2.1.	TECHNICAL SCHEDULE FOR 33kV ZINC OXIDE SURGE ARRESTOR	264

2.5.2.2.	TECHNICAL SCHEDULE FOR ACSR CONDUCTOR	267

2.5.2.3.	TECHNICAL SCHEDULE FOR OPGW CONDUCTOR	269

2.5.2.4.	TECHNICAL SCHEDULE FOR 33KV ISOLATOR	272

2.5.2.5.	TECHNICAL SCHEDULE FOR TENSION INSULATORS	273

2.5.2.6.	TECHNICAL SCHEDULE FOR SUSPENSION INSULATORS	275

2.5.2.7.	TECHNICAL SCHEDULE FOR WOODEN POLE 14 METRES LONG MIN. TOP DIAMETER	277

2.5.3.	OTHER REQUIREMENTS FOR WOOD POLES	280

2.5.4.	Securing of nail plates	280

DRAWINGS	281

3.	DRAWINGS, DOCUMENTATION AND SAMPLES	282

3.1.	Drawings and documentation	282

3.2.	Sample Drawings	285

3.2.1.	Important Instructions to Bidders!	285

3.2.2.	List of Drawings	285

3.3.	Submittals to be attached to the Bid	286

3.3.1.	Overhead Line Submittals	286

3.3.1.1.	Drawings	286

3.3.1.2.	Documentation	286

3.4.	Submittals during contract period	287

3.4.1.	Programme of submittals	287

3.4.2.	Drawing numbers	287

3.4.3.	Overhead Line Drawings & Records	288

3.4.3.1.	Drawings to be submitted during the contract period	288

3.4.3.2.	Specific required Contractor’s Records	289

3.4.3.3.	Final Records	289

3.4.4.	Final records- General Requirements	290

3.4.5.	Installation and maintenance instructions	290

PART 3A: EMPLOYERS REQUIREMENTS: TRANSMISSION LINES

- SECTION -I	SCOPE OF WORKS AND SUPPLY

  - General

The main objective of the project is to increase the power transfer capacity to Chingola, Lufwanyama, Chililabombwe, Kalulushi, Mufulira and Kitwe Districts by reinforcing the existing transmission and distribution network. This reinforcement will allow ZESCO to supply power to customers whose power supply applications have been pending for some time. This is a turnkey contract and the Contractor’s duties as described in these bidding documents, include but are not limited to the following:

The following works will be carried out on the below-mentioned lines:

- Carry out detailed survey for all the transmission and distribution line routes outlined in the route maps under drawings section.

- Carry out detailed soil investigation for the 132kV double circuit transmission line routes outlined in the route maps under drawings section.

- Carry out bush (vegetation, trees, and anthills) clearing, validate route survey and profiling, tower spotting, conductor profiling provided.

- Construction of access roads complete with culverts where necessary.

- Design, supply, and erection of all foundations complete with stubs.

- Design, supply, and erection of suspension towers

- Design, supply, and erection of tension towers

- Supply and installation of insulators, fittings, and hardware

- Supply and stringing of conductors, complete with spacers and vibration dampers.

- Supply and stringing of earth wires and OPGW complete with vibration dampers.

- Supply and installation of earthing counterpoise wire

- Supply and installation of bolts, nuts, washers, and other materials as specified in Bill of Quantities, to the extent required to complete the line installation.

- Terminate the lines to the line bays in the respective substations.

- Carry out works to restore existing feeder roads to their original condition or better.

- Carry out environmental restoration works as per Environmental Management Plan.

    - Chingola District

      - Transmission Lines

- Construction of 31km of double circuit 330kV line from Luano 330/220kV substation to Chingola 330/132/33kV substation. The line shall be on self-supporting Steel lattice structures with double Bison conductor per phase.

- Construction of 4km 330kV lines to line in - line out of the existing 330kV Luano - Kansanshi line. The line shall be on self-supporting Steel lattice structures with double Bison conductor per phase.

- Construction of a 9km of 132kV double circuit line from Chingola 330/132/33kV substation to Refractory 132/11kV substation. The line shall be on self-supporting Steel Monopoles with single Bison conductor per phase.

- Construction of a 29km of 132kV double circuit line from Chingola 330/132/33kV substation to Nchanga 132/33/11kV substation. The line shall be on self-supporting Steel Monopoles with single Bison conductor per phase.

- Excavate, lay and terminate 6No 4km of 1Cx630mmsq, 132kV Aluminium XLPE cable for two circuit from Refractory 132/11kV substation to Nchanga 132/33/11kV substation.

- Construction of a 25km of 132kV double circuit line from Chingola 330/132/33kV substation to Kabundi 132/33/11kV substation. The line shall be on self-supporting Steel Monopoles with single Bison conductor per phase.

- Construction of a 29km of 132kV double circuit line from Chambishi East 330/132/66kV substation to Kabundi 132/33/11kV substation. The line shall be on self-supporting Steel Monopoles with single Bison conductor per phase.

    - Chililabombwe District

      - Transmission Lines

      - Construction of a 25km of 132kV double circuit line from Chingola 330/132/33kV substation to Chililabombwe 132/33/11kV substation. The line shall be on self-supporting Steel Monopoles with double Bison conductor per phase.

      - Construction of a 25km of 132kV double circuit line from Kabundi 132/33/11kV substation to Kakoso 132/33/11kV substation. The line shall be on self-supporting Steel Monopoles with double Bison conductor per phase.

      - Construction of a 10km of 132kV double circuit line from Chililabombwe 132/33/11kV substation to Kakoso 132/33/11kV substation. The line shall be on self-supporting Steel Monopoles with double Bison conductor per phase.

    - Kitwe District

      - Transmission Lines

- Construction of a 13km of 132kV double circuit line from Mwambashi 132/33kV substation to Kalulushi 132/33/11kV substation. The line shall be on self-supporting Steel Monopoles with double Bison conductor per phase.

    - Kalulushi District

      - Transmission Lines

- Construction of a 13km of 132kV double circuit line from Chambishi East 330/132/66kV substation to Mwambashi 132/33kV substation. The line shall be on self-supporting Steel Monopoles with double Bison conductor per phase.

    - Mufulira District

      - Transmission Lines

- Construction of a 14km of 132kV double circuit line from Chambishi East 330/132/66kV substation to Mufulira 132/33kV substation. The line shall be on self-supporting Steel Monopoles with single Bison conductor per phase.

- Construction of a 22km of 132kV double circuit line New Kitwe 132/33/11kV substation to Mufulira 132/33kV substation. The line shall be on self-supporting Steel Monopoles with single Bison conductor per phase.

    - Lufwanyama District

      - Transmission Lines

- Construction of a 76km 132kV double circuit tower with one (1) circuit strung on the line from Chingola 330/132/33kV substation to Lufwanyama 132/33kV substation. The line shall be on self-supporting Steel Monopoles with single Bison conductor per phase.

Each of the scope above shall include the scope for termination of the line into the respective substation line bays and integrating into the substation.

The Drawings section of the bid documents shows the line route maps and coordinates for the transmission lines in the project scope.

  - Supply of Materials

The Contractor shall supply materials as specified in the Bill of Quantities, including those materials that may not be specifically referred to but are necessary for the delivery of the whole scope of works.  The specified quantities may be varied during execution of the Contract, refer to Conditions of Contract.

  - Conductors and earth wires

The contractor is required to supply the whole quantity of the required BISON conductor for the 330kV transmission line. All 330kV transmission lines will be twin conductor per phase. Flexible spacers, rigid spacers with counterweights for jumpers, joints and dead ends, repair sleeves, vibration dampers and all conductor accessories shall be supplied by the contractor. The 132kV lines will be Bison single or double conductor per phase. Joints and dead ends, repair sleeves, vibration dampers and all conductor accessories shall be supplied by the contractor. Joints and dead ends, repair sleeves, vibration dampers and all conductor accessories shall be supplied by the contractor.

The aerial earth wires shall be ACS of which one shall be equipped with fibre optic cable as described in the Specifications, Technical Schedules, and Bill of Quantities. The contractor shall supply the earth wires for this project. Jointing and termination accessories for ACS shall be supplied by the contractor. The supply of joint boxes, tower clamps, approach cable, vibration dampers and all fittings for OPGW shall be supplied by the contractor.

  - Towers

The contractor shall supply all the tension towers and suspension towers (self-supporting) for the entire project. The supply shall include all necessary tower body parts for the 330kV single and double circuit lattice towers and 132kV double circuit steel monopoles. Bolts, nuts, and washers for all towers are deemed to be included in the tower assembly.

  - Foundation Materials

Foundation materials such as reinforcement steel, binding wire, formwork material, cement etc, shall be deemed to be included in the Bill of Materials for foundations in the erection works of foundations.

  - Insulators and Fittings

All insulators, fittings, clamps and necessary hardware for suspension and tension insulators for conductors, as well as complete suspension and tension attachment sets for earth wires shall be supplied by the Contractor.

The Contractor shall supply fibre glass reinforced silicon rubber insulators complete with associated live and dead-end hardware. All suspension and tension towers shall employ the said insulators.

  - Survey and Design

The Contractor shall submit his unit prices for profile survey and carry out the detailed line survey in accordance with the specification and as directed by the Project Manager. The line routes under the project scope shall follow, as much as possible, the attached line route maps.

The termination points for the 330kV lines shall be between the landing gantries at New Luanshya substation. The termination points for the 132kV lines shall be the landing gantries at the respective substations in Ndola, Mpongwe and Luanshya. The general line routes are as indicated on the route maps provided. The employer shall avail the contractor as part of his instructions survey data showing the coordinates of the proposed new substations, all the corners on the chosen line routes and the positions of the existing substations. The line coordinates shall serve as the chosen route for the proposed lines. The contractor must note that the obligation of the employer is to furnish bidders with CORNER POINTS ONLY for the lines. The line corner points are for the Employers’ convenience only and for execution of other works related to the project. The towers and foundation drawings provided are for bidding purposes only.

  - Geotechnical Investigations and line design

The contractor shall be responsible for geotechnical investigations, pegging, line profiling, Tower spotting, tower and foundation designs. The contractor shall also be responsible for equipment testing, procurement, shipment, delivery to sites, installation, and commissioning works.

  - Access and Bush Clearing

All access and wayleave roads, and installation of gates where necessary, shall be the responsibility of the Contractor. The Contractor shall carry out all works to make access, wayleave roads and bridges required for the construction of the line. Bush cutting and clearing, which shall include demolishing anthills and cutting down trees, as given in the specifications, shall be the responsibility of the Contractor. The costs of all roads (approach roads, obstacle bypass roads etc) and bridges required by the contractor to access the line route shall be deemed to be included in the price of the wayleave and access roads.

  - Tower Design

- 330kV Towers

The employer possesses outline drawings for 330kV Single circuit tower types AS, BT, C, D, DE, and DEF. Type AS is a suspension tower and type BT, C, D and DE are tension towers; and for the 330kV double circuit tower types 300s, 300T10, 300T30, 300T70 and 300T90. The type 300S is a suspension tower and 300T10, 300T30, 300T70 and 300T90 are tension towers. The contractor shall, as much as possible propose new detailed designs for all towers based on the outline drawings provided by the employer. Based on contractor’s proposed and subsequent approved designs, the contractor shall produce shop floor drawings for the manufacture of the tower members. The employer shall attend due diligence, type tests and factory acceptance tests for the 330kV towers in the manufacturers home country.

- 132kV Towers

- Double Circuit

The contractor shall propose new designs for the 132kV double circuit monopoles including any special towers where required. Subject to the employer’s approval, the contractor shall also produce Shop floor drawings for the manufacture of the tower members. The employer shall attend due diligence, type tests and factory acceptance tests for the 132kV double circuit towers in the manufacturers home country.

  - Polymer Insulators

The bidder shall supply fibre glass reinforced silicon rubber insulators complete with associated live and dead-end hardware. All suspension and tension towers shall employ the said insulators. The 330kV and 132kV lines shall employ polymer insulators.

  - Drawings and Documentation

The employer shall provide outline drawings and documentation for the towers in the project scope to the successful bidder. The enclosed outline drawings are for illustration purposes only.

After implementation the Contractor shall supply as part of the handover documentation all ’As built’ 5 sets of drawings and records as hard copies. Soft copies of all drawings shall be in both AutoCAD and Adobe PDF format. These shall be provided on a Hard drive.

  - Training

The Contractor shall arrange and sponsor all training activities as provided for in the project management schedule underprice schedules. The Contractor is expected to coordinate activities in such a way that reasonable time is allowed for each session.  It will be the sole responsibility of the Contractor to follow the trainer’s schedules so that the Employer does not miss any activity or is not delayed. The training details regarding number of trainees, courses and types, preferred training institute or company and timing shall be as outlined in the project management schedule underprice schedules. It is the responsibility of the Contractor to schedule all training (including traveling) so as not to coincide with project implementation works. Therefore, all training shall be scheduled as soon as possible after contract signing.

The contractor shall be required to train the employers’ staff in transmission line design and transmission line construction and maintenance works. The training for transmission line design shall cover the general design and work undertaken by the contractor on this project. The transmission line construction and maintenance training shall involve attaching the employer’s staff to the contractor on site for the duration of the contract. Part of this training shall be conducted in the contractor’s home country where applicable and as such the price for this item shall include:

  - Return airfare for the employer’s staff and

  - Accommodation and per diem for the employer’s whilst in the contractor’s home country.

The Contractor shall also plan for the employer’s staff to undertake established courses at recognised institutes in network analysis, load flow, EMT, fault and dynamic studies using DigSilent software and Transmission Line maintenance. The Contractor shall procure and supply DigSilent, PSSE, PSCAD and PLS-CADD, software licences. The Contractor shall also undertake sizing of transmission lines compensation equipment to submission and approval of conceptual designs.

The Contractor shall also arrange for employer’s staff training in World Bank Procurement procedures and World Bank project management courses.

The Contractor shall propose the training course contents as offered, after contract signing, and the Employer shall approve the details.

The contractor shall be responsible for all travel arrangements of the trainees, including accommodation, per diem and air travel.

  - Prices

The transmission line pricing shall be on a per unit basis in US dollars.

  - Timing

The Project duration shall be thirty-six (36) months and the bidder shall submit the schedule of implementation in Microsoft Project in both hard and soft copy. The schedule shall clearly show the Cash flow plan, number of construction teams and team leaders to be employed for construction. The schedule shall also clearly show the milestones for the 330 kV and 132kV line works.

The following delivery periods shall apply, based on Contract commencement date.

- Within 3 months: Procurement of employer’s vehicles, site mobilization and completion of detailed survey

- Within 6 months completion of geotechnical investigations, line profiling, tower spotting and construction bush clearing.

- Within 12 months: site delivery of transmission line insulators, stub angles, fittings, machinery for workshop, all equipment for conductor and earthwire, works, steel materials, reinforcement bars, bolts, nuts, washers, earthing materials, substations earth works, completion of foundation and commencement of tower erection works for transmission and distribution lines.

- Within 36 months: complete the construction of transmission lines

  - Factory Acceptance Tests

The Contractor shall arrange and sponsor all factory premises inspection and equipment acceptance test excursions. The Contractor is expected to coordinate activities in such a way that reasonable time is allowed for each session. It will be the sole responsibility of the Contractor to follow the manufacturer’s schedules so that the Employer does not miss any activity on the inspection or acceptance list. All the factory due diligence inspections shall be carried out before approval of sub-contractors for manufacture and supply of equipment.

It will be up to the manufacturer’s factory to demonstrate to the Employer, during inspection, their Quality Assurance system.

  - Tower Prototype

The employer shall inspect the selected tower manufacturer’s premises and factory. The Contractor shall facilitate that the employer carries out inspection of all fully assembled prototypes of tower types before tower manufacture and supply. All tower types to be supplied shall be preceded by a prototype assembly to confirm correct fitting and erection. For each voltage level, the employer shall select tower types to undergo tests and these tests shall be witnessed by the employer’s representatives.

  - Silicon Rubber Insulators:

The employer shall inspect the selected insulator manufacturer’s premises and factory and witness the Factory Acceptance testing of the insulators.

  - Bison

The employer shall inspect the selected conductor manufacturer’s premises and factory and witness the Factory Acceptance testing of the conductor.

  - Optic Fibre Ground Wire:

The employer shall inspect the selected OPGW manufacturer’s premises and witness the Factory Acceptance testing of the OPGW.

- GENERAL TECHNICAL CONDITIONS

  - Extent of Supply

The supply comprises design, procurement, manufacture, testing at works, delivery at site, erection, testing on site, commissioning, and maintenance during the Defects Liability period for the supply of steel, bolts, nuts, washers, guy wires, foundation and earthing materials, conductors, earth wire, insulators, hardware, fittings and accessories and all works related to transport and erection.

All components and accessories necessary for safe and efficient operation of the works and equipment in accordance with sound engineering practice shall be included in the supply.

All temporary access tracks for construction purposes shall be the responsibility of the Contractor, and no additional payment will be made for these tracks.

The Contractor is required to construct along the line route a permanent access track for erection of the line and for the Employer to carry out future maintenance on the constructed line. All Gazetted infrastructures that shall be damaged during construction shall be left in original or better conditions after the construction period.

  - Marking

A legible mark of origin shall be applied to all castings and forgings.  Every facility for tracing the origin of the material shall be given to the Project Manager.

All members of steel structures shall be marked with the dimension of the member.  The marking shall be applied before Zinc-coating and shall be sufficiently rough to allow for easy identification after the Zinc-coating.  The mark shall be preferably placed near one end in the same relative position of each member.

  - Crossing of Obstacles

The Contractor shall make all necessary temporary provisions and take all necessary precautions, including notifications to relevant authorities, the erection of guard structures as required where work is to be carried out in spans crossing roads, tele-communication lines, power lines, rivers, streams or other obstacles, in order to maintain the safety of the public and to avoid damage.  The Contractor shall notify the Project Manager and the owner of any such obstacle in reasonable time before making the crossing.  Power lines to be crossed will normally be taken out of service and be earthed and so remain during the time required by the Contractor to complete the Work.

Prior to making the crossing the Contractor shall obtain the Project Manager’s approval of the precautionary arrangements and installation methods intended for use, and the time required for the work.

No additional payment will be made for temporary provisions as per above.

  - Corrosion Protection

    - General

All parts of the work shall be protected against corrosion under service conditions.  The protection shall also prevent corrosion during transport, storage, and erection.

Damage to the protection during transport, erection etc. and jointing shall be repaired to the same quality as specified for the object.

    - Surface Protection

All steel and iron surface to be painted shall be prepared by means of sand or shot blasting or other approved method.

The surface shall be of clean metal and shall be dry and free from any foreign matter at the time of painting.

    - Painting

The quality and colours as well as the application of the paints shall be approved by the Project Manager. The Contractor shall submit detailed information, samples and the manufacturer’s recommendations for the paints for approval.  The painting shall be carried out in an efficient and workmanlike manner to the satisfaction of the Project Manager.

All ungalvanized external surfaces except nuts, bolts and washers which may be removed	 for maintenance purposes shall be painted as follows:

1.	A primary coat of rust-inhibiting paint with minimum thickness 10 m (0.07 - 0.09 kg/m2)

2.	Two coats of non-glossy oil and weather resisting paint, the second of which shall be applied on completion of work tests with thickness 30 m (0.13 - 0.16 kg/m2).

The coats of paint shall have different colours.

After the equipment have been erected, the priming paint shall be cleaned and repaired where necessary, and two coats of final paint shall be applied.

    - Galvanising

Except where otherwise specified all ferrous parts shall be galvanised.

Galvanising shall be applied by the hot-dip process and shall consist of a continuous coating to minimum thickness as follows:

| Item | Tolerances | Average of Specimens tested. mm | Any Individual Specimen tested. mm |
| --- | --- | --- | --- |
| Rolled steel exposed to the atmosphere only | 6 mm 7 mm | 95 115 | 85 100 |
| Rolled steel underground surface |  | 215 | 190 |
| Cast iron and malleable iron |  | 95 | 76 |
| Bolts, nuts and washers |  | 55 | 45 |

The Zinc coating shall meet the requirements according to ASTM A123, A153, A239 and A385, or relevant BS.

Minor damage to the galvanizing resulting from transportation and the like shall be repaired at site in an approved manner, e.g. by painting with an approved Zinc-rich paint, containing at least 92 weight per cent Zinc powder.

After galvanizing all members shall be dipped in a dichromate solution bath to avoid formation of white rust during storage and transportation.

Prior to bundling of steel sections, after galvanizing, all members shall be completely dry.

Where cutting, chamfering, drilling etc. is carried out on site, a Zinc rich paint shall be applied.

    - Bituminous Paint

All underground steelwork except anchor bolts, reinforcement and other steel encased in concrete, shall be painted with two coats of bitumen or bituminous paint of a type to be to the approval of the Project Manager.  The paint or bitumen shall be applied to 500 mm above ground on steel poles and to 150 mm above the upper surface of concrete where concrete foundations are used.

  - Structural Steel and Cast Iron

Structural steel shall be made by the open-hearth basic oxygen or electrical furnace process and shall comply in quality with the requirements for ASTM A36 or equivalent.  Steel of higher tensile grade if offered, shall be ASTM A572 grade 50 or equivalent.

Steel shall comply with the requirements of ASTM A143, and embrittlement tests shall be made in accordance with that specification.

If the Contractor intends to use more than one quality of steel, he will be required to take every precaution to the satisfaction of the Project Manager against any possible intermixing of different qualities during transport, storage, handling, manufacture, and installation.

Cast iron shall have a tensile strength of at least 140 N/mm2.  It shall be made from the best grey pig and scrap iron and shall be close-grained, tough, and uniform in character.

Malleable iron shall be of the black hearth type with a tensile strength of not less than 330 N/mm2.

  - Copper, Aluminium Alloys and Clad Steel

Copper and aluminium stranded conductor shall meet the requirements of IEC standards.

Specification of proposed aluminum alloys shall be submitted to the Project Manager for approval.

The preferred copper-clad steel to be supplied shall be Copperweld or equal.

  - Cement

Cement for concrete shall be Portland cement conforming to the BS standard or equivalent standard.  Weathered or congealed cement, or cement more than six months old after production shall not be permitted to be used unless otherwise approved by the Project Manager after quality test.

  - Erection

All erection work shall be planned and carried out in collaboration with the Project Manager, taking into consideration the stipulations of relevant Safety Measures, and shall be to the approval of the Project Manager.

The Contractor’s obligations regarding the provision of Contractor’s equipment are set out in the relevant Clauses of Conditions of Contract.  Regarding the supplies of electricity, water and compressed air for use in the execution of the Works, reference is made to the relevant Clauses of Conditions of Contract.

The Contractor shall provide at the site during all erection work, such labour together with qualified experienced supervision as shall be necessary for the erection work to the satisfaction of the Project Manager.  All the costs of the provision at the site of such labour and supervisory staff, together with all costs for the provision of staff during loading and unloading of the Contractor’s plant and equipment, shall be deemed to have been included by the Contractor in his price stated in the Bill of Quantities, and no extra payment of the above-mentioned costs shall be required by the Contractor nor allowed by the Employer.

All plant shall be inspected during erection and shall pass such tests as are required by the Project Manager to prove compliance with the requirements of the contract, notwithstanding earlier testing at the Contractor’s workshop.

  - Electrical Clearances, General

The minimum air clearance between any phase conductor or any live part and grounded or the phase to ground clearance shall be in accordance with Zambian regulations.

  - Electrical Design of 330 kV and 132kV Lines

The bidder shall provide designs for 330kV and 132kV to the approval of the employer using appropriate IEC standards or equivalent.

    - Electrical Characteristics

The electrical characteristics are selected to conform as far as possible with the existing installations.

|  | 330 kV | 132kV |
| --- | --- | --- |
| - Nominal voltage of a three-phase system | 330 kV | 132 kV |
| - Highest voltage of three-phase system | 363 kV | 145kV |
| - Rated Lightning impulse withstand voltage | 1300 kV | 650kV |
| - Rated frequency | 50 Hz | 50 Hz |
| - Maximum shielding angle to outermost phase conductor, in towers | 20o | 15° - 20° |

    - Conductor Clearance to Ground

The minimum clearance between line conductors and ground or other objects shall be as specified in the conditions corresponding to the 80oC, still air sag of the line conductors and with any angle of swing of the conductors from the vertical between zero and 45o, it being assumed (for simplicity) that the sag is always applicable. The clearances for 330kV are as follows:

|  | 330 kV | 132kV |
| --- | --- | --- |
| - Normal ground | 7.6m | 6.7m |
| - Road crossing | 8.25m | 6.7m |
| - Railway crossing | 13.4m | 8.55m |
| - Buildings, poles, structures, and walls, etc. Upon which a man may stand | 6.1m | 6.7m |

Where line erected under this Contract crosses over another power line, or over a telegraph or telephone wire, clearances shall be provided as laid down in the National Regulations or as may be otherwise approved.

Where obstructions of other types are met, the clearances shall be approved.

The distance from a tower-foundation to the nearest part of a road or railway shall not be less than 40 m.

    - Phase Spacing

Sufficient separation between phases is necessary to prevent swinging contacts and flashovers between conductors. The distance between conductors of dissimilar circuits on one tower shall be at least 1.15 times the distance between phases of the same circuit.

    - Phase to Earth Clearance

The minimum air clearance between any phase conductor or any live part and grounded part shall be as specified below:

| Insulator String Swing Out | Minimum Air Clearance 330 kV | Minimum Air Clearance 132 kV |
| --- | --- | --- |
| 0o | 2800 mm | 1200mm |
| 35o | 2500 mm | 1200mm |

The specified clearance between line conductors and support steelwork shall be obtained on the assumption that the conductor may leave the suspension clamp at any angle between 0o and 20o to the horizontal measured from the plane of the clamp.

330kV and 132kV Towers

Under the specified wind loadings, it shall be assumed that the jumper loops will swing transversely through an angle not greater than that stated in the Technical Schedules.  To ensure this, each complete twin jumper shall be provided with not less than two jumper weights of aggregate mass, 80 kg.  Such weights will be designed also to act as jumper spacers for twin conductor jumpers.  Where jumper insulator sets are to be provided these are to be equipped with weights of not less than 40 kg and to be to the approval of the Project Manager.

    - Shield Angle of Earth wire

The maximum shield angle of earth wire over outer line conductor shall be 20o from vertical.

    - Phase Angle Transposition

The bidder shall determine the need for roll transposition for the phase conductors and seek the approval of the Project Manager.

  - Mechanical Design

    - Insulators and Fittings

The insulators except suspension clamps, compression type dead end clamps or strain clamps, shall be designed for the same load combinations as for towers and the minimum safety factors related to the electromechanical or mechanical failing load shall be:

For all lines.

-	Normal loading			:	3.0

-	Exceptional loading			:	2.0

The safety factors shall relate to the specified mechanical load (SML) for the insulators.  Where old insulators are replaced, the new insulators shall have an electromechanical breaking strength not less than the old insulators.  Dimensions of ball and socket couplings, or clevis and tongue couplings, as the case shall be to facilitate interchanging with insulators presently installed in the network.  For the 330-kV line, to conform to previous practice in Zambia, and for interchangeability, the 120 kN insulators shall have 20 mm pin shank diameter.

Minimum factors of safety for steel fittings incorporated in the insulator sets related to guaranteed breaking load shall be the same as for insulators.

Dead end clamps and tension joints shall have a guaranteed breaking strength of not less than 95 % of that of the conductors.

    - Conductors and Earth Wire

The following design limitations shall apply to the conductors and earth wire for lines:

Phase conductor:

-	Temperature -1oC, full wind, initial tension not to exceed 26 % of the UTS.

-	Temperature +15oC, still air, final tension not to exceed 19.5 % of the UTS.

-	Final sags under maximum temperature to be calculated at +80oC.

Earth wire (GSW):

-	Temperature -1oC, full wind, initial tension not to exceed 21.5 % of the UTS.

-	Temperature +15oC, still air, final tension not to exceed 17.2 % of the UTS.

-	Temperature +80oC, still air, final sag 20 % less than the sag for conductors.

Option with ACS Earth wire:

-	Temperature + 80oC, still air, final sag 20 % less than the sag for conductors.

-	Maximum tension under worst loading condition not to exceed 40 % of UTS.

OPGW Earth wire:

-	Temperature -1oC, still air, initial sag not to exceed initial sag of conductors at -1oC.

-	Temperature +20oC, still air, final tension not to exceed 15%

of the UTS.

-		Maximum tension under worst loading condition not to exceed 40% of UTS.

    - Tower Design

The bidder shall submit tension and suspension tower designs for the lines according to his specifications to the approval of the employer using appropriate IEC/IEEE/ASCE standards or equivalent.

The towers to be used for the lines, shall during tower plotting be applied in such a way that the limitations specified in technical schedules are not exceeded with respect to wind/weight spans, ground clearances, heights and other parameters.  During tower plotting the towers shall be applied in such a way that the specified ground clearance is maintained at +80oC.  The tower plotting and setting out shall be to the approval of the Project Manager.

- DATA AND REQUIREMENTS FOR PHASE CONDUCTORS AND EARTH WIRES

  - Phase Conductors (ACSR)

The line conductors shall consist of aluminium conductor, steel reinforced, (hereinafter referred to as “ACSR”) of the cross section and having the characteristics stated in the schedule below. The conductors shall comply in all respects with the requirements of IEC 209 or other approved standards. The steel core wires shall be performed so that they remain inert when the conductor is cut. The steel core shall be covered with an approved grease of applied mass per unit length. To minimise corrosion, it is required that grease be applied during the conductor stranding process. The grease used must be recognised in the industry, commonly used for conductor greasing purposes, and must have a minimum drop temperature of not less than 180oC.

The stranding of each layer shall be as close and even as possible. The outermost layer shall be right-handed for ASCR.

The aluminium shall be of the highest purity commercially obtainable, and the contractor shall submit certificates of analyses giving the percentage and nature of any impurities in the metal of which wires are made. Precautions shall be taken during manufacture, storage, and erection of steel core aluminium conductors to prevent the possibility of contamination by copper or other materials which may adversely affect the aluminium.

In case of local damage to isolated strands of conductor during erection the use of repair sleeves of approved type may be permitted at the discretion of the Project Manager.

For the 330kV line, each phase shall comprise twin conductors per phase, disposed horizontally, with a normal centre-to-centre separation, in the span, of 450 mm. At suspension insulator sets the separation shall be reduced to 300 mm; in the middle sections of jumper connections between tension insulator sets, and in down leads from terminal towers, the separation shall be 250 mm. For the 132kV double circuit, each phase shall comprise single or double Bison conductor per phase, disposed vertically. The bidder shall provide appropriate designs to the approval of the employer for the 330kV and 132kV lines.

The ACSR conductors have the following physical properties:

| Name of Conductor | 330kV BISON | 132kV BISON |
| --- | --- | --- |
| Appropriate British Standard No. | 215 | 215 |
| Material | ACSR | ACSR |
| Cross-section | 431.3 mm2 | 431.3 mm2 |
| Overall diameter | 27.0 mm | 27.0 mm |
| Stranding Aluminium | 54 x 3.0 mm | 54 x 3.0 mm |
| Stranding Steel | 7 x 3.0 mm | 7 x 3.0 mm |
| Weight | 1450 kg/km | 1450 kg/km |
| Nominal breaking load | 120.9 kN | 120.9 kN |
| Initial modulus of elasticity | 51000 N/mm2 | 51000 N/mm2 |
| Final modulus of elasticity | 69000 N/mm2 | 69000 N/mm2 |
| Permanent elongation due to creep | 0.00038 m/m | 0.00038 m/m |
| Elongation coefficient | 19.3 x 10-6/oC | 19.3 x 10-6/oC |
| Rated DC resistance at 20oC | 0.0757 Ω/km | 0.0757 Ω/km |

Conductors are in accordance with the following IEC and BS standards:

IEC 60209	Aluminium Conductors, Steel-reinforced

IEC 60888	Zinc Coated Steel Wires for Stranded Conductors

IEC 60889	Hard-drawn aluminium wire for overhead line conductors.

IEC 61089	Round wire concentric lay overhead electrical stranded conductors

BS 215           Aluminium Conductors, Steel-reinforced

Bidders are allowed to propose other conductors with superior electrical and mechanical properties but whose dimensions and unit weight shall not introduce loadings above the design of the current towers. The mechanical and electrical characteristics of the proposed conductor shall be included in the bid. Brochures for such conductors and the applicable standards shall be included in the bid.

  - Aerial Earth-Wires

The 330kV lines shall employ two overrunning earth-wires of the Aluminium Clad Steel (ACS). One of these will be equipped with a fibre optic earth wire (OPGW). The 132kV lines shall employ single earth wire equipped with a fibre optic earth wire (OPGW).

    - Aluminium Clad Steel Wire (ACS)

The ACS Earth-wire shall be concentric-lay-stranded aluminium clad steel wire, according to IEC standards.

The earth wire shall have the following physical properties:

| Specification for ACS 7 No. 6 AWG |  |
| --- | --- |
| Material | Aluminium Clad Steel |
| Conductor Designation | ACS 7/4.11 |
| Cross-section | 93.1 mm2 |
| Overall diameter | 12.34 mm |
| Stranding Aluminium Clad Steel | 7 x 4.11 mm |
| Weight | 619.5 kg/km |
| Nominal breaking load | 101.14 kN |
| Modulus of elasticity | 158600 N/mm2 |
| Elongation coefficient | 13.1 x 10-6/oC |
| Rated DC resistance at 20oC | 0.916 Ω/km |

Manufacturing, testing and delivery of the earth-wire shall be in accordance with the following IEC standards.

IEC 1232	Aluminium Clad Steel Wire for Electrical Purposes

IEC 1089	Round wire concentric lay overhead electrical stranded conductors.

The aluminium clad steel strands of the whole conductor delivery shall all be manufactured by one and the same manufacturing process.

    - Fibre Optical Earth-wire (OPGW)

      - Standards and Codes

The OPGW and components shall comply with the requirements of the latest revision of the following Standards, Publications and Codes:

ASTM B399	Specification for Aluminium - Alloy 6201 - T81 Wire for Electrical Purposes.

IEC 60050	International Electrotechnical Vocabulary

IEC 60794 	Optical Fibre Cables

IEEE 1138	Standard Construction of Composite Fibre Optic Ground Wire (OPGW) for Use on Electric Utility Power Lines

      - Quality Assurance

It is the intention of the Employer to accept only equipment of proven design from manufacturers who have a record of successful manufacture and supply of OPGW, and hardware accessories installed in conditions like those existing in Zambia. Proof of such capability must be provided prior to award of contract. The following information shall be supplied with bids:

- Details of similar cable and hardware supplied by the same.

manufacturer and in service to date. Such details shall show date of supply, length of cable, and comments on service history.

- A detailed programme of the tests to be carried out during

manufacture.

- Details of the precautions taken in the cable design to prevent.

molecular hydrogen permeation of the optical fibres.

The Contractor shall carry out the following:

- All inspections and routine tests list in the Standards and

Publications in particular those listed in IEEE Standards 1138.

- Provide test reports of all tests carried out.

- Provide the Project Manager, for review, detailed instructions.

Giving the method to be used to make the cable splice. No work is to be carried out prior to Project Manager’s review of such instructions.

      - Submittals

Upon award of Contract the Contractor shall submit for Project Manager’s review the following data:

- . Drawings showing dimensions and details of each item of material to be.

supplied.

- . A list giving per drum, the drum number, the size of cable, the exact

length, the net weight, and the gross weight. The length shall take into

account sag, splices, drops at the splice locations, etc.

- . Sag and tension data.

- . Ensure shipping marks etc. meet the requirement of Section 8 of IEEE

Standard 1138.

Contractor shall supply type test reports and certificates of compliance with type tests stipulated in the Standards, Publications and Codes stipulated in this Section of the Specification.

Contractor shall supply manuals and instructions delineating how the installation and particularly, repair of OPGW must be affected. Full instructions for splicing shall be provided.

      - Design

The optical fibres supplied shall have dual operating wavelengths at 1310 nm and 1550 nm nominal. The fibre optic communication system will comprise of composite fibre optic overhead ground wire (OPGW) between substations and underground optical fibre cables links from each substation gantry to the termination equipment installed in the substation buildings.

OPGW on the gantry shall be insulated from the gantry structure except for a ground bonding wire at the tension assembly.

##### 3.2.2.4.1	Optical Fibre Requirements

The Optical Fibre shall have the following physical properties:

| Performance parameter |  |
| --- | --- |
| Type of propagation mode | Standard single mode (ITU-T G.652) |
| Coating diameter | > 200 m |
| Coating concentricity error | < 10 m |
| Coating non-circularity | < 5% |
| Cladding diameter | 125 m |
| Cladding diameter deviation | <=1 m |
| Mode field diameter @1550 nm | 9.3 m |
| Mode field diameter deviation | <=0.5 m |
| Finished cable attenuation | <=0.36 dB/km @1310 nm <=0.22 dB/km @1550 nm |
| Chromatic dispersion | <=3.5 ps/(nm.km) @1228-1399 nm <18 ps/(nm.km) @1550 nm |
| Cut-off Wave Length | 1100-1280 nm (measured on 2 m fibre) <=1270 nm (measured on 22 m fibre) |
| Minimum number of fibres | 24 |
| Normal temperature range | -10 ... 80oC |
| Maximum temperature < 1.0 second | 180oC |
| Lifetime expected | 40 years |

##### 3.2.2.4.2 Optical Fibre Ground Wire Requirements

The OPGW shall have the optical fibres embedded within the earth-wire and shall be totally protected against moisture. The fibre design shall preferentially be based on the loose tube method of fibre protection, whereby the fibre tubes and interstices shall be filled with water repellent compound. The fibres in the tube shall be of different colours. The fibre must be protected from wind induced, vibration, mechanical forces, both during installation, operation and service, strain and extreme temperature exposure caused by short circuit currents through the wire.  The fibres must remain strain free throughout installation, operation, and service.

The OPGW shall have the following physical properties:

| Performance parameter |  |
| --- | --- |
| Maximum outer wire diameter | 15.0 mm |
| Minimum static bend diameter | 350 mm |
| Minimum Ultimate strength | 48 kN |
| Minimum delivery length per drum | 4.0 km |
| Normal temperature range | -10 ... 80oC |
| Maximum temperature < 1.0 second | 180oC |
| Short time current | 10 kA |

To minimise crevice corrosion between the conductor wires, the wires themselves must be a minimum diameter of 3 mm, and the use of conductor grease is required. A minimum of 2 layers of wires is required, and the fibre tube shall not be in the outset layer. The grease used must be recognised in the industry, commonly used for conductor greasing purposes, and must have a minimum drop temperature of not less than 180oC. The wires shall be aluminium clad steel (ACS) and/or aluminium alloy.

The sag and tension of OPGW shall meet the requirement stated in Clause B2.4.2. At all temperatures under both “initial” and “final” conditions, the sag shall be less than or equal to the sag of the phase conductors. The maximum initial and final everyday tensions (20oC, no wind) shall be limited to these values that ensure that fatigue damage due to vibrations does not occur for the service life of the transmission line. If these limits are exceeded, then suitable dampers shall be supplied.

The length of OPGW as set out in the Bill of Quantities is based on the horizontal line length. The Contractor shall make allowance for sag, terrain variations, jumpers, downlead to joint boxes, splices, and wastage etc. within the quoted price.

##### 3.2.2.4.3   OPGW Fittings

The Contractor shall design and furnish all associated OPGW hardware and accessories required for a complete operational OPGW. This shall include, but not be limited to vibration dampers, suspension tower hardware, dead end tower hardware, joint boxes, ground bonding leads to tower and down lead tower attachment hardware. Hardware and fittings which avoid any lateral crushing of the cable must be employed.  Helical preformed fittings or similar, which apply pressure radically around the cable thus avoiding crushing forces which may distort or deform the OPGW optical unit are to be used.  Contractor shall ensure no degradation of fibre transmission quality will occur due to the use of the fittings and hardware proposed.

All joints in optical fibre shall be arc fusion welded and each complete splice shall be housed in a protective, weatherproof splice box mounted on the tower legs a minimum of 5 m above ground level. The joint boxes shall have the capacity for up to minimum 24 single fibre splices and shall store excess fibre for at least 1 resplicing.  Convenient elastic hooks shall be used to snap organisers into a stack.  The box shall include all the accessories needed such as splice holders, strain relief devices and self-adhesive labels. The material of the box shall be equipped with brackets for tower mounting and made of acid-proof stainless steel and shall be covered for outdoor use. The lifetime of the joint boxes shall be longer than that of OPGW.

An extra length of approximately 1.5 m of OPGW shall be left around the box for repeat splices. Cable to and from the splice box shall be attached to the tower at approximately 1m intervals. The cable bushings shall have diameter adjusted to the OPGW and be waterproof.

Sectioning of the OPGW cable and splicing of the optical fibres shall generally be arranged on dead-end towers but where necessary this may be carried out on other towers providing that such towers are capable of withstanding additional stringing loads. This shall be subject to review by the Project Manager. No mid-span joints shall be allowed in the OPGW under any circumstances.

##### 3.2.2.4.4   Optical Fibre Cable

An underground optical fibre cable shall be supplied and laid from the OPGW cable on the substation gantry to the telecommunication equipment room. The cable shall be non-metallic but suitable for direct burial. To prevent damage to the cable during maintenance work in the cable trenches the optical fibre cable shall be laid in suitable metallic ducts. The contractor shall supply and install these ducts according the referred to acceptable standards for such works.

##### 3.2.2.4.5   Optical Fibre Joint

a)	Description of Work

- Dismantling of the fibre cable ends

- Fusion splicing at the ground

- Testing and printing out every approved splice

- Installation of joint boxes on the tower legs

- Winding up the joint ends and mounting them into the boxes

- Fastening the OPGW to the tower leg

- Laying and splicing of optical fibre cable from the OPGW on the substation gantry to the telecommunication room

- Installation of optical fibre termination cubicles complete with optical patch panels in the telecommunications rooms.

b)	Requirements

- The splice boxes shall withstand the environmental requirements.

- The splice boxes shall have white or light colour.

- All splice boxes shall be covered by a white metal shield for sun and shot protection.

- All splices shall be documented on PC file and print out including attenuation and monitor picture.

- Splice attenuation shall be better than 0.02 dB.

- Splice protection sleeves shall be provided.

#### 3.2.2.5	OPGW Installation

Contractor shall install the OPGW according to the requirements of IEEE Standard 1138.

To ensure the OPGW is installed correctly Contractor shall ensure the following is adhered to while installing OPGW:

To prevent twisting of OPGW during installation 3 anti-twist counterweights shall be installed from a flexible tube section at the lead end of OPGW while installing. Counterweights shall be capable of flexing longitudinally to allow passage through sheaves but shall be rigid in the lateral direction.

Minimum bending radius of OPGW during installation is 350 mm.

Contractor shall ensure the OPGW is properly spliced as required. Carry out tests during installation to ensure the quality of the splices is adequate as specified herein, and continuity of the fibres is ensured. Contractor shall obtain his own equipment for splicing fibre optic cable and carrying out tests. Test equipment may be retained by Contractor at the end of the project. One complete set of splicing equipment and test set shall be provided to the Employer. The cost of this splicing set shall be deemed to be included in the contract price.

      - Field and Acceptance Testing

All field and acceptance tests shall be carried out in accordance with IEEE Standard 1138 and shall be successfully completed prior to the cable commissioning.

Field and acceptance testing insofar as the OPGW itself is concerned shall consist of proving the installation provided by the Contractor has fibres which meet the specifications, and which are optically continuous from one end of the OPGW to the other.

The length of OPGW earth-wire as set out in the Bill of Quantities is based on the horizontal line length between the terminal towers plus two percent for sag, terrain variations, jumpers and cutting.  Any additional lengths required for jointing, lead-down in towers/terminals or for other reasons shall be included in the unit rates and will not be subject to additional payments.

##### 3.2.2.6.1	Type Tests

The Contractor shall furnish certified type test reports for the OPGW systems. Copies of certified results for type tests carried on the optical fibres shall be presented as part of the bid. The type tests shall be according to the relevant ITU, IEC or IEEE standards and shall include the following tests:

- Water ingress.

- Tensile performance.

- Crush.

- Aeolian Vibration.

- Galloping.

- Sheave.

- Creep.

- Stress – Strain

- Impact.

- Temperature cycle.

- DC Resistance.

- Short Circuit.

- Lightning

        - Factory Acceptance Tests (FAT)

Factory acceptance tests shall take place at the supplier’s premises after all the pieces of equipment have been assembled and in a state in which they will be installed. The Contractor shall notify the employer at least four weeks before the equipment is ready for shipment so that the employer can arrange personnel to participate in the factory testing of optical fibre systems. No equipment shall be shipped before the factory acceptance tests.

The supplier shall submit a comprehensive factory test procedure to the employer four weeks before the FAT for approval. The employer reserves the right to seek clarifications on the submitted procedure and add any other possible tests to the test procedures before approving it. The FAT shall be according to the relevant ITU, IEC and IEEE standards which shall be stated by the Contractor. The FAT shall be carried out on at least the following:

- OPGW.

- Optical Fibre Approach Cable.

- OPGW Fittings including joint boxes.

All the FAT will be witnessed by ZESCO staff. The Contractor shall make all necessary arrangements for ZESCO personnel to witness the FAT.

  - Supply

The length of conductor as set out in the Bill of Quantities is based on the horizontal line length. The Contractor shall make allowance for sag, terrain variations, jumpers, and wastage etc. within the quoted price.

All conductors, earth wires and accessories shall be supplied by the contractor. No materials shall be supplied by the Employer.

The conductors shall be supplied on drums of approved material in accordance with B.S 1559 or other approved standard construction to enable the conductors to be run out smoothly, and in lengths as long as can be conveniently handled and erected. Drums shall be marked with type, size, and length of conductor on the drum, project no. address of employer and with an arrow to show the correct direction for rolling from place to place. Wooden drums and battens shall be preserved by an approved method against fungal and termite attack. Plastic or equivalent material is to be provided between conductor and the reel and lagging. Fibreboard lagging is acceptable provided it is placed between flanges of reel; otherwise, wood lagging is required. Reels shall be of a quality to stand up to outdoor storage in a tropical climate.

Empty conductor drums where not returnable to the manufacturer’s works shall be deemed after use to be the property of the contractor who shall be responsible for their disposal.

- DESIGN REQUIREMENTS, INSULATORS AND FITTINGS

  - Insulators

    - General

For this contract silicone composite insulators shall be used. The insulators of IEC designation CS (120) B16S16-1340/9112-AL shall be used.

The insulators shall conform to the latest revision of the standards listed below, which shall be verified by a type certificate issued by the manufacturer.

IEC Publication 60060		High Voltage testing techniques

IEC Publication 60120       Dimensions of ball and socket couplings of string insulator units.

IEC Publication 60305         Characteristics of string insulator units of the cap and pin type.

IEC Publication 60372-1        Locking devices for ball and socket couplings of string insulator units. Part 1: Dimensions and general requirements.

IEC Publication 60372-2	Locking devices for ball and socket couplings of string insulator units. Part 2: Tests

IEC Publication 60372	Locking devices for ball and socket couplings of string insulator units:

Amendment 1			Dimensions and tests.

IEC Publication 61109	Composite Insulators for Insulators for A.C Overhead lines with a nominal Voltage greater than 1 kV – definitions, Test methods and Acceptance Criteria.

IEC Publication 437		Radio interference test on high voltage insulators.

IEC Publication 575		Thermal-mechanical performance test and mechanical performance test on string insulator units.

IEC Publication 60455		Specification for solventless polymerisable resinous compounds used for electrical insulation.

IEC Publication 61467 (1997-02)	Insulators for overhead lines with nominal voltages above 1000V – AC power arc tests on insulator sets.

IEC Publication 61466-2 (1997-02)	Composite string insulator units for overhead lines with a nominal voltage greater than 1000V, part 2 standard strength classes and end fittings.

IEC Publication 60071-2 (1996-12)	Insulation coordination, Part 2.

IEC Publication 60815 (1986-05)	Guide for the selection of insulators in respect of polluted conditions.

ISO/R 1101/1, 1969	Tolerances of form and of position. Part 1: Generalities, symbols indication on drawings.

It is the Contractor’s responsibility to maintain close and constant liaison between the manufacturer of insulators and the manufacturer of fittings, so that all component parts of an insulator string are perfectly adapted to one another.

All materials, whether fully specified herein or not, shall be of first-class quality and shall conform to the best modern practice and comply in all respects with these specifications.

All materials shall be free from foldability, and other exterior and interior defects which can affect its strength, ductility, durability, or ability of function.

All materials shall be inspected in full to prove compliance with requirements of the Specifications to the satisfaction of the Project Manager. The testing shall be carried out in accordance with relevant standards approved by the Project Manager.

Weather sheds and sheath material shall be 100% silicone-based polymer-based material. The weather sheds shall withstand the effects of saline atmosphere, oxygen, and ultra-violet for a minimum period of 35 years.

End fitting material shall be forged steel, hot-dip galvanised and shall be permanently sealed to prevent moisture and foreign materials from entering the end fitting-rod interface.

Rod material shall be vinyl ester or epoxy with an electrical grade glass fibre matrix and manufactured by pultrusion processing.

### 4.1.2	Dimensions and Tolerances

Dimensions and tolerances shall comply with the values recommended in IEC 305.

Dimensions and tolerances of ball and socket coupling shall comply with those recommended in IEC 120.

Internal heights of socket coupling shall comply with IEC 372-1.

Dimensions and tolerances of holes for split-pins shall comply with the values recommended in IEC 372-2.

Dimensions and tolerances of split-pins shall comply with those recommended in IEC_372-1. W-clips are not acceptable.

### 4.1.3	Electrical Requirement

The electrical requirements of the insulator units shall be as stated below.

The type test shall be performed on several insulators as stated in Annex A and be in accordance with the relevant IEC standards.

The noise level shall not exceed 60_dB over 1 V at 245kV test voltage and 500_kHz measuring frequency.

The insulators shall have some form of protection against corona cutting. Corona rings are preferred.

### 4.1.4	Mechanical Requirements

The mechanical requirements of the insulator units shall be as stated below.

Electromechanical or mechanical failing load test shall be performed in accordance with IEC 383, amended as follows:  The test load shall be increased from an initial value which is equal to about 75% of the specified minimum failing load at a rate of 15 to 30% of this failing load per minute.  In the electro-mechanical failing load test, it is required that puncture shall not occur before mechanical breakdown.  Before the electromechanical failing load or mechanical failing load test, the insulators shall have passed the temperature cycle test specified in IEC 383.  The criteria as stated in Annex A shall be fulfilled.

Thermal-mechanical performance test in accordance with IEC 575.

### 4.1.5	Materials

All materials, whether fully specified herein or not, shall be of first-class quality and shall conform to the best modern practice and comply in all respects with these specifications.

All material shall be free from folds, cracks and other exterior and interior defects which can affect its strength, ductility, durability, or ability of function.

All material shall be inspected and tested in full to prove compliance with the requirements of the Specifications to the satisfaction of the Employer or the Project Manager. The testing shall be carried out in accordance with relevant standards approved by the Employer or the Project Manager.

### 4.1.6    Component Parts

Insulating parts shall be of silicon rubber in accordance with the relevant IEC standards.  Caps shall be made of malleable cast iron, spheroidal graphite cast iron, or forged steel. The graphite in malleable cast iron shall only appear in the form of temper carbon, and the graphite in spheroidal graphite cast iron shall only be present in spheroidal form.

Pins shall be made of forged steel. In tensile tests the pins shall exhibit ductile fractures characterized by a considerable contraction of area.

Caps and pins shall be hot dip galvanised.

Split-pins shall be made of copper alloy or stainless steel and shall comply with the requirements specified in IEC-372-1.

### 4.1.7	Assembly

The verification of dimensional requirements of the insulator units shall be as stated below.

The type tests shall be performed on several insulators as stated in Annex A.

When gripping the insulator between a ball (dummy) and a socket end (dummy), the radial run-out of the insulating part shall not exceed 3% of the nominal insulator diameter.

With the same arrangement, the axial run-out of the insulating part shall not exceed 4% of the nominal insulator diameter. The axial run-out shall be measured at the periphery of the insulating part. For definitions, see ISO/R 1101/1, 1969.

Assembly shall be performed in such a way that the mechanical properties cannot be affected by the zinc and to ensure that the insulating part is not subject to any mechanical stress due to pressure exerted by the bottom edge of the cap.

The verification of the locking system shall be performed in accordance with IEC 383 on a

number of Insulators.

### 4.1.8	Marking

Each insulator unit shall be marked with the name or trademark of the manufacturer and the year of manufacture in accordance with IEC 383. In addition, each insulator unit shall be marked with the specified electromechanical or mechanical failing load in conformity with IEC 383, or the first part of the designation in accordance with IEC 305.

    - Testing

### 4.1.10	 Packing

Insulators shall be packed in crates accessible by material handling machines (2-way entry).

The packing shall afford adequate protection for insulators during ordinary handling and shipping.

Each package shall be marked with manufacturer name, number of units and catalogue number, as well as Employer’s name and destination in Zambia.

The packing, storage, transportation to site, onsite handling, installation, care during stringing, and pre-commissioning inspection should be handled according to the recommendations set forth by CIGRE SC 22, WG 03 and Section 10 of ANSI/IEEE 987-1992.

Each package shall be marked with the type of designation used by the manufacturer.

### 4.1.11 Experience

Only insulators made by competent manufacturers with a continuous production record, of composite insulators for the required voltage applications of at least 10 years will be acceptable. Bidders shall submit full details of the proposed insulators, type test certificates, details concerning the manufacturer and listing of previous purchasers of the proposed manufacturers’ composite insulators.

4.2	Insulator Sets

### 4.2.1	 General

The insulator sets shall conform to the latest revision of the standards below, which shall be verified by a type test certificate issued by the manufacturer.

IEC Publication 60060		High voltage testing techniques

IEC Publication 60120	Dimensions of ball and socket couplings of string insulator units.

IEC Publication 60305	Characteristics of string insulator units of the cap and pin type.

IEC Publication 60372-1	Locking devices for ball and socket couplings of string insulator units. Part 1: Dimensions and general requirements.

IEC Publication 60372-2	Locking devices for ball and socket couplings of string insulator units. Part 2: Tests

IEC Publication 60372	Locking devices for ball and socket couplings of string insulator units:

Amendment 1 Dimensions and tests.

IEC Publication 61109	Composite Insulators for Insulators for A.C Overhead lines with a nominal Voltage greater than 1 kV – definitions, Test methods and Acceptance Criteria.

ISO/R 1101/1, 1969		Tolerances of form and of position. Part 1: Generalities, symbols indication on drawings.

### 4.2.2 Electrical Requirements

The electrical characteristics of the insulator sets shall be as stated below:

Nominal voltage					 330kV	           132kV

Highest voltage					 363kV            145kV

Power Frequency withstand wet			 580kV	           275kV

Switching impulse withstand voltage		 	 850kV	           650kV

Dry lightning impulse withstand voltage		 1300kV            750kV

Frequency					            50 Hz	              50Hz

Insulator strings and accessories shall be designed so that, when installed, no visible corona discharges appear at the 330kV system voltage for 330kV, and at 132kV system voltage for 132kV.

The corona extinction voltage shall be at least 1.15 times the highest system voltage level when lowering from a level with visible corona.  Radio interference tests of the complete insulator sets shall be performed in accordance with IEC Publication 437.  The noise level shall not exceed 60_dB over 1 V at 245 kV test voltage and 500kHz measuring frequency for 330kV system. Appropriate standards shall also be applied and used for 132kV.

### 4.2.3	 Suspension and Tension Insulator Sets

The following suspension and tension insulator set and assemblies shall be used in accordance with the tender document:

- Suspension Set

The suspension sets shall consist of composite insulators with end fittings, shackle and suspension clamp dimensioned for ACSR-BISON conductor including armour rods. These shall be applicable to suspension for the 330 kV and 132kV

- Tension Set

The tension sets shall consist of double tension insulators with end fittings and all other necessary fittings including attachment to tower and tension clamp, as well as jumper clamp. These shall be applicable to tower types of BT, C, D, DE and G for 330kV single circuit and 300T10,300T20,300T30,300T70 and 300T90 330kV double circuit towers.

Each insulator sets i.e., tension and suspension shall be equipped with suitable arcing horns to the approval of the Project Manager.

Dimensioned insulator assembly drawings for the 330kV lines and 132kV line shall be submitted with the Bid and be to the approval of the Project Manager.

The complete insulator set, shall be subjected to power frequency and impulse withstand test in accordance with IEC Publications 60 and 383.

### 4.2.4 Pollution Level

The environmental pollution level for the 330kV line and 132kV line can be considered to range from medium to heavily polluted and the minimum creepage distance shall be 31mm/kV.

4.3	Earth Wire Assemblies

The tension clamps shall develop a holding force not less than 95 % of ultimate strength of the earth wire without causing slipping of, or damage to the earth wire or any part thereof in accordance with BS 3288.

The Bidder shall submit with his bid dimensioned drawings of the suspension and tension sets.

The tension assembly to be attached to the tower shall comprise an adjustable device for trimming the wire tension.

4.4	Fittings

### 4.4.1   General

Clamps and fittings shall be of a design approved for the relevant conductor.

All hardware shall at least provide ultimate strength as described in General Technical Conditions.

Connecting attachments, including bolts, nuts, and washers, shall have a minimum breaking strength not less than the assembly in which they will be incorporated.

All materials, whether fully specified herein or not, shall be of first-class quality and shall conform with the best modern practice and comply in all respects with these specifications.

All material shall be free from folds, cracks and other exterior and interior defects which can affect its strength, ductility, durability, or ability to function.

All material shall be inspected and tested in full to prove compliance with the requirements of the Specifications to the satisfaction of the Employer or the Project Manager. The testing shall be carried out according to the relevant standards approved by the Employer or the Project Manager.

BS 3288	Insulator and conductor fittings for overhead power lines.

Part 2: Specifications for a range of fittings.

ASTM A 153	Zinc coating (hot dip) on Iron and Steel hardware.

The tension insulator sets for twin Bison or equivalent for 330kV line shall be equipped with devices for individual adjustment of the sags of the sub conductors in each phase.

### 4.4.2	   Splices

Phase conductor

The splices shall be of the compression type and shall consist of two parts, one of galvanised steel for the steel core and one of aluminium alloy for the aluminium part of the conductor.

All splices shall develop at least 95% of the ultimate strength of the phase conductor in accordance with BS 3288.

The resistance of all splices shall not be more than 50% of the resistance of the conductor itself on the same length as the splice.

The splices shall be filled with grease after compression to protect the conductor against corrosion.

Overhead earth wire (ACS)

The splices shall be of the compression type and shall consist of two parts, one of galvanised steel for the mechanical strength and one of aluminium alloy for the conductance.

All splices shall develop at least 95% of the ultimate strength of the overhead ground wire in accordance with BS 3288.

The resistance of all splices shall not be more than 50% of the resistance of the conductor itself on the same length as the splice.

Fibre Optical Overhead Earth-wire

Welded splicing joint technique shall be employed.

The OPGW joints shall be spliced and protected efficiently in joint boxes mounted on the lower part of the tower.  The joint boxes shall have the capacity for up to minimum 48 single fibre splices and shall store excess fibre for at least 1 resplicing.  Convenient elastic hooks shall be used to snap organisers into a stack.  The box shall include all the accessories needed such as splice holders, strain relief devices and self-adhesive labels.  The material of the box shall be equipped with brackets for tower mounting and made of acid-proof stainless steel and shall be covered for outdoor use.

The cable bushings shall have diameter adjusted to the OPGW and be waterproof.

### 4.4.3	 Repair Sleeves

The repair sleeves shall be of the compression type. The compression repair sleeve shall preferably be two-piece type.

When properly applied, such repair sleeves shall achieve 95% of the ultimate strength of the conductor when one third of the aluminium wires of the outer layer is damaged in accordance with BS 3288.

The resistance of the repair sleeves shall not be more than 50% of the resistance of the conductor itself on the same length as the repair sleeve.

The repair sleeves shall be greased to prevent the conductor against corrosion.

    - Tension Clamp

      - Phase conductor

Tension clamps shall be of the compression type comprising an aluminium compression body together with an integral lug for connection of the jumper terminal and a steel compression eye.

Due consideration shall be given to cold flow characteristics and contact area requirements of connectors and conductors.

Bolts shall be used as clamping devices only and not as current carrying parts. All bolts, nuts, and washers shall be of high strength galvanised steel.

When installed, the assembly shall develop a holding force not less than 95% of the ultimate strength of the conductor without causing slipping of, or damage to the conductor or any part thereof in accordance with BS 3288.

The current carrying capacity of the tension clamp shall be equal to, or better than that of the conductor.

The tension clamp shall be connected to the live end of the tension insulator string so as to ensure adequate flexibility.

The tension clamps shall be greased to protect the conductor against corrosion.

      - Overhead earth wire

Tension clamp shall be of wedged type or compression type.

When installed, the assembly shall develop a holding force not less than 95% of the ultimate strength of the ground wire without causing slipping of, or damage to the wire or any part thereof in accordance with BS 3288.

      - Fibre Optical Overhead Earth-wire (OPGW)

Fittings which avoid any lateral crushing of the cable must be employed.  Helical preformed fittings or similar, which apply pressure radially around the cable thus avoiding crushing forces which may distort or deform the OPGW optical unit must be used.  All fittings have to be tailored to match the proposed OPGW.

### 4.4.5	 Jumper Terminal

Jumper terminals are included in this contract and shall be of the compression type comprising an aluminium compression body together with an integral lug for connection purpose.

The resistance over the tension clamp and the jumper terminal shall not be more than 50% of the resistance of the conductor itself on the same length as the tension clamp and jumper terminal.

The jumper terminals shall be greased to protect the conductor against corrosion.

### 4.4.6   Suspension Clamp

The suspension clamps shall be designed to accommodate conductor equipped with armour rods.

The suspension clamp shall be light and free to pivot in the vertical plane. The pivoting centre shall be close to the conductor axis. The conductor groove shall be bell-mouthed at both ends. The groove shall be free of burrs and edges. It shall be tailored to suit the conductor for a turning angle of at least 25°.

Clamping pressure on the conductor shall not be applied near the ends of the supporting groove of the clamp where conductor bending stresses are high. Clamping bolts shall be provided with locking devices.

The minimum failing load of suspension clamps shall be at least 2.5 times the maximum working load due to installation, wind, or broken conductor condition. The suspension clamp shall prevent the conductor from slipping through the clamp due to the load of broken conductor condition.

The suspension clamp shall be designed to withstand thermally and mechanically the short circuit current of 20 kA for 1 second.

Any visible or audible corona must not arise on the suspension clamp at the highest system voltage. The edges of the suspension clamp shall be rounded to minimise micro spark and accompanying radio interference.

It is desirable to use non-magnetic materials to keep the iron losses small. All ferrous parts apart from those made of stainless steel shall be protected by hot-dip galvanising.

The clamp design shall be such as to permit the installation of an additional device for the suspension of counterweights where required.

### 4.4.7 Vibration Dampers

Conductors and earth wires shall be provided with vibration dampers of the Stockbridge type to dampen effectively Aeolian vibrations at frequencies ranging between 5 Hz to 60 Hz.

The dampers shall withstand without any permanent deformation or damage to the conductor and the damper itself due to vibrations.

The dampers shall be free from visible or audible corona must not arise on the suspension clamp at the highest system voltage. To minimise micro spark and accompanying radio interference, the edges of the dampers shall be rounded.

The damper clamps shall be of aluminium alloy. The conductor seat shall be smooth and free from irregularities. The damper clamp shall have sufficient grip to maintain the dampers position on the conductor without damaging the conductor or causing premature fatigue damage on the conductor under the clamp. The clamp grip must not be impaired by conductor vibration. The clamp fastening system shall cope with the loosening effects of conductor vibration. All fastenings shall be self-locking.

The dampers shall be designed for live line installation.

The number of vibration dampers listed in the price schedules is provisional.

The Contractor shall present the manufacturer's application data of the dampers he will provide. The exact quantities of dampers required will be based on the application data. The bid shall include drawings of vibration dampers proposed for the project complete with technical details.

### 4.4.8	Arcing Horns

Both ends of the suspension and tension insulator sets on the whole length of the line shall comprise arcing horns of approved design.

The live ends of all suspension and tension insulator sets shall comprise arcing horns of approved design.

The arcing horns shall be of mild steel or aluminium and have the necessary dimensions to reduce, as far as possible, damage when flash-over-occurs.

The arcing horn on the live end shall have sufficient diameter to prevent the cause of visible corona and/or radio interference.

The arcing horn on the live end of the suspension sets shall withstand a mass of 150 kg applied at the tip.

The construction of the arcing horns shall comply with the following requirements:

- Arcing horns shall effectively protect the insulators and the fittings from damage due to an arc.

- Arcing horns shall effectively improve the voltage distribution across the insulator sets.

- Arcing horns and fittings protected by them shall be free from visible and audible corona discharge at the highest system voltage.

- The arc must not greatly alter the functionality of the arcing horns.

Arcing horns shall be designed to facilitate easy installation and replacement as normal work.

### 4.4.9	Spacers for 330 kV Lines

Each phase shall comprise twin conductors, disposed horizontally, with a normal centre to centre separation, in the span, of 450 mm. At suspension insulator sets the separation shall be reduced to 300 mm; in the middle sections of jumper connections between tension insulator sets, and in downleads from terminal towers, the separation shall be 250 mm.

The spacer shall withstand the forces initiated from the short current, wind, longitudinal movement, and sub-span oscillation.

The spacer shall not initiate any bending moment in the conductors at normal working conditions.

The tightening torque shall not exceed 60 Nm.

The conductor clamps shall be of aluminium alloy. The bidder shall provide a spacer application chart for the approval of the Project Manager. The quantities of spacers in the price schedules are provisional, the bidder shall submit exact quantities for the approval of the Project Manager.

The bidder shall provide appropriate designs for spacers for the approval of the employer.

### 4.4.10 Armour Rods

Armour rods of the factory-formed type shall be installed on all conductors in the suspension clamps. Armour rods shall be of aluminium alloy for use on the phase conductors. The ends of rods shall be well rounded. The Armour rods must not damage the conductor in service under vibrations.

### 4.4.11 Corona Rings

Corona rings shall be supplied and fitted for both 132kV and 132kV lines

Particular Technical Requirements for the 330kV and 132kV Lines

GENERAL DESIGN DATA

The general electrical design data for the plant and equipment shall be as follows:

| Item | Description | Unit | 132kV | 330kV |
| --- | --- | --- | --- | --- |
|  | Nominal system voltage, phase to phase | kV | 132 | 330 |
|  | Highest system voltage, phase to phase | kV | 145 | 363 |
|  | System Frequency | Hz | 50 | 50 |
|  | Impulse withstand voltage (1.2/50 µsec wave) - Internal insulation - External insulation, sea level | kV peak kV peak | 650 | 1300 |
|  | Power frequency withstand voltage 1 minute. - Internal insulation - External insulation, sea level | kV peak kV peak | 275 | 570 |
|  | Assumed highest switching surge |  |  |  |
|  | Conductor clearances to ground - Normal ground - Road crossing - Rail crossing - Power and communications lines - Buildings, poles, structures and walls, etc. upon which a man may stand | m m m m m | 6.70 6.70 8.55 3.55 4.10 | 7.6 8.25 13.4 6.1 |
|  | Conductor Phase clearance to earth (minimum air clearance between any phase conductor or any live part and grounded part) - No wind clearance - Assumed insulator or jumper swing corresponding to a wind pressure of 430 Pa - Assumed insulator or jumper swing corresponding to a wind pressure of 215 Pa | m m m | 1.22 0.30 0.77 |  |
| 9. | Insulation Distances for Insulators |  |  |  |
|  | - Min surface creepage distance measured from live metal to fixing base | mm | 3,300 |  |
|  | - Min protected surface creepage distance | mm |  |  |

ANNEX A – REFER TO RELEVANT IEC STANDARD ABOVE

TYPE TEST OF STRING INSULATOR UNITS

CROSS REFERENCE TABLE for AC insulators

|  | Insulator to be tested |  |
| --- | --- | --- |
| Type of Test | Silicon Rubber Insulators |  |
|  | Nos | Item |
| Routine visual inspection | 50 | 1-50 |
| Routine mechanical test | 50 | 1-50 |
| Routine electrical test | - | - |
| Verification of dimensions Gauging of socket Gauging of pin Creepage distance | 15 | 1-15 1-15 11-15 11-15 |
| Verification of axial runout radial runout | 15 15 | 1-15 1-15 |
| Verification of locking system Dimensions Hardness test Resistance to bending Resistance to corrosion | 5 | 11-15 |
| Radio interference test | 10 | 1-10 |
| Temperature cycle test | - | - |
| Electromechanical failing load test | - | - |
| Mechanical failing load test | 10 | 1-10 |
| Porosity test | - | - |
| Galvanising test | 5 | 11-15 |
| Dry lightning impulse withstand voltage test | 5 | 11-15 |
| Wet power-frequency withstand voltage test | 5 | 11-15 |
| Thermal shock test | 5 | 11-15 |
| Puncture test | 5 | 11-15 |
| Thermal-Mechanical performance test | 10 | 16-25 |

The following criteria of the type test shall be fulfilled for the electro-mechanical failing load, mechanical failing load and thermal-mechanical performance test on string insulators.

Xt = SFL + 0.72 St

where:	Xt:	means failing load from type test

St :	standard deviation from type test

SFL:	specified electromechanical or mechanical failing load.

ANNEX B

SAMPLE TEST OF STRING INSULATOR UNITS - REFER TO RELEVANT IEC STANDARD ABOVE

CROSS-REFERENCE TABLE for AC insulators

|  | Insulator to be tested |
| --- | --- |
| Type of Test | Silicon Rubber |
|  | Nos |
| Routine visual inspection | E1 & E2 |
| Routine mechanical test | E1 & E2 |
| Routine electrical test | - |
| Verification of dimensions Gauging of socket Gauging of pin Creepage distance | E1 & E2 |
| Verification of axial runout radial runout | E1 & E2 |
| Verification of looking system Dimensions Hardness test Resistance to bending. Resistance to corrosion | E2 |
| Temperature cycle test | - |
| Electromechanical failing load test | - |
| Mechanical failing load test | E1 |
| Porosity test | - |
| Galvanising test | E2 |
| Thermal shock test | E2 |
| Puncture test | E2 |

The sampling shall be according to:

Lot size		Sample size

(N)			E1		E2

N<300			Subject to agreement

300<N<2000		4		3

2000<N<5000		8		4

5000<N<10000	12		6

The following criteria of the sample test shall be fulfilled for the electromechanical failing load or mechanical failing load on string insulators.

Xs > SFL + C1 Ss		Yes = Accepted

Xs > SFL + C2 Ss		No  = Rejected

Xs > SFL + C1 Ss		Yes = Re-test with double sampling

Xsr > SFL + C1 Ssr		Yes = Accepted  No = Rejected

Where:	Xs  :	means failing load from sample test

Xsr :	means failing load from sample re-test

Ss  :	standard deviation from sample test

Ssr :	standard deviation from sample re-test

Sample size (E1)

Coefficient	4	8	12

C1 and C3	1.0	1.42	1.7

C2		0.8	1.2	1.5

5. MATERIAL SPECIFICATIONS FOR STEEL TOWERS

5.1	General

The Contractor shall supply tension towers and suspension towers for all three (3) types of overhead lines. The Contractor shall assume full responsibility for the adequacy and accuracy of the supplies. No omission or ambiguity on the drawings or in these specifications will relieve the Contractor from the responsibility of furnishing first class materials and workmanship.  Should any inaccuracy be found, any further work done before these discrepancies are corrected will be at the Contractor’s risk.

5.2	Materials

Steel members, steel plates, bolts, nuts and washers shall comply with the requirements for materials in these Specifications. All ferrous parts shall be galvanized. All materials to be supplied by the Contractor shall be new and un-used.

5.3	Towers for 330 kV Line In – Line Out

### 5.3.1	General Requirements

The towers shall be designed to carry the line conductors with the necessary insulator sets, earth conductors and all fittings under the conditions and with the factors of safety specified. The loading conditions and design criteria on which calculations and design are to be based are specified in the technical schedules.  Under the specified loading conditions the allowable stresses shall not be exceeded in any part of the tower.

The line conductors for the 330 kV Line In –Line Out shall be in one horizontal plane, with the two earth wires symmetrically disposed above.  The positions of the earth conductors with respect to the line conductors shall be as stated in this specification and on the drawings.

All tension and suspension towers shall be of the self-supporting type. The self-supporting towers shall be designed and constructed to be suitable for adding body and hillside leg extensions when necessary.

Provisions shall be made for the attachment of stringing and maintenance equipment to the cross-arms.

### 5.3.2	Tower Types and Duties

The towers shall be one of the following standard types as stated in the table below:

- For the 330 kV Single Circuit Towers

| TYPE | POSITION OF USE | ANGLE OF DEVIATION | TYPE OF INSULATORS | DRAWING NO. |
| --- | --- | --- | --- | --- |
| AS1 AS2 AS3 BT C D DEF DE G | Straight line self-supporting Straight line self-supporting Straight line self-supporting Self-Supporting Straight or angle Self-supporting, straight line or angle Self-supporting, heavy angle Self-supporting, heavy angle Dead end Self supporting, transposition | 0o-2o 0o-2o 0o-2o 0 – 10o 10-30o 30o - 60o 60o - 90o 60o - 90o 0o-10o | Suspension Suspension Suspension Tension Tension Tension Tension Tension Tension | See 330KV Tower outline drawings in appendix |

For 330KV Double circuit towers

| TYPE | POSITION OF USE | ANGLE OF DEVIATION | TYPE OF INSULATORS | DRAWING NO. |
| --- | --- | --- | --- | --- |
| 300S 300T10 300T30 300T70 30090 300TR | Straight line self-supporting Self-Supporting Straight or angle Self-supporting, straight line or angle Self-supporting, heavy angle Self-supporting, heavy angle Self-supporting, transposing | 0o-2o 0 – 10o 10-30o 30o - 70o 70o - 90o 0 – 10o | Suspension Tension Tension Tension Tension Tension | See 330KV Tower outline drawings in appendix |

The employer has designs for all the towers listed above.

The towers are designed such that, where required the towers may be extended or reduced by extensions of the height stated in the Bill of Quantity. Extensions and reductions shall be designed so that the towers with their foundations shall comply with all the specified requirements for the standard height towers and foundations.

Special towers, special foundations, special extensions, and special parts for standard towers, shall be provided where required and shall be of approved design.  The type of tower to be used at each position shall be approved by the Project Manager or his representatives.

### 5.3.3	Use of Standard Towers

The standard towers shall be designed for use in accordance with the Specification requirements for span lengths and deviation angles.

Where the Line in-Line Out route makes a deviation or due to rough terrain the relation between wind span and weight span is such that the swing out angle of the suspension insulator set (including counterweights) exceeds the value of 45 degrees, angle towers with tension insulator sets shall be used.  (Uplift conditions).

Where in a long straight run of towers it is, in the opinion of the Project Manager, desirable to section and tension off the line and earth conductors, type BT (for 330 kV) towers shall be provided at approved positions.  Section lengths shall normally not exceed 5 km for the 330-kV line.

### 5.3.4	Span Lengths

The expression “span length” shall be taken to mean the horizontal distance between the centre lines of adjacent towers.

For the 330 kV Line in – Line out, the design ’average’ span length is 450 m for Bison conductor and shall be the span length on which all standard tower heights, assuming level ground and + 80oC conductor temperature, shall be based. All towers shall be or are, however, be designed for the following maximum weight and wind span with Bison conductor:

- 330 kV Lines

| Type | Angle of Deviation or Entry | Weight Span | Wind Span |
| --- | --- | --- | --- |
| All towers | All towers | 900 m | 495 m |

It must be noted that the design span with +80oC conductor temperature is determining tower heights, as per specifications for the suspension towers.

### 5.3.5	Loading Conditions for 330 kV Towers

1.	Normal Loading

The assumed maximum simultaneous loadings on the towers, the appropriate maximum angles of deviations and span lengths being (except as modified by the following vertical loadings) as specified in accordance with the particulars given in chapters 9 and 10:

Vertical Loads

On all types of towers, the mass of the line and earth conductors, the mass of the insulators, insulator fittings, earth conductor fittings and ancillary apparatus where applicable.  It shall be assumed that the maximum loads will include the actual total mass of twice the standard span lengths of the line and earth conductors, stated in Schedules of chapters 9 and 10.  For the minimum load condition the mass of line and earth conductors shall be zero.

Transverse Loads

The wind pressure stated in chapters 9 and 10 acting at right angles to the lines on the whole projected area of the line and earth conductors, over 80 % of the adjoining spans, and the transverse horizontal resultant of the line and earth conductor tensions stated in chapters 9 and 10 and the wind pressures stated in chapters 9 and 10 on 1 ½ times the projected area of the members of one face of the towers.  An assessment of wind on insulator sets shall be included at a wind pressure of 430 Newtons per square metre.

Longitudinal Terminal Loads (on terminal towers only)

The longitudinal components of the line and earth conductor tensions stated in Schedules technical, acting simultaneously from all phases and earth wires on one side of the tower only.

2.	Unbalanced loads

The standard types of towers shall be designed for the unbalanced conditions shown in the table below.

Simultaneous unbalanced loading conditions

| Tower Type Unbalanced Conditions in any one span | Transverse, (as % of those specified in Clause 5.3.5-1 |  | Vertical (as % of those specified in Clause 5.3.5-1 | Longitudinal |
| --- | --- | --- | --- | --- |
|  | Due to Wind | Due to Angle of Deviation |  |  |
| All Towera At any one phase attachment and At any one earth conductor attachment | 75 % 75 % | 50 % 50 % | 75 % 75 % | 62,200 N 20,500 N (Both in same direction) |

Care shall be taken in the design to allow for any additional loads to which the towers may be subjected during the erection of the towers themselves and of the conductors and insulators.

### 5.3.6	Content of Drawings

Three sets of drawings shall be submitted to the Project Manager for approval.

The size and layout shall be in accordance with clause 1.11 of the general requirements)

These drawings shall show the following data and information for the towers to be supplied by the Contractor including tower body and leg extensions as necessary:

1.	An outline drawing of the tower showing all basic design dimensions.

2.	Electrical clearances.  Note: Deflections of tower and suspension set shall be considered.

3.	Specified loading conditions.

4.	A tabulation of the calculations showing the design of each member, i.e. steel quality, angle size, unsupported length, slenderness ratio, number and size of connection bolts required, ultimate strength of each member in compression, tension, shear and bearing and maximum design load from the loading conditions.

5.	A tabulation form showing the design of the redundant members.

6.	Wind loads on the tower at each point of application.

7.	A tabulation showing the total stress in each member due to each specified ultimate loading case.

8.	Stress diagrams or computer data so that the client can readily check the strength of the tower from the loading conditions specified.

9.	Details of conductor, earth wire and foundation attachments, including design calculations.

10.	The compression and reactions and corresponding horizontal shears for each governing load case.

11.	All erection shop drawings shall show the members assembled in place, clearly indicating all dimensions, the size, number and lengths of bolts required in each connection and the piece mark of each member.

12.	A bill of materials shall be prepared in tabulation form, listing all materials required for fabrication and assembly of the tower incl. bolts, nuts, step bolts, packings and washers.  The list shall show the number of members required, the piece mark and the total weight of the body and each extension.  For purpose of computing member weights, a specific density of 7.85 grams per cubic centimetre of steel shall be used.  Deductions shall not be made for clippings and bolt holes.  All weights shall be black weights (ungalvanized).

13.	Assembly drawings.

14.	Drawings or forms showing all setting out data and measurements for all tower types with body extensions and individual leg extensions.

5.4	Towers for 132kV Lines

### 5.4.1	General Requirements

The towers shall be designed to carry the line conductors with the necessary insulator sets, earth conductors and all fittings under the conditions and with the factors of safety specified.

The bidder shall provide the loading conditions and design criteria on which calculations and design are to be based are specified in the technical schedules.  Under the specified loading conditions the allowable stresses shall not be exceeded in any part of the tower.

The line conductors for the 132-kV double circuit line shall be in vertical plane, with one earth wire above.  The bidder shall design and make available to the employer the positions of the earth conductor with respect to the line conductors, and these shall be indicated in the design drawings.

All towers shall be self-supporting towers.

All tension towers shall be of the self-supporting type.

The self-supporting towers shall be designed and constructed to be suitable for adding body and hillside leg extensions when necessary.

Provisions shall be made for the attachment of stringing and maintenance equipment to the cross-arms.

### 5.4.2	Tower Types and Duties

The towers to be used on the line shall be self- supporting steel monopoles, with the minimum defined wind and weight spans given below. For profiling purposes, the range of lowest conductor attachment height for all structures shall be (13m; 14m; 15m; 16m; 17m)

- For the 132kV

| TYPE (TO BE FURNISHED BY THE BIDDER) | POSITION OF USE | ANGLE OF DEVIATION | TYPE OF INSULATORS | DRAWING NO. |
| --- | --- | --- | --- | --- |
| A B C D/DE F (Special Tower River Crossing) | Straight line self-supporting Self-Supporting Straight or angle heavy angle Self-supporting, steel monopole Angle, Dead end | 0 - 2o 0 – 30o 30 - 60o 60o - 90o 0 – 45 o for dead end | Suspension Tension Tension Tension Tension | TO BE FURNISHED BY THE BIDDER |

The employer does not have designs for the double circuit 132kV towers. Therefore, the bidder is expected to design the towers.

The towers should be designed such that, where required the towers may be extended or reduced by extensions of the height stated in the Bill of Quantity.

Extensions and reductions shall be designed so that the towers with their foundations shall comply with all the specified requirements for the standard height towers and foundations.

Special towers, special foundations, special extensions, and special parts for standard towers, shall be provided where required and shall be of approved design.  The type of tower to be used at each position shall be approved by the Project Manager or his representatives.

### 5.4.3	Use of Standard Towers

The standard towers shall be designed for use in accordance with the Specification requirements for span lengths and deviation angles.

Where the transmission line route is a straight line, suspension type self-supporting with suspension insulator sets shall normally be used for the 132kV line.

Where the transmission line route makes a deviation or due to rough terrain the relation between wind span and weight span is such that the swing out angle of the suspension insulator set (including counterweights) exceeds the value of 45 degrees, angle towers with tension insulator sets shall be used (Uplift conditions).

Where in a long straight run of towers it is, in the opinion of the Project Manager, desirable to section and tension off the line and earth conductors’ towers shall be provided at approved positions. Section lengths shall normally not exceed 5 km or a specific design length to be agreed with the employer.

At transformer stations the transmission lines shall be terminated on type D towers which will normally be erected with the plane of the cross-arms parallel to the station gantries and the transmission lines shall be assumed to terminate on the towers at any angle up to but not exceeding 45o from the tower centre line normal to the length of the switching station.  The downlead conductors between the terminal tower and the switching station structures shall be strung with substantially reduced tensions, to be provided in the Technical Schedules by the bidder and shall normally be attached at both ends on tension insulator strings and shall be assumed to terminate on the switching station gantry at any angle up to but not exceeding 30o from the tower centre line normal to the gantry.  Earth conductors shall be included in downlead spans.

Where it is necessary to provide transposition, transposition towers with tension insulators shall be used. These towers shall preferably be straight line tension towers, modified to accommodate the necessary additional insulators and cross-connecting conductors. The transposition towers shall be provided with appropriate phase plates on both faces to indicate the phase position changes. The location of the preferred transposition point shall be advised by the project manager or his representative.

### 5.4.4	Span Lengths

The expression “span length” shall be taken to mean the horizontal distance between the centre lines of adjacent towers.

For the 132kV line, the design ’average’ span length shall be provided by the bidder for Bison conductor and shall be the span length on which all standard tower heights, assuming level ground and + 80oC conductor temperature, shall be based. In addition, there are towers with extensions.

The bidder shall design and provide for all towers shall be the maximum weight and wind span with Bison conductor as in the table below:

- 132kV lines

| Tower Type (TO BE FURNISHED BY THE BIDDER) | Angle of Deviation or Entry | Weight Span (m) | Wind Span (m) |
| --- | --- | --- | --- |
| A B C D/DE F | 0o - 2o 0o - 30o 30o - 60o 60o - 90o 60o - 90o | 300 300 300 450 | 450 500 500 650 750 |

It must be noted that the design span with +80oC conductor temperature is determining tower heights, as per specifications for the suspension towers.

### 5.4.5	Loading Conditions for 132kV double circuit Towers

1.	Normal Loading

The assumed maximum simultaneous loadings on the towers, the appropriate maximum angles of deviations and span lengths being (except as modified by the following vertical loadings) as specified by the bidder in Clauses 5.4.2 to 5.4.4 shall be in accordance with the particulars given by the bidder in technical schedules and as follows:

Vertical Loads

(i)	On all types of towers, the mass of the line and earth conductors, the mass of the insulators, insulator fittings, earth conductor fittings and ancillary apparatus where applicable.  It shall be assumed that the maximum loads will include the actual total mass of twice the standard span lengths of the line and earth conductors. For the minimum load condition, the mass of line and earth conductors shall be zero.

(ii)	On all types of tower nett total uplift per phase shall be provided by the bidder and a nett total uplift per earth conductor shall also be provided by the bidder to the satisfaction of the employer.

Transverse Loads

The wind pressure stated in the technical schedules 9 and 10 acting at right angles to the lines on the whole projected area of the line and earth conductors, over 80 % of the adjoining spans, and the transverse horizontal resultant of the line and earth conductor tensions provided by the bidder in schedule technical schedules 9 and 10, and the wind pressures in technical  schedules 9 and 10 on 1 ½ times the projected area of the members of one face of the towers.  An assessment of wind on insulator sets shall be included at a wind pressure of 430 Newtons per square meter.

Longitudinal Terminal Loads (on terminal towers only)

The longitudinal components of the line and earth conductor tensions provided by the bidder in technical schedules 9 and 10, acting simultaneously from all phases and earth wires on one side of the tower only.

2.	Unbalanced loads

The standard types of towers shall be designed for the unbalanced conditions shown in the table below.  At the conductor attachment points not affected by the unbalanced loadings, all loads shall be as specified in Clause 5.4.5-1 above.

Simultaneous unbalanced loading conditions

| Tower Type Unbalanced Conditions in any one span | Transverse, (as % of those specified in Clause 5.4.5-1 |  | Vertical (as % of those specified in Clause 5.4.5-1) | Longitudinal (N) |
| --- | --- | --- | --- | --- |
|  | Due to Wind | Due to Angle of Deviation |  |  |
| TYPES A, B, C, D, F At any one phase attachment At any one earth conductor attachment | 75 % 75 % | 50 % 50 % | 75% 75% | TO BE FURNISHED BY THE BIDDER |

Care shall be taken in the design to allow for any additional loads to which the towers may be subjected during the erection of the towers themselves and of the conductors and insulators.

### 5.4.6	Content of Drawings

Three sets of drawings shall be submitted to the Project Manager for approval.

The size and layout shall be in accordance with clause 1.11 of the general requirements)

These drawings shall show the following data and information for the towers to be supplied by the Contractor including tower body and leg extensions as necessary:

1.	An outline drawing of the tower showing all basic design dimensions.

2.	Electrical clearances.  Note: Deflections of tower and suspension set shall be considered.

3.	Specified loading conditions.

4.	A tabulation of the calculations showing the design of each member, i.e. steel quality, angle size, unsupported length, slenderness ratio, number and size of connection bolts required, ultimate strength of each member in compression, tension, shear and bearing and maximum design load from the loading conditions.

5.	A tabulation form showing the design of the redundant members.

6.	Wind loads on the tower at each point of application.

7.	A tabulation showing the total stress in each member due to each specified ultimate loading case.

8.	Stress diagrams or computer data so that the client can readily check the strength of the tower from the loading conditions specified.

9.	Details of conductor, earth wire and foundation attachments, including design calculations.

10.	The compression and reactions and corresponding horizontal shears for each governing load case.

11.	All erection shop drawings shall show the members assembled in place, clearly indicating all dimensions, the size, number and lengths of bolts required in each connection and the piece mark of each member.

12.	A bill of materials shall be prepared in tabulation form, listing all materials required for fabrication and assembly of the tower incl. bolts, nuts, step bolts, packings and washers.  The list shall show the number of members required, the piece mark and the total weight of the body and each extension.  For purpose of computing member weights, a specific density of 7.85 grams per cubic centimetre of steel shall be used.  Deductions shall not be made for clippings and bolt holes.  All weights shall be black weights (ungalvanized).

13.	Assembly drawings.

14.	Drawings or forms showing all setting out data and measurements for all tower types with body extensions and individual leg extensions.

5.5	Design Requirements

### 5.5.1	General

Tension and suspension towers including extensions shall be of steel, bolted construction.

The bases of the tower bodies and body extensions shall be square in plan and the tower body shall be the same whether used with or without body extensions and with identical bracings in all directions.

The towers shall be designed in accordance with the second order theory.

Steel structures shall comply with the requirements of ASCE-Guide for Design of Steel Transmission Towers, the latest edition.

Any other standards that the contractor may wish to apply shall be internationally recognised and be to the approval of the Project Manager.

### 5.5.2	Steel Standards and Quality

The steel shall comply in quality and strength with internationally recognised standards to the approval of the Project Manager.  The appropriate Specification which details both mechanical and chemical properties shall be provided, together with evidence that the particular steel offered has had not less than five years satisfactory service experience on transmission line towers.  The steel shall be free from blisters, scales, laminations, or other defects.

All bolts shall be made of one type of steel only.

The steel shall be of a quality that will not have its physical properties changed and not become embrittled by hot-dip galvanizing.

Guy wires shall comprise stranded galvanised steel wire and shall comply with BS 183, unless otherwise approved.

### 5.5.3	Members

Stresses in tension members shall be calculated from the net area after reduction for holes.  In case of a single angle member connected by one flange only, the net area shall be reduced by 10 %.  For connections with one bolt only, the net area shall be reduced with 30 %.  Allowable ultimate tensile stress is equal to the yield point Fy of the steel.

Redundant members supporting leg members or supporting other members shall be designed for a transverse load at each node point of minimum 1.7 % of the maximum load in the leg member or the other member respectively.

Allowable ultimate stress in tension and compression on extreme fibres is equal to the yield point Fy of the steel.

The ratio between unsupported length of a member and the relevant radius of gyration, L/r, shall not exceed:

1.	Compression members		L/r

- Leg members			120

- Other members			200

- Redundant members		250

2.	Tension members			350

Minimum thickness of members shall be:

- Leg and main compression

members in crossarms and

shield wire peak			6 mm

- Other members			4 mm

- Redundant members		4 mm

- Gusset plates	6 mm or minimum thickness of connecting member +2mm

Maximum lengths of members shall not exceed twelve (12) meters.

Flat bars and rods shall not be used for tower members. The angle between any two members, which are connected to each other, shall not be less than 13o.

All members which can be subjected to the weight of a linesman shall be designed to withstand an ultimate load of 1.50 kN, at the most unfavourable point, without permanent deformation.

### 5.5.4	Bolted Connections

Bolts shall conform to the requirements of Clause 5.4.5.

Bolted connections may have one bolt only.

Minimum bolt spacing is equal to two point five (2.5) times the bolt diameter.

The distance from the centre of a fastener hole to the end of any connected part shall not be less than two (2.0) times the bolt diameter minus five (5.0) mm and the distance to the adjacent edge shall not be less than one point five (1.5) times the bolt diameter.

The distance from the centre of a bolt to the face of the outstanding flange of an angle or other members shall be such as to permit the use of a socket wrench, in tightening the nut.

The bolt hole diameter shall be equal to the bolt diameter plus one point five (1.5) mm.

Allowable ultimate bearing stress for bolts as well as members is equal to one point zero (1.0) times the ultimate stress Fu of the steel.

Allowable ultimate shearing stress for bolts and members is equal to zero point six (0.6) times the ultimate stress Fu of the steel.

### 5.5.5	Bolts, Nuts and Washers

Bolts in towers shall be high strength grade and of Metric standard.  Connection bolts, step bolts and nuts shall be high strength bolts conforming relevant BS-EN standard or equivalent.  All bolts shall be of the same steel quality for the entire supply under this contract.

Bolts and nuts shall be of standard design. Nuts shall be tapped after galvanizing and the threads of the nuts left bare and greased.  Washers shall be used under the nuts.  Bolt lengths shall be such as to ensure that bearing is upon the shank and not upon the thread of the bolt.  The threaded part shall end within the washer.  When installed, the bolt shall project through the nut not less than the greater of three (3) mm and three and half threads and not more than ten (10) mm.  Taper washers shall be used where required.

Special anti-vandal bolts and nuts shall be supplied for all towers and shall only be for installation from ground level to just immediately above the ant-climb. The design of the antivandal bolts shall be to the approval of the Project Manager. Drawings showing the proposed antivandal bolts together with details shall be included in the bid.

All bolts, nuts and washers shall be furnished 5% in excess of the actual number required to compensate for normal field losses.

All bolts, nuts and washers shall be galvanised.

5.6	Detailing Requirements

### 5.6.1	Splices

Splices in all members shall be of the butt-splice or lap-splice type.

Splices of the tower leg or extensions shall be located immediately above horizontal members or diagonal brace connection.

### 5.6.2	Attachment of Insulator Strings

Suspension towers will be fitted with single suspension insulator strings.

Angle and terminal towers will be fitted with double dead-end insulator strings.  One attachment point for each sub conductor shall be provided.

For the towers where jumper insulator sets, as shown on the drawing, are to be provided, they shall be equipped with necessary attachment possibilities.

The earth wire suspension and Tension assemblies shall be proposed by the bidder.

The attachment points shall be designed so that eccentricities are avoided as far as possible and suitable for using the shackles as shown on the drawings.  For suspension towers, an unobstructed transverse swings out angle of 45o shall be provided for.

### 5.6.3	Miscellaneous

The design shall be such as to keep the number of different parts as small as possible and to facilitate transport, erection, and inspection.

Horizontal members shall be placed wherever possible so that the horizontal flange is on the top.  Pockets and depressions likely to hold water shall be avoided and, if not avoidable, shall be properly drained.

Tension members shall not be made of flats or rods.

The holes necessary for accommodating the earthing counterpoise connections as specified shall be provided on each leg of every tower and extension.  Holes for all required number signs, danger signs, step bolts etc. shall be provided on each tower.

Approved means shall be provided on all towers and extensions to avoid risk of livestock being caught and injured in the angles between tower members.  Suspension towers shall be equipped with approved devices immediately above each suspension insulator attachment point, to prevent the perching of birds at these points.

### 5.6.4	Accessories

1.	Anticlimbing Devices and Steps

Each tower shall be fitted with an anti-climbing device of approved type, the component parts of which shall be securely fixed to prevent pilferage, fixed at a height of approximately 3.5 metres above ground.  The position of the anti-climbing device on the tower shall be such that a standard device is used regardless of the arrangement of tower body and leg extensions which may be employed.

On each tower one leg shall be provided with steps of approved type at not more than 380 mm centres starting immediately above the anti-climbing device and continuing to the top of the cross-arm.  Below the anti-climbing devices, holes shall be provided for step bolts at the centres stated above.  Sets of step bolts to fit these holes shall be provided where required by the Project Manager, at the price stated in Bill of Quantities.

2.	Notice Plates

Conspicuous danger and property plates and route and tower number plates of approved types vitreous enamelled and resistant to fading under the climatic conditions at Site, shall be provided and fixed in approved positions on all towers.

Phase plates of approved types coloured red, white and blue respectively to indicate the line conductor phases shall be provided for each circuit and fixed in approved positions on all towers.

Aerial number plates shall be provided and fixed in an approved position on both earth wire peaks of every tenth tower.

Enamelled plates shall be provided with fibre washers, front and back, at the securing screws or bolts.

The bidder shall submit a design proposal for 132kV plates, and the design shall be subject to the approval of the Project Manager.

### 5.6.5	Tower Leg Attachment

For self-supporting towers, the connection of the tower to concrete foundations shall be by means of a steel stub angle.  The stub angle shall be of the same dimension as the tower leg member to which it connects.  Typical layout is shown on attached drawings.

All necessary input data such as leg slope, gusset plates, loads, distances from centre line and ground level etc. shall be provided by the Contractor for use in his foundation design, and be submitted together with the foundation design for approval.

### 5.6.6	Templates

The Contractor shall supply enough suitable setting templates for the correct location and inclination of the tower legs.

The templates shall be of structural steel and designed to the satisfaction of the Project Manager.

### 5.6.7	Tower Erection, Stringing and Maintenance

Three methods for erection of the towers shall be possible:

Hinged derrick

Climbing derrick

Mobile crane

The towers shall be provided with plates or holes for plates or eyehooks attachment for erection and maintenance.

  - SPECIFICATION FOR STEEL MONOPOLES

5.7.1 General

The following structure types are included in this specification:

- single circuit or double circuit self-supporting intermediate structures (planted or flanged).

- single circuit or double circuit self-supporting terminal structures (planted or flanged).

- single circuit stayed terminal structure (planted or flanged).

- single circuit or double circuit stayed angle strain structure (planted or flanged).

- single circuit or double circuit self-supporting angle strain structure (planted or flanged)

- single circuit or double circuit stayed pivot-base structures: and

For double circuit lines, 2 single circuit stayed angle strains may be used. For termination of double circuit lines, 2 single circuit stayed terminal structures may be used.

    - Dimensions

The overall lengths of the poles shall be determined by from the profile drawings. The actual pole length shall not differ from the stated overall length by more than 50 mm.

The base and tip diameters of the actual structure shall not differ from the designed diameter by:

- 5 mm for diameters up to 350 mm

- 1,5 % for diameters over 350 mm

Diameters at slip joints shall not differ such that the minimum required slip length is not obtained.

5.7.3 Finish

The finished product shall have a smooth external surface free from steel splinters and welding splatter. All surfaces shall be clean and shall present a neat appearance. All corners shall be rounded with no sharp edges.

    - Joints

Flanged and slip joints should be aligned such that there is minimum pole deflection around the joint

      - Slip joints:

The overlap section of a slip joint shall be at least 1.5 times the top diameter of the male section. In the case of a non-uniform cross section pole, the overlap section of the slip joint shall be at least 1,5 times the largest top diameter of the male section. Female slip joints shall have rapping plates on seams to avoid splitting. The slip length shall not differ more than 50mm from the designed slip length. Provision shall be made on the structure for jacking lugs in order for the slip joints to be installed to the correct tension and depth. The correct tension shall be noted on the manufacturers detail design drawings.

      - Flanged joints:

Flanged joints shall be manufactured with a jig set up in the manufacturer’s workshop to ensure squareness of the flange onto the pole. Mating faces of cross-arm flanges shall be square to ensure surface contact on assembly. One set of 10 off x 0.5mm thick finger packs shall be supplied with each batch of 10 poles for slight pole adjustments. These packs shall be of such a nature that they can be installed without unbolting flanges.

    - Welds

Coded welding personnel shall perform all welding. Finished welds shall be smooth with no sharp edges. Welds shall be of a strength that does not change the designed proof load, ultimate load or crippling load. The ends of longitudinal welds shall be strengthened at slip joints on female sections to prevent splitting.

Butt welds shall have 100% penetration.

Seam welds shall have a minimum penetration of 60 % except in the area of slip joints where 100 % penetration is required. The inside weld at the slip joint shall be ground back to ensure no obstruction when obtaining the desired slip lengths.

All shaft circumferential welds and their associated sections of longitudinal welds and all longitudinal welds for the female parts of a slip joint shall be full-penetration welds in order to achieve full base material strength.

The shaft shall be centrally welded onto the base plate. All shaft structural welds shall be performed with submerged arc technology.

Cross-arm tubular sections shall be centrally welded onto the connecting flanges. All fitting-related welding shall be performed with inert gas technology.

    - Openings

If specified, openings (e.g. bolt-holes, slots etc) shall be made in the poles during the manufacture of the poles. These openings may be required for the attachment of cross-arms and other equipment. All openings shall be made before galvanizing or treating.

Bolt hole tolerances are as follows:

- 6 mm for foundation bolts.

- 2 mm for all other bolts.

Plates for insulator attachments shall be manufactured with keyholes and dimensions in accordance with the supplied insulator details.

    - Ladders/Climbing system

Brackets for removable climbing steps, if applicable, shall be vertically spaced at 300mm and configured such that the climber has a comfortable climbing path. The brackets shall permit easy installation of removable steps without becoming trapped or wedged into the brackets.

Brackets welded onto the structures for propriety system, if applicable, shall suit the spacing of the ladder brackets. The ladder supplier shall be consulted for attachment details. If this system is used on a structure, the brackets on the structure shall start at approximately 9m above ground level. This lower portion shall be accessed by means of a standard ladder and will prevent unauthorised persons climbing the structures.

Should a permanent ladder be required on the structure, the ladder shall be supplied loose and bolted onto the structure on site. This will ensure that no damage is caused to the ladder during transportation.

The type of climbing device shall be specified by the purchaser.

    - Galvanising and pole treatment

These structures will be used in all environments, from coastal regions to inland areas. All poles shall be hot dip galvanised to ISO 1461 and shall have a minimum coating thickness of 105 microns.

All structures shall be suitably straightened after galvanizing without causing damage to the galvanizing surface or to the structure itself. No curved, bent or twisted structures will be accepted.

Poles to be planted shall be bitumen treated from 200 mm above the ground line to 500 mm below ground line.

    - Steel requirements

The minimum thickness of the steel used for manufacture of poles shall be 4.5 mm unless specified in the data schedules. The steel used shall be grade S355JR in accordance with EN 10025. If different grades of steel are used for manufacture these must be approved by the employer before manufacturing commences. The manufacturer shall ensure that mill certificates are available and traceable to structures manufactured.

All bolts used shall be grade 8.8 bolts. No electroplated bolts will be permitted.

    - Deflection Requirements

The horizontal deflection for a structure loaded with safe working loads shall be no greater than 2.2% of the total pole height. The permanent horizontal set allowed after application and removal of working loads shall be no greater than 1% of the total pole height.

The horizontal deflection for a structure loaded with ultimate loads shall be no greater than 5.5% of the total pole height. The permanent horizontal set allowed after application and removal of ultimate loads shall be no greater than 3% of the total pole height.

    - Drawings

The structure layout drawings are a guideline of what is required with regard to layout, attachment heights, stay levels, wind and weight spans etc. The manufacturer shall ensure that designs and manufacturing are suited to the structure required.

A set of manufacturing drawings is required for checking and approval purposes before manufacturing commences.

A complete and correct set of drawings are required for record on completion of the job.

    - Tests

All tests are to be in accordance with IEC 60652: Loading tests for overhead line structures.

One structure for each structure type will be type tested, the length chosen for the structure will be the length with the largest loads in the structure. SANS 10280 provides for a reduction in the strength factor of the material in order not to subject the structures to full scale testing. This option is to be disregarded by the contractor and full scale testing is mandatory.

      - Acceptance criteria for tests

The mast shall resist all working loads without showing signs of buckling or crippling. Any signs of member buckling, signs of buckling onset, connection failure or deflections in excess of those of the deflection requirements of this document shall constitute the failure of the structure

      - Ultimate load test

The ultimate load test shall be completed on all structures being tested and shall be executed once the working load tests are done. The ultimate loads indicate the loads the structure will carry including factors of safety as specified. Tests shall be carried out on strong and weak planes of asymmetrical poles. The tests need only be completed in one direction on symmetrical poles.

The load shall be applied to the structure in increments of 10 % up to 90 % of the ultimate load, thereafter in increments of 5 % of the ultimate load until failure. This 100% load shall be held for 60 seconds before being released. Deflection readings shall be taken whilst the load is being applied and once the load has been released.

The structure shall withstand the applied loads for 60 seconds without failure of any component. Deflections in excess of those depicted in the deflection requirements shall constitute the failure of the structure.

      - Straightness test

Straightness shall be taken as the maximum distance measured between the centre-line of the faces of the pole being measured, at any point along the length of the pole, to a line drawn from the centre of the tip of the pole to the centre of the butt of the pole. The measurements shall be done on at least two faces of the pole which are at 90° to each other. Measure, to the nearest 5 mm, the deviation from straight.

    - Marking and packaging

      - Marking

All structures and components to be uniquely identified with permanent marking which will enable the details of the structure to be established at any time after assembly. All identification marks and structure-related information are to be easily readable after the structure has been assembled. The following information shall be clearly and indelibly marked with characters at least 20mm high and indented 1mm. This information shall be 1.5 m above the ground line on finished poles:

- the manufacturers name, trade name or trade mark;

- the overall length of the pole in meters e.g. “23 m”;

- the ultimate load design e.g. “ UL = 23 kN”;

- the crippling load (if applicable) e.g. “CL = 100 kN”

The following information shall be marked on the pole and be in included in an erection procedure to be issued with every batch of pole dispatch to site:

  - the minimum and maximum slip joint penetration limits

  - holding-down bolt torque requirements

  - maximum axial slip-joint assembly load

  - orientation of sections with respect to one another to be clearly and permanently marked

  - pole/baseplate orientation with respect to the line to be identified

      - Packaging

All structures shall be suitably stacked to avoid damage during transport. Dunnage shall be used between steel members to avoid these touching and damaging each other. No buckled, bent or twisted structures and associated bracketry will be accepted on site. The manufacturer shall deliver to site, with the structures, adequate quantities of Zinc-fix squish packs to patch small areas of damaged galvanizing due to transport. Large areas of damaged galvanizing will not be accepted.

    - Method of erection

Ensure that a safe working area around the pole and the hole is maintained.

With the truck mounted crane, position the bottom, middle and top sections of the pole as close to the foundation hole as possible.

The structures shall be completely assembled with all cross-arms access ladders and accessories installed before lifting the structure in place. All bolt connections shall be properly torqued before erection of the structure.

Align the bottom, middle and top sections of the pole to slide into one another.

Ensure that the sections are as horizontally level in relation with one another as possible before start of assembly.

Bottom Section Slinging:

- Using the slipknot/choke-hold method sling with 2 x 3 m round nylon slings.

- Ensure lowest wrapping end is closest to pole section base.

- Ensure highest ends are below earth attachment-brackets.

- Attach 2 x D-shackles one at each end of the slings.

Middle Section Slinging:

- Using the slipknot/choke-hold method, sling with 2 x 3m round nylon slings.

- Ensure highest wrapping end is closest to pole section top.

- Attach 2 x D-shackles, one at each end of the slings.

Attach a coffin hoist to each set of slings on opposite sides of the pole, ensuring that the coffin hoists are primarily attached in-line, middle section to bottom section.

Measure the length of the pole and see how far the two sections must be pulled together to give the correct length of the pole as indicated on engineers drawing.

Mark required slip distance of top pole with insulation tape.

With the coffin hoists, tension both sides equally until the two sections have slid together up to insulation tape mark.

Manually manoeuvre the top section to assist with the sliding together of the sections. Remove insulation tape after correct slip level has been achieved.

Follow the same procedure as above when joining the middle and top sections of the pole.

No structure shall be erected prior to a final inspection on the pole excavations and approval thereof by the Site Supervisor.

Mono-pole structure erection will be subjected to the following criteria:

All structures shall be erected vertically within 2mm in 1.0m in both transversal and longitudinal directions. For the correct structure orientations in relation to the line direction refer to detail drawings;

The deviation from plumb for each installed structure are to be recorded after errection and after completion of the stringing operations.

The contractor are required to rake terminal or bend point structures that are predicted by theoretical calculation to deflect by more than 1.0% of pole length. The location and magnitude of raking on poles shall be calculated by the contractor, based on everyday service loads at zero Pa wind, and initial conductor tensions at 15˚C.

Raking of poles may be achieved through tilting of base plates, tilting of the HD bolts arrangement or by adjusting tensions in stays supporting the bend structures.

During the structure erection the tension in all stays shall be 10% (±2%) of the minimum breaking strength of the stay wire, after all rigging equipment has been removed.

All structures shall be properly cleaned prior to the erection thereof. Sand, mud and other dirt must be thoroughly cleaned with nylon brushes.

Structures should only be lifted into place at the identified lifting points as detailed by the design and the manufacturer of the structures.

5.8	Manufacturing Requirements

### 5.8.1	Technical Documents

Manufacture, supervision, and inspection shall be carried out in due order in accordance with the following documents:

1.	The contract agreement

2.	The approved drawings

3.	This technical specification

4.	Standards and specifications to be employed by the Contractor and approved by the Project Manager

5.	The Contractors (or Sub-Contractors) Quality Assurance Program (QAP)

### 5.8.2	Quality Assurance Program (QAP)

The manufacturer of the towers shall have a QAP which shall be subject to the approval of the Project Manager.

### 5.8.3	Manufacturing Tolerances

Manufacturing tolerances shall be in accordance with the specified and/or agreed standards.

### 5.8.4	Manufacturing

1.	Straightening and Bending

Straightening and bending of steel shall only be carried out in accordance with methods to be proposed by the Contractor and approved by the Project Manager.

Straightening and bending shall not cause any notches or other defects that would have a detrimental influence on the bearing capacity of the structure.

The straightening and bending of a finished welded or bolted structure requires the Project Manager’s consent in writing.  After the straightening and bending the structure shall be carefully examined.

2.	Cutting

Cutting of parts shall be made in such a way as not to cause any notches diminishing the strength or any detrimental stresses.  Cutting shall be made in such a way that deformations are avoided.

3.	Bolt Holes

Besides by drilling, bolt holes may be punched if the thickness of the material does not exceed 13 mm and the diameter of the hole is not inferior to the thickness of the material.

In other cases, the holes shall be either drilled or sub-punched and thereafter reamed or drilled.  The diameter of the die for sub-punching of holes shall be at least 2 mm smaller than the nominal diameter of the hole.

The punching shall be done by pressing, not by hitting; the punch shall fit closely to the die. The holes shall be straight and smooth with a clean surface. The outside dimensions of the material to be punched must not alter and the material not bent.  Burrs shall be removed.  Incorrect holes may be neither partly nor wholly filled out by welding.

### 5.8.5	Numbering of Parts

All separate parts of towers shall be marked with the part identification number which consists of the following numbers:

-	Tower type number

-	The running number of the part in question.

The marking shall be stamped onto the part before hot dip galvanizing using numbers not less than 12 mm high.  The marking shall be placed near one end in the same relative position on each part.  The marking shall be clearly visible after galvanizing and be located on the outside of the structure so that they are visible after erection.

### 5.8.6	Welding

1.	Qualifications for Executing the Welding Work

The welding work on the structures, if employed, shall be performed with a labour management experienced in welding and with skilled welders.  The qualifications shall be testified by a certificate.

2.	Execution of the Welding Work

The sequence of welding shall be such as to cause as small deformations and welding stresses as possible.

The welding shall be performed with equipment and in premises suitable for the purpose.

Equipment shall be well suited to the type of weld to be performed so that the right quality shall be attained.

No gaps or hollows may appear in the welding into which acid may penetrate during the pickling procedure preceding galvanizing.

The weld shall be ground flush to the surface in such places where the welding bulge prevents a perfect fitting of components together.

A high bulge or uneven weld surface may be levelled out by chiselling or grinding.

3.	Filler Metals for Welding

Standard filler metals shall be used and the strength class and quality shall be chosen to correspond to the base material.

### 5.8.7	Galvanising

All ferrous parts shall be galvanized in accordance with the clause for corrosion protection.

5.9	Packing, Storing and Transport

It shall be the Contractor’s responsibility to pack, store and transport all the material so that their physical properties do not deteriorate.

Every delivery shall contain a complete material list, a copy of which shall be sent in advance to the Project Manager.

The costs for packing, storing, handling and transportation shall be included in the bid price.

5.10	Testing

Before starting the manufacture, an inspection plan written by the Contractor showing the different inspection procedures shall be mutually agreed between the Contractor and the Project Manager.

The Contractor shall keep the Project Manager informed about the course of manufacture of materials and works, so that the inspection and testing can be performed in the presence of the Employer’s and the Project Manager’s representative.

Before every inspection and test supervised by the Project Manager the Contractor shall satisfy himself that the work is in all respects in accordance with the Specification ready for inspection and testing.

Routine test shall be performed in accordance with the relevant standards and according to instructions by the Project Manager.

Representative samples, selected at random, of all materials amongst lots ready for despatch, may be subject to tests in order to verify their conformity with Specification.

The tests shall be performed by the Contractor or his Sub-Contractors, and the costs are deemed to be included in relevant Schedules.

Testing of components shall be carried out to the satisfaction of the Employer.

All test results shall be documented in test reports which shall be delivered in triplicate to the Project Manager within 2 weeks after the tests have been carried out.

### 5.10.1	Shop Assembly

One complete tower of each tower type including step bolts and anti-climbing devices shall be manufactured and galvanized for shop assembly and erected in the presence of the Project Manager or other employers presentative. The Project Manager or representatives will check the component parts for proper fit and ease of assembly. Any defects shall be amended to the satisfaction of the Project Manager, before commencement of delivery.

### 5.10.2	Tower Test

For double circuit 132kV, one tower of each standard type complete with step bolts and anti-climbing devices shall undergo full scale testing in accordance with IEC Publication 652 “Loading tests on overhead line towers”, at the place of manufacture or at a testing station to be agreed upon.  The towers shall be erected on rigid foundations. If required by the Project Manager, the 330kV tower shall also be tested as described above for 132kV.

The Contractor shall provide a comprehensive testing programme which shall be subject to approval by the Project Manager prior to testing.

Each tower which will be tested shall prove compliance with the factors of safety stated in this Specifications without showing signs of failure or permanent distortion in any part.

During design checking and approval, the number and types of towers to be tested will be decided.  If a tower should fail to withstand the test loads, the Contractor shall re-test the modified tower at his own expense, if so required by the Project Manager.

No part of any tower submitted for tests shall be used as part of the delivery.  The tested tower members shall be marked and disposed in an approved manner.

The test reports shall include all the required documents according to the IEC publication 652.

Unless otherwise specifically approved, steel towers submitted for test shall be galvanized.

### 5.10.3	Testing of Mechanical and Chemical Properties of Steel

Steel samples shall be taken at random amongst lots of completely galvanized tower members.  These samples shall be tested in accordance with the standards agreed and approved for the project.

### 5.10.4	Galvanisation Tests on Tower Members, Bolts and Nuts

The uniformity of the zinc coating on galvanized steel articles shall be tested as specified in relevant standard.

### 5.10.5	Welding Tests

Welding tests shall be carried out in accordance with approved standards and to the approval of the Project Manager.

Guy wires shall be tested in accordance with IEC 888 and shall include Mechanical Tests and Zinc Coating Test.

6. 	MATERIAL SPECIFICATIONS, FOUNDATIONS

6.1	General

Foundations shall be designed for the relevant specified tower types for good and poor soils both in dry and fully submerged conditions and for rock, as applicable.

The responsibility for proving the adequacy of the foundation type at each tower site shall rest with the Contractor. Necessary soil surveys and tests shall therefore be undertaken by the Contractor in accordance with these specifications.

Parallel to soil investigations, in water-logged locations, the Contractor shall also make water tests (analysis) to ensure the application of the correct cement type.

Pile foundations or special foundation designs may be required in difficult locations or in exceptionally poor soil.

The Contractor is required to design, as necessary, for each type of tower, suitable foundations, including pile foundations if required.  Where existing foundation capacity is inadequate, foundations shall be re-built or re-placed in accordance with new soil classifications to be carried out by the Contractor.

The Contractor shall be free to propose alternative types of foundations providing these comply with all requirements specified.

6.2	Design Requirements

The design of standard foundations shall take the following parameters into account:

-	All loads transferred from towers with the same load combinations as for towers.

-	Weight of towers.

-	Relevant soil parameters.

-	Relevant safety factors.

-	Specified ultimate stresses allowable for concrete and steel.

Foundations shall be designed to make adequate provision for horizontal shear forces in the region of the ground line.

Allowance shall be made in foundation design for the effects of seasonal rains, drying out, cyclic loading and wind induced vibration of tower members.

For the design of guy anchors, the guy tension shall be assumed to act vertically upon the anchors.

In flooded areas the height of foundations for Monopoles towers above ground shall be about 1200 mm for 330kV towers and for 132kV towers to ensure protection of the steel against corrosive water.

The upper surface shall be slightly sloped to prevent accumulation of water.

The walls of the excavation for the foundations shall be undercut at their base where possible.

The minimum concrete cover for reinforcing bars shall be 50 mm for 330kV towers and appropriate cover for 132kV towers.

For 330kV towers, the minimum depth of the foundations shall be 1800. Appropriate design shall be made for 132kV towers.

In addition, under all reinforced foundations, for 330kV and 132kV towers, a blinding layer of concrete of 100 mm has to be laid.

For 330kV towers, all foundation concrete shall be designed with a height not less than 500 mm above ground. Appropriate designs shall be made for the 132kV towers to the approval of the employer.

For 330kV towers, all foundation concrete shall be designed with a height not less than 500 mm above ground. Appropriate designs shall be made for the 132kV towers minimum 300mm to the approval of the employer.

All concrete structures shall be designed in accordance with BS 8110, Structural Use of Concrete, and BS 4461, Cold Twisted Steel Bars for Concrete Reinforcement, or equivalent internationally recognised standard.

For 330kV towers, the maximum stresses in concrete foundation structures under the specified loading conditions, taking the relevant safety factors into account shall not exceed the values specified below; a similar design shall be made the bidder for the 132kV towers to the approval of the employer.

| Description (330kV) | Unit | Ultimate |
| --- | --- | --- |
| Tensile stress due to bending | kN/m² | 2070 |
| Bond stress, galvanised steel/ concrete | kN/m² | 1030 |
| Bearing stress | kN/m² | 20000 |
| Punching shear stress | kN/m² | 6900 |

6.3	Soil Classification

For design purposes the soil has been classified into five types as follows:

| Soil Class | Soil Density kg/km3 | Cone angle of uplift | Ultimate bearing capacity kN/m² |
| --- | --- | --- | --- |
| 1 | 2000 | 30° | 750 |
| 2 | 1600 | 25° | 350 |
| 3 | 1600 | 20° | 200 |
| 4 | 1600 | 10° | 100 |
| 5 | 1000 | 0° | 90 |

Soil class 1 is solid rock. Soil class 5 is submerged foundation; hence the density of soil and concrete shall be reduced. Soil classes 2, 3, and 4 are various types of earth. Relevant soil class has to be determined for each tower site based on results from soil tests carried out.

If it should prove advantageous, or if allowed for in the specifications for the lines on which works are to be carried out, the properties shown above for each soil class may be adjusted. Adjustments may also be permitted on the basis of new soil tests.  Any adjustment after soil investigation results are available shall be to the approval of the Project Manager.

6.4	Foundation Loadings

Ultimate loads derived from the tower design calculations for existing lines, including safety factors, shall be used in foundation design.

6.5	Foundation Types

### 6.5.1	General Requirements

Suitable types of foundations shall be designed for each soil class and tower type as necessary:

330kV Transmission Line

-	Type concrete pad and chimney for self-supporting suspension towers and all tension towers.

-	Rock foundations, for all tower types.

-	Reinforced concrete blocks, as guy wire anchors.

-	Grouted rock bolts, as guy wire anchors in solid rock.

-	Special foundations, i.e. raft type or piled type in very poor soil conditions, for all tower types when and if necessary.

132kV Transmission Line

Strain structures shall have flanged poles with pad and chimney foundations. The intermediate structures may have either directly planted poles or flanged poles with pad and chimney foundations. For sections where shallow rock is encountered or where construction are to be undertaken under outage conditions flanged poles with pad and chimney foundations are recommended.

For the standard tower types, the design of the foundations for the compression and the tension leg shall be the same.

Foundation design shall be modified when this is necessary due to ground water, or other complications, in order to provide the required factors of safety.

The upper surface of all types of concrete foundations shall be sloped in an approved manner to prevent accumulation of water and the whole exposed surface shall be rendered with concrete composed of one part of cement and two parts of sand.

Cement shall be of Portland or other approved composition conforming to internationally recognised standards. Recommended manufacturers mix ratios for particular concrete grade shall be used initially for mix design. Where concrete might be liable to chemical attack, sulphate resistant cement of approved type shall be used.

All aggregates shall be obtained from approved sources, and be clean and free of clay, earth, organic matter, salt or impurities.

The proportions of cement and aggregates to be used in the concrete shall be verified on the basis of tests by an independent laboratory, using aggregates from the same sources as those used by the Contractor.

### 6.5.2	Rock Foundations

For soil class 1 rock anchors may be used where good quality rock is encountered at or near the ground surface.

Rock anchors shall consist of deformed bars, not less than 25 mm in diameter for 330kV towers (similar design shall be provided by the bidder for 132kV towers), securely grouted in holes pre-drilled in the rock. Required number, depth and spacing of the bars will depend on the quality of the rock. The contractor's proposed solution shall in each case be approved by the Employer or the Project Manager.

If required by the Employer or the Project Manager selected rock anchors shall be tested at site. Payment of testing as ordered by the Employer, or the Project Manager will be made according to relevant unit prices in the Bill of Quantities.

If the Contractor should prefer the technique of placing stubs/concrete foundations in holes blasted in the rock, for economical or technical reasons, the holes shall be made in such a manner as to eliminate the possibility of serious cracking of the rock. The dimensions of the holes shall be approved, but the depth of the stub actually grounded into the rock shall in no case be less than 1000 mm for 330kV towers (The bidder shall provide designs for 132kV towers, and these shall be approved by the employer). The stubs shall be completely galvanised, except that it shall be permissible to cut off, on site, lengths at the bottom ends of the stubs where the upper surface of the rock is at or near ground level. The stubs shall be firmly keyed and grouted into the rock and shall be encased as for other types of foundations with the exception that the encasing concrete shall extend down to the upper surface of the rock.

The guy wires of the guyed suspension towers may be anchored by means of bolted rock anchors, provided that the rock is of a sufficient quality.

### 6.5.3   Pad and Chimney foundations

For type 2, 3 and 4 foundations pad and chimney will normally be required. Concrete spread footings of pad and chimney type can be used where the bearing capacity of the ground is at least 100 kN/m2 within a reasonable depth below ground.

Uplift resistance shall be based on the following.

Weight of foundation:

-	Weight of an inverted frustum of earth with a bottom area equal to the base of the foundation

and sides with an angle to the vertical (sexagesimal) as stated in the table.

-	The density of the soil shall be assumed as stated in the table.

-	The density of concrete shall be assumed to be 2200 kg/m3 in dry soil and 1200 kg/m3 in soil below the water table.

Vertical pressure:

-	In calculating the vertical pressure, the weight of soil over the foundation shall not be included.

The vertical pressure shall in no case exceed the ultimate bearing capacity of the soil as stated in the table.

Horizontal pressure:

-	The design shall make adequate provision for horizontal pressure at and below ground level.

The chimney shall be reinforced for the full uplift and shear loads.

The main concrete block shall be pyramidal in shape. To provide for soils with reduced bearing and/or uplift resistance, the base of the pyramid may be extended by means of a reinforced concrete pad.

The maximum angle between base and side of concrete foundation for uplift conditions shall be 70 degrees.

Pad and chimney foundations shall be employed with undercut excavation if possible. For 330kV towers, the undercut shall extend to a minimum of 300 mm outside the walls of excavation which shall be vertical. The bidder shall provide designs for 132kV towers.

The adhesion between the galvanized stubs and concrete foundation blocks shall be calculated to transmit 50% of the entire load to the foundation. Cleats, bolted on the stubs, shall transmit the remaining 50%.

The tower stubs, which shall have the same inclination as the tower leg member, shall extend into the main concrete block.

All steelwork below ground level (except concrete reinforcement rods) shall be completely galvanised and firmly keyed and grounded into concrete designed to withstand the load due to the specified conditions. Concrete shall be reinforced in order to ensure that the concrete stresses do not exceed the figures stated in above. Cover over reinforcement shall not be less than 50 mm.

### 6.5.4	Steel Grillage Foundations

Steel grillage foundations shall not be used for 132kV and 330kV lines.

The bidder shall provide similar designs for double circuit 132kV towers for approval by the employer.

### 6.5.5	Special Foundations (Pile Foundations)

Where ground conditions are unsuitable for the installation of the types of foundations described above, the Contractor will be required to decide to provide piled or raft or other special foundations as may be approved.

The total uplift, compression and horizontal forces assumed for the design of special foundations shall be those developed on the tower under consideration at the site on the line route.

6.6	Tower Leg Connection and Anchorage

For self-supporting towers, the connection of the tower to concrete foundations is by means of a steel stub angle. The stub angle shall have the same size as the leg member to which it connects and shall be hot dip galvanized for the full length.

The Contractor shall provide stub angles with holes for earthing and connections to tower body.

The anchorage of the steel stub angle in concrete foundations shall be provided by cleats bolted to the stub to provide adequate bond with the concrete.

All stub angles shall have at least two cleats at the lower end. Minimum embedded length at the stub angle shall be as required to resist pull-out.

The spacing between cleats shall be three times the flange width of the cleat. Minimum distance from upper cleat to the top of concrete shall be eight times the flange width of the cleat angle.

6.7	Materials

### 6.7.1	Concrete

Concrete shall have a minimum 28 day's strength of 20 N/mm2 in accordance with BS 1881, using minimum 300 kg cement/m3 concrete.

### 6.7.2	Steel Reinforcement

Steel reinforcement shall consist of hot rolled deformed bars conforming to the requirements of BS 4449:1969 grade of steel "High Yield" but with minimum yield strength of 3700 kg/cm2.

7. 	EARTHING AND SOIL INVESTIGATIONS

7.1	General

Towers shall be permanently and effectively earthed.

The individual tower footing resistance shall be less than 10 Ohms. In some areas tower footing resistance higher than 10 Ohms can occur, in such cases this must be Improved to less than 10 Ohms by copper earth rods or inter tower counterpoise connection.

7.2	Earthing Arrangements

Reference is made to tower earthing drawings, Earthing Counterpoise, Typical Arrangement.

Individual tower earthing shall be made with counterpoise cables type galvanised steel wire 7x3.25 mm.

All towers shall be connected to earthing counterpoise wires, each not less than 30m long.  The cables shall be connected to the tower legs and be arranged in radial formation at an angle of 45o to the centre line of the route.  The number of cables per tower shall be determined based on earth resistance measurements to the approval of the Employer or the Project Manager.

In exceptional cases the counterpoise cable may be extended in a ditch not projecting beyond the wayleave.  Alternatively, a coil of cable may be buried at the end of the standard-length radial counterpoise.  Coils shall be electrically connected to the radial counterpoise in an approved manner. The Contractor shall submit proposed connection detailed sketches for approval.

All towers, including the terminal tower, shall be connected by continuous counterpoise cable, which also shall be suitably connected to the substation earthing grid. The Contractor is responsible for liaison with substation Contractors for this installation.  It is the responsibility of the contractor to supply and install suitable clamps and connectors for connecting the counterpoise to the substation earth grid.

The counterpoise cable shall be everywhere buried in a trench not less than 800 mm deep along the route as far as possible straight. No shallower cable installation will be accepted. Care shall be taken to avoid interference with existing buried cables or pipes.

Terminal towers shall be provided with additional connection devices for connection to the continuous counterpoise.

7.3	Measurements and Tests

Where earthing resistance measurements are to be carried out, the method of measurement and type of instrument shall be subject to approval by Project Manager. The measuring instrument shall have a valid calibration certificate. No measurement results will be accepted before this instrument approval is granted. Based on these measurements, it will be decided if and where counterpoise and extended counterpoise shall be installed to improve the earthing resistance. The Contractor will submit improvement proposals to be approved by the Employer. All earthing measurements shall be carried out before the overrunning earth wires are erected.

The measurements shall also be duly recorded on the tower footing earth resistance profile. This record(s) shall also be submitted as part of As-built documentation.

7.4	Counterpoise Wire

Wires for connecting towers to earthing, wires for coil and radiating earth conductors and continuous counterpoise shall be type galvanised steel wire 7x3,25 mm, with cross-section 58,0 mm2, in accordance with BS 183.

The steel grade shall be 350.  A higher grade will result in a stiffer wire more difficult to bend and install and therefore shall not be accepted.  This wire must not be confused with the overhead earthwire as specified under informative data for Conductor & Earthwire.

7.5	Connections

The counterpoise shall be directly connected to the steel towers with bolted connectors of an approved material suitable for use with the counterpoise. The counterpoise connection point or points to the tower shall be of robust assembly and utilise anti-vandal bolts.

Connections to the substations earthing grid shall be made by compressed clamps or bolted connectors of approved design.

Towers shall be provided with adequate devices for connection of counterpoise.

For reinforced concrete foundations, the foundation bolts (if any) and the reinforcement steel shall be connected electrically to the earthing counterpoise.

At the approach of the counterpoise cable to the tower connection, the cable shall be buried under the coping of the concrete foundation box.

7.6     Scope of Works and Specifications for Soil Investigations

The scope of works of particular interest at the moment comprises subsurface soil investigations, laboratory testing of the obtained soil samples to determine the strength of the soils and general description of soil types along the line routes for the purpose of foundation classification and selection.

In view of the foregoing, site soil investigations and laboratory testing are required to be undertaken for the planned line routes at specified locations to determine the bearing capacities of the soil strata and other relevant soil engineering properties. General description of soil types and variations is required to be done in between specified locations for the entire line routes and two substation sites.

### 7.6.1 Preamble

The tenderer is advised to visit the sites and satisfy oneself as to the extent and nature of work.  The Contractor must conform to the instructions of the Engineer in carrying out all the required soil tests.

When deemed necessary the geotechnical contractor shall be required to perform sub-soil tests at any other selected would be tower locations, other than those indicated in the schedule, to the depth and by method of test specified by the ZESCO Project Manager or his designated proxies. The contractor may be required too, to make arrangement for comprehensive soil investigations to be carried out at any specified tower site including deep boring and laboratory analysis of undisturbed samples. The details of performing the test, tools and equipment to be used, shall be submitted to ZESCO Project Manager for approval. The sub-soil tests shall be carried out by the method as stated hereafter, under the supervision of a named qualified person.

All tests shall be carried out by an approved soil testing laboratory.

The contractor shall take sufficient care of the excavated trial pit and shall be responsible for any subsidence or failure due to insufficient care being taken in his examination of ground conditions prior to carrying out of the tests.

The results of all soil tests shall be submitted to ZESCO Project Manager in approved standard format together with proposals for each location investigated as regards the employment of a determined soil bearing capacity. A record shall be kept of each site location investigated including details of the strata of the ground throughout the depth of excavation, the presence or absence of water during investigation and liability to seasonal flooding, nature of ground (swampy or dambo) together with results of tests carried out and all other relevant information.

Where the transmission line traverses through areas of expansive clays like black cotton soils, the geotechnical contractor shall apart from Standard Penetration Test, propose and conduct other test for determination of bearing capacity of the soil. Care must be taken as black cotton soils can be very stiff in dry condition and can be very soft or liquefy under moist conditions.

7.6.2 Field Geotechnical Investigation and Sampling for Laboratory tests

Tests shall be conducted at predetermined, surveyed and pegged locations at the project site. The Contractor shall excavate trial pits up to 5 meters (or up to bedrock) in order to undertake Geotechnical field tests as specified. The Contractor shall submit a final report with actual test results from the sampling locations.

The data obtained from each sub-soil test shall include date of test, structure number/ station, ground level and surface conditions, test method, sample description, limit of strata, ground water level, soil classification up to the depth of sub-soil test and results of laboratory testing of samples. The data thus obtained shall show the nature and extent of the soil strata over the area under consideration. The contractor shall propose in his Geotechnical report, the recommendation for the types of foundations for each location based on the soil bearing capacity as determined from soil and laboratory tests.

General description of soil and vegetation shall be given for areas between consecutive test locations as regards susceptibility to waterlogging and flooding. The consultant shall include in the report a discussion of his findings especially in cases where ground conditions are very adverse and could propose special foundations.

### 7.6.3 	Soil Augering and Sampling

Shallow boring by rotary drilling rig and soil auger to maximum depth of 5.0m may be required depending on site conditions. The soil shall be classified in the field. Selected small and large samples shall be submitted to the laboratory for analysis as instructed by ZESCO Project Manager.

Chemical Analysis

At selected locations, especially areas prone to seasonal flooding, the contractor shall determine the concentration of sulphates, the degree of alkalinity in the soil and ground water and chlorides as CL- at depth specified and when required by ZESCO Project Manager. The values of sulphate concentration shall be expressed in per cent of SO4 per million for sulphate in soil and in parts of SO4 per million for sulphate in ground water. Alkalinity shall be expressed as a PH and parts CaCO3 per million and the CL- content of water in soil as parts per million (ppm).

### 7.6.4 	Data Obtained and Logging

The data obtained from each sub-soil test shall include date of test, structure number, station, ground level and surface conditions, test method, sample description, limit of strata, ground water level, soil classification up to the depth of sub-soil test and results of any laboratory testing of samples. The data thus obtained shall be prepared in approved standard form to show the nature and extent of the soil strata over the area under consideration. These shall then be compiled and submitted to the project manager as complete soil investigation report. Determination and selection of foundation type shall be the responsibility of ZESCO. However, the contractor shall give in his soil investigation report, THE RECOMMENDATION FOR EACH LOCATION INVESTIGATED, THE SOIL BEARING CAPACITY as determined from soil and laboratory tests. General description of soil and vegetation shall be given too for areas between consecutive test locations as regard vulnerability to water logging, flooding, and description of dambo areas, rocky or hilly areas, nature and type soil especially taking note of expansive clays so that a close to reality interpolation and extrapolation of soil properties can be made for intermediate areas. The contractor shall include in the report a discussion of his findings especially in cases where ground condition are very adverse and would call for special foundations.

### 7.6.5 	Test Locations and Accessibility

The specified field tests shall be conducted at predetermined, surveyed locations. UTM coordinates will be availed to the Contractor for the location of the test sites. The contractor shall be required to have or hire the services of GPS for easy identification of the coordinated and pegged locations in accordance with the provided for UTM coordinates.

Soil investigation Tests shall be done at every proposed tower location subject to approval by ZESCO Project Manager of location to be investigated.

### 7.6.6 	Safety

High Safety Standards shall be observed for the whole duration of works.

7.6.6 Geotechnical Tests and Associated Engineering Parameters

The following table below outlines the relevant geotechnical tests that need to be undertaken and the associated engineering parameters:

| Item | Geotechnical Test | Engineering Parameters | Aim of Test |
| --- | --- | --- | --- |
| 1 | Atterberg Limit | - Liquid limits, WL - Plastic limit, WP - Plasticity Index, IP - Shrinkage limit, Ws | Soil consistency over a range of different moisture contents |
| 2 | Particle Size Distribution | - Coefficient of Curvature, Cc - Coefficient of Uniformity, Cu | Coefficient of Curvature, Cc Coefficient of Uniformity, Cu |
| 3 | Moisture content | - Moisture Content, w - Degree of Saturation, S | To assess effect of water on most engineering characteristics of soil |
| 4 | Soil unit weights | - Bulk Density, Ɣb - Dry Density, Ɣd - Specific Gravity, Gs | Basic soil engineering properties and classification |
| 5 | Shear Strength tests for soil | - Internal angle of Friction, φ - Cohesion, c | To assess the resistance of soil to deformation |
| 6 | Maximum Dry Density and Optimum Moisture Content of soil | - Density (kg/m3) - Moisture content (%) | To assess the suitability of the soil for backfilling and compaction during construction of foundations |
| 7 | Soil Bearing Capacity | - Bearing capacity, kPa | Field test to determine capability of sub surface soil to support structural loads; otherwise use of pile foundations would be recommended |
| 8 | Uniaxial compressive Strength for rock samples | - UCS, kPa | To assess the compressive strength of any encountered rock stratum |
| 9 | Consolidation test | - Coefficient of consolidation, Cv - Compression index, Cc | To determine settlement characteristics of subsurface soil |

    - Field work scope

| S/N | DESCRIPTION |
| --- | --- |
| 1 | Mobilisation and Demobilisation to/from site including transportation of samples |
| 2 | Standard Penetration Tests - SPT (N-Value) including excavating (and backfilling) of trial pits (holes) or augering to determine Soil Bearing Capacity to the depth of 5.0m below ground level |
| 3 | DCPT (When necessary) |
| 4 | Geotechnical description of the soils profile to a maximum depth of 5.0m – Logging trial pits |
| 5 | Trial pit Sampling for soil classification from each test pit |

    - Laboratory work scope

| S/N | DESCRIPTION |
| --- | --- |
| 1 | Particle Size Distribution or Sieve analysis soil samples |
| 2 | Atterberg Limits |
| 3 | Unit weights and Moisture contents for soil recovered from Trial pits |
| 4 | Maximum Dry Density (MDD) and Optimum Moisture Content (OMC), Natural Moisture Content, Moisture-Density relationship |
| 5 | Shear Strength tests (undisturbed soil samples) (Triaxial / Direct Shear test) |
| 6 | Uniaxial Compressive Strength (UCS) tests from rock samples recovered from Trial pits (if any) |
| 7 | Oedometer tests for ground settlement characteristics (with all associated parameters) |
| 8 | Chemical Analysis of Water (Chlorides, Sulphates, pH) |

### 7.6.7 Contractors experience and Tools

The prospective contractor (bidder) shall provide the following information along with the bid.

  - Curriculum vitae of proposed lead geotecnical engineer.

  - Curriculum vitae of any other geotecnical engineer.

  - A list of proposed equipment and tools (for vehicles state make, type and condition)

  - Description of GPS and copies of any calibration certificates GPS is for navigation and identify/tracing of coordinated / pegged points supplied by Employer.

  - Company’s profile

  - Provide access to the Employer for the inspection of contractor’s survey equipment and tools.

As guide to the item 1 above, the Employer shall require the following qualification and experience for the key staff and personnel for the Project.

Lead Geotechnical Engineer

- A minimum academic qualification of a degree in land civil engineering or a similar field

- Have a minimum working experience of 5 years soil investigation and demonstrated knowledge of soil laboratory and material testing related to buildings, roads and transmission lines works.

- Be fully conversant with the use of proposed equipment and be able to give preliminary results of soil properties at site without recourse to head office.

Geotechnical Engineer

- A minimum academic qualification of a degree in land civil engineering or a similar field

- Have a minimum working experience of 5 years in soil investigation and demonstrated knowledge of soil laboratory and material testing related to buildings, roads and transmission lines works.

- Be fully conversant with the use of proposed equipment and be able to give preliminary results of soil properties at site without recourse to head office.

Geotechnical Technician

- A minimum academic qualification of a Diploma/Technologist in Civil engineering or a similar field

- Have a minimum working experience of 5 years conducting Geotechnical Investigations and other geological engineering activities and studies. Have a minimum working experience of 5 years’ soil investigation and demonstrated knowledge of soil laboratory and material testing related to buildings, roads and transmission lines works.

Be fully conversant with the use of proposed equipment and be able to give preliminary results of soil properties at site without recourse to head office.

Tools

- The soil investigation contractor shall provide, maintain and operate suitable and appropriate instruments and auxiliary equipment and materials, commensurate with the various tasks and precision requirements of the soil investigation Works.

- Type of field/laboratory work and equipment intended to be used by the Contractor for the performance of this Work shall correspond to the nature of the described Works and shall be in accordance with the standard investigation and material testing procedure and used code of practice shall be quoted.

- All equipment, instruments, materials and auxiliary equipment shall be in perfect operating condition. Nevertheless, prior to the start of soil investigation activities, equipment, instruments, etc, shall be checked by the geotechnical engineer as to their proper functioning and accuracy.

- During the Soil investigation period, the survey instruments shall be checked, if necessary, adjusted at regular time intervals.

- Instruments/equipment which have suffered from use, damage or accidents to a degree making them unfit for further use at the site, shall be removed from the site and replaced immediately by the contractor.

- The contractor shall have its own suitable transport for its personnel on site. The transport shall be suitable for harsh terrains; four-wheel drive vehicles with a high wheelbase are preferred. The contractor shall therefore state the type of vehicles they intend to use for this project.

- Apart from the above, the contractor is expected to have on site standard outdoor tools such as machetes, axes, etc.

It is the total responsibility of the contractor to ensure that all his equipment is in good working order.

### 7.6.8 Completion period

The contractor shall be bound to carry out and complete the above works within 45 days from the date of contract effectiveness.

### 7.6.9 General environmental guidelines for wayleave clearing.

Introduction

A Wayleave is a swath or area of land appropriately cleared of vegetation under a power line or any such infrastructure.  A line-of-sight bush clearing (Not more than 3.0m wide) is done in virgin vegetation for the purposes of survey.

It is against this background that these guidelines are developed for the purpose of controlling and checking the contractor engaged in the exercise under different line systems.  The recommended width of vegetation clearance should be equal to double the height of the line structure under which it falls.  A 330kV transmission line for instance, would ideally have a swath of 50m of cleared vegetation, thus 25m on either side.  The obvious need for this exercise cannot be over emphasized for the obvious problems arising from vegetation interference on the system.

Wayleave Sizes

Transmission Line					Size (m)

330 kV							50

132 kV							32

66 kV							30

Wayleave Variations

The above wayleave sizes are supposed to be followed under normal practice for the protection of the transmission and distribution electrical systems.  However, variations arise where these lines traverse certain protected and some public or privately-owned properties like farms, national parks, forest reserves, heritage and cultural sites.

Wayleave Permits

The trend in wayleave management has changed due to many factors that include but not exclusive to the following:  increased public awareness on environmental issues, private land ownership, and improvements in the local legislation that regulate natural resources management.

It is against this background that in certain areas special permits should be obtained before any vegetation management in a wayleave can be conducted.  The permits that should be sorted out include those but not exclusive to:  Forestry Department, National Heritage Conservation Commission, Zambia Wildlife Authority, farmers and other private entrepreneurs.

Waste Management

- Do not litter near water sources.

- Use pit latrines for human waste.

- Use pits to dispose litter and cover pits after use.

- Consult local leaders for waste disposal sites.

Vegetation Clearing

- Stamp vegetation and not uprooting.

- Cut vegetation to an appropriate height as opposed to burning.

- Seek permission to clear vegetation in private properties as opposed to imposed access.

- Trim vegetation in restricted areas as opposed to cutting and complete removal of vegetation.

- Make sure you leave some growth at least 4 – 6 cm above the ground.  This will minimize soil erosion.

- Remove all the plant growth around electric poles especially wooden ones.

- Do not use fire to clear wayleaves because this may result in power failure and destruction to vegetation.

- Do not use chemicals, such as herbicides for wayleave clearance to avoid pollution

- Treat all private property with care for security reasons and avoid trespassing.

Protected Areas

- National Parks/Forest Reserves are protected areas with wildlife and forestry resources.  In such areas do not light fires unless in designated areas only for cooking

- Do not litter in a national park.

- Do not poach or kill any animal, bird or other forms of wildlife.  Wildlife/Forestry Officers have the right to search/inspect your car if they suspect contravention of the law.

- When the contravention of the law has occurred, the company and/or an individual who has contravened the law will be held responsible for such contravention.

- Do not cut fresh trees for camp use.  Only use dry or dead trees.

### 7.6.10 Co-ordinates

Refer to the line route maps and substations co-ordinates in the appendices.

8.	CONSTRUCTION WORKS

8.1	330kV and 132kV Routes

The line routes are shown under line routes co-ordinates and drawings.

8.2	Profile Survey

All surveying of longitudinal profiles and setting out shall be carried out by the Contractor, to the approval of the Project Manager.

The Contractor shall be responsible for the location of tower positions on the profiles in accordance with this specification and all setting out for construction, all to the approval of the Project Manager.

Where the line route is running parallel to another similar line the towers shall be in step with the existing towers where possible.

The Contractor shall be responsible for checking the correctness of longitudinal profiles when surveying for tower site pegging, and carry out correction of plans, profiles, and design accordingly.

Wherever survey pegs have been removed or lost, the Contractor shall be responsible for their accurate replacement.

The line shall basically run along the line route shown on maps in scales 1:50,000 or 1:250,000 that will be provided by the Employer as part of his instructions to the Contractor.  Any minor and major deviations from the planned line route shall not be accepted, unless approved by the Employer.

Longitudinal profiles and surveying data MAY BE provided by the Employer.  In such cases setting out shall be carried out by the Contractor as described above.

Before construction commences the contractor shall provide the Project Manager (at not less than ten (10) days’ notice) with lists of the towers that have been pegged and are available for inspection.

The contractor shall provide for each type of suspension guyed tower location four survey marks (preferably iron pegs in concrete) two in the transverse and the other two in the longitudinal direction through the tower location. These marks shall be used for alignment of towers during erection.

8.3	Wayleaves

The Contractor, according to his own judgement, shall construct all access roads (including approach roads and obstacle bypass roads) necessary for the construction of the line. The Employer will not make any additional payments for the construction of such access roads.  At the end of line construction, the wayleave and other access roads to towers shall be left in an acceptable condition for future use by the Employer’s operation and maintenance personnel.

Obtaining of wayleaves for access to line right-of-way shall be the responsibility of the Contractor without any extra charge to the Employer.

All necessary authorizations, permits and approvals as may be required to ensure access for construction, storage and transportation of materials/equipment and all other authorization as may be required for the construction of the line will be the responsibility of the Contractor.

The ZESCO standard wayleave width for 330kV is 50m wide and 132kV is 32m wide. This standard is for horizontal configuration of line phase conductors.

8.4	Access for Construction

The obtaining of wayleaves and access permits along the wayleave, but not transport routes and access tracks leading into the wayleave will be provided by the Employer to enable the Contractor to carry out the erection of the lines.  The Employer will permit the Contractor to use existing access routes and tracks where and if such facilities exist.

In general, a wayleave road or access track shall be built by the Contractor along the line route.  This will be the main access for construction and maintenance, and it will, unless impossible, be located within the wayleave.

The Contractor shall make all necessary arrangements for approach and access roads (in addition to the one along the wayleave) with the property owners, but if any difficulties arise the Contractor shall inform the Project Manager. The employer shall not allow for additional payment arising from the referred to approach and access roads.

If the Employer is unable to provide the above-mentioned wayleaves in time, the construction programme shall be modified by agreement with the Project Manager.

All handling of materials to the site which is rendered necessary by restricted access rights must be agreed with the Project Manager and paid for at the daywork rates stated in the Bill of Quantities.  Restricted access rights may arise because of specific wayleave restrictions, but not because of difficult ground conditions.

The arrangements for the removal, where necessary, of obstruction such as cultivated trees, pipes, field drains, village houses or huts, telephone, telegraph, and power lines, preventing the erection of the permanent works will be made by the Contractor at the expense of the Employer at the given daywork rates, except where such works shall be covered by specified unit prices.

The Contractor shall be responsible for the maintenance of fences and farm gates so the satisfaction of the property owners or occupants.  On completion of the Contract Works all fences and gates shall be left in the same condition as they were found.  Where additional permanent gates become necessary in existing fences to provide access to the Site, they shall be supplied and installed by the Contractor to approval at the rates specified in the Bill of Quantities.  All permanent gates shall be supplied with a standard lock and key, including a chain to facilitate locking.

The Contractor shall, at his own expense, will make arrangements to warn in reasonable advance any owner or tenant of the impending construction work in order to ensure that there are no new developments within or near the wayleave.

The Contractor shall, at his own expense, make good to the reasonable satisfaction of the Project Manager, authorities, owners and tenants concerned, all land, property, roads, tracks, bridges, drains, fences, walls, hedges, gates and the like which are damaged or disturbed during the execution of the Works and shall remove all surplus construction material after erection. Temporary provisions shall be made by the Contractor to prevent straying of, or damage to, livestock during the execution of the Works and until the permanent reinstatement of fences, walls, hedges, gates and the like is completed. The Contractor shall be held responsible for any damage to livestock due to failure to comply with the above requirements.

In the event of any dispute or complaint arising between the owner or occupant of property and the Contractor over reinstatement of fences or gates, damage to crops, or over other works on his property, the Contractor shall attend to the matter properly and immediately inform the Employer of the circumstances.

8.5	Plan and Profile Drawings

Profiles shall be drawn to the following scales:

-	Horizontal scale:	1:5,000

-	Vertical scale:		1:500

Ground detail shall be shown to within 30m on either side of the centre line, plus permanent building detail within 50m.

A north arrow shall be shown for each plan and profile sheet.

Location and description of benchmarks and other ground control survey monuments shall be shown.

Route or section length on plan centre line, every whole kilometre with a heavy line, and tick mark at 100 metre intervals shall be shown.

Survey sketches of power and telephone lines crossing the centre line shall be made and show the following details:

-	Voltage,

-	Number of towers,

-	Rough sketch of tower configurations,

-	Centre of the two nearest towers on the left and right side of the centre line, even when these are further away from the centre line than 50 m,

-	Angle between crossing line and profile centreline,

-	Elevation of suspension points of conductors and earth wires.  Sag of conductors between two structures,

-	Temperature at time of survey,

-	Centre line profile of the crossing line shall be shown.

Side profiles shall be shown for 10m left and right of centre line, only if side slope is 5 % or greater.

Side profiles shall be shown at 20 m up-slope from centre line in all cases.

Profile lines shall be indicated as follows, looking in the direction of higher station number:

-	Centreline profile:	solid line			(_________)

-	Up-slope profile:	dotted line, 10 m from C/L	(..................)

-	Up-slope profile:	dashed line, 20 m from C/L	(-------------)

The Contractor shall also provide a masterplan, preferably to scale 1:50,000 to correlate all survey sheets, indicate main communications, property boundaries, trigonometrical stations relative to the line route, and tabulate all data required for pegging of tower positions, including angle points with the appropriate measurements and directions and angles of deviation.

8.6	Tower Plotting and Design

### 8.6.1	Clearances

The structures shall be located to provide not less than the minimum electrical clearances under the maximum sag conditions.

### 8.6.2	Tower application charts

Application charts shall be prepared and submitted for each tower type.

Each application chart shall show the minimum and maximum weight span and wind span capability for a specific line angle at the design span of 450 m for the 330-kV line and appropriate design span for the double circuit 132kV.

### 8.6.3	Sag template (if applicable)

Before submitting profiles for approval, the Contractor shall provide the Project Manager with sag templates based on the range of equivalent spans required.  Each template is to be clearly endorsed with the design loading conditions, particulars of conductors, equivalent span and scales which shall be appropriate to the scales of the relevant profile drawings.

The sag templates shall be used in the design of the transmission line to determine graphically on plan and profile drawings the location and height of structures and show the lowest conductor at the maximum temperature specified.

Sag data for preparation of the above curves shall be shown on drawings submitted with the templates.

The sag templates shall be made of heavy-duty transparent celluloid or plastic material. These templates shall be part of the As-build documentation.

### 8.6.4	Tower Plotting

The contractor shall train the employer’s staff attached to the project in the use of the software used for design. This shall be part of the scope of supply. Towers shall be plotted on the profile in the most optimum location considering both engineering and economics.  Considerable study and several layouts may be required in rough terrain to determine optimum tower location.

In order to maintain clearances, uplift, insulator swing and structural loadings within required limits, the location of each tower shall firmly conform to the requirements set out in the specifications.

Structures shall be located on plan view with correct stationing by scaling along the centre line from a reference point of known stationing.

The Contractor shall submit to the Project Manager for approval, copies of structure lists, upon which shall be indicated: number of towers, type of tower, deviation angle, actual span lengths, weight and wind span, intersection lengths, type of foundation, leg extensions, line attachments, number of joints, number of spacers, dampers, grounding and a free space for notes of crossings and remarks.

### 8.6.5   PLS-CADD Data Requirements

The Contractor shall provide survey data and profile & plan drawings in PLS-CADD format.

Terrain and obstruction data shall be described by coordinate position and feature characteristic collected by the Contractor.  The Contractor shall measure the position of any features or objects as necessary to define the project.  The method of acquisition shall be proposed by the Contractor and may include ground survey with total station and data recorder, aerial photogrammetric surveys, or remote sensing (i.e., lidar) surveys that produce horizontal and vertical positions with codes to describe different features. The width of coverage shall be a minimum of 30 meters left and right from the route centreline.

The deliverable documents shall include:

- CAD Drawing file for Plan and Profile with tower locations on CD-ROM

- DTM (Digital Terrain Model) file on CD-ROM

- A PLS-CADD backup (“.bak”) file containing all the above.

(a)	CAD Drawings

Planimetric drawing for the digital image files shall be submitted in DXF format; however, the original DWG used to create the DXF shall be submitted as well. The planimetric drawing shall be in the coordinate system, as approved by the Project Manager.

(b)	DTM Data

The Contractor shall provide the survey data in an ASCII text file (or files) with one data point per record (line) in the file.

8.7	Site Inspection, Tower Locations

Each tower site as plotted on the plan and profile drawings shall be inspected to assure optimum location for safety of operation and line reliability as well as optimization for construction and maintenance.

Areas subject to water or wind erosion shall be avoided where possible, in particular on selection of tension towers.  Areas where the risk for damage to tower foundations by torrential floods is obvious shall be avoided.

The Contractor shall locate and peg the centre point of all towers to the satisfaction of the Project Manager and shall provide and install a suitable temporary marker carrying the tower number.  Each tower location shall be defined by its longitudinal coordinate as established by measuring the distance to an adjacent survey peg with known coordinates.  The Contractor shall keep a record of all tower locations “as installed”.

The Contractor shall locate the tower foundations from the tower centre point and shall perform all additional measurements necessary to facilitate construction.  In particular, the Contractor shall measure the slope of the ground at each tower location and he shall, on the basis thereof, select and propose tower leg extensions as required.

The Contractor shall provide all site inspection data to the Project Manager, with the completed plan and profile and structure list, for approval.

Unless otherwise specified straight line, towers shall always be installed so as to have the crossarm at right angles to the line direction, and angle structures to always have the crossarm bisecting the line deviation angle.

8.8	Bush Clearing

The clearing will consist of the removal and disposal of trees and other vegetation, houses, huts, ant hills, etc.  All clearing and trimming of trees that pose danger to the line within the right-of-way shall be as specified herein, or specifically directed by the Project Manager.

The width of the strip may vary according to the mean height of the bush or forest and shall be determined by ensuring that any tree after falling will not be less than 20m clear of the tower centre line for 330kV line (appropriate design shall be made by the bidder for double circuit 132kV line to the approval of the employer), or standing trees would not cause flashover from a conductor deflected up to 45o from the vertical.  In determining the flashover clearance and in estimating the mean height of the bush or forest, due allowance shall be made for seasonal growth.  Tree stumps are to be uprooted and removed to prevent regrowth. Shrubs shall be cut down to 30cm height above ground. The attached drawings show the required clearing of the wayleave.

The Contractor shall not clear the line route by bull-dozing or other mechanical equipment unless approval to do so have been obtained from the Employer or the Project Manager, property owners or occupants, and care shall be taken to avoid unnecessary removal of topsoil, damage or interference to roads, ploughed lands, water courses, contours and land ridges to avoid soil erosion.  Should such damage be incurred, the Contractor shall make repairs at his cost where necessary to the satisfaction of the owners or occupants of property. Where mechanical equipment is employed for bush clearing it shall be assumed that such costs are built into the contractor’s costs and the employer shall not be required to make additional payment for the use of such equipment. The employer is aware that the density of trees and the size of the trees varies along the line route. The bid shall therefore be understood to include the costs of clearing the entire line route. The employer shall not allow for additional payment arising from, say density and size of ant hills and density of trees or the size of trees. Bidders are encouraged to make a fair assessment of the site during the mandatory visit to the site.

All timber and bush shall be removed to the outer limits of the cleared strip, except when used as erosion protection in seasonal stream courses.

Anthills shall be smoothly levelled off to a slope not exceeding 15o, wherever they may cause ground clearance problems.

The vehicle access track along the length of the cleared line route, to the tower sites, shall be used where possible for purposes of maintenance.  Any alternative route for the track shall be agreed with the Project Manager.  When using or maintaining tracks, care shall be taken to avoid erosion and the forming of water courses that can develop into a gulley.

If required, disposal of timber, brush, etc. other than as stated above, or any land drainage or bridging or prevention of soil erosion or similar special work arising because of the works on the transmission lines shall be executed to approval at rates to be agreed.

8.9	Crossings

The relevant national regulation shall be complied with at crossings of roads, rivers, streams, other power lines, communication lines and railways.  All necessary permits will be obtained by the Contractor. No additional payment shall be made for any temporary guarding or scaffolding required for erection of the conductors at such crossings.  Existing power lines will have to be shut down before stringing of conductors and earth wires at crossing points.  Where possible, this work shall be carried out on weekdays, but where necessary it may have to be undertaken on Sundays or public holidays.  In any event, the work shall be carried out only under the supervision of the Employer or their representative, and the Contractor shall give a minimum of ten days clear notice of the dates on which each crossing is to be affected.  No extra charge, in addition to the prices quoted in the Bill of Quantities, for work required to be carried out on Sunday or public holidays will be accepted.

It is the responsibility of the contractor to make all the necessary arrangements with the relevant authorities when making a crossing.

8.10	Material Transport and Handling

All transport and all handling of materials from Employer’s or Contractor’s storages or depots to each tower site, shall be carried out by the Contractor.  Prices for this shall be included in the relevant Bill of Quantities.  The Contractor shall provide all vehicles, machinery, tools, and equipment necessary to carry out the Contract Works.  He shall also be responsible for the adequate supply of fuel, lubricants, and spare parts.  All materials shall be handled carefully to avoid breakage and damage.  The Contractor shall be responsible for such damage and for the delivery of the correct types and quantities of material to each work location. All breakages and damages will be replaced by the Contractor at his own cost.

The Contractor shall be responsible for timely delivery to site of materials supplied by himself.

Costs for transport and handling of materials, from storages to sites, shall be included in the unit prices for construction works.

8.11	Soil Investigations

### 8.11.1	General

When deemed necessary, Contractor shall be required to perform sub-soil tests at any tower location to the depth and by the method of test specified by the Project Manager.  The details of performing the test, and for tools and equipment to be used, shall be submitted to the Project Manager for approval.

The sub-soil tests shall be carried out by the method as stated hereafter under the supervision of a qualified person, who shall be subject to approval of the Project Manager.

All tests shall be carried out by an approved soil test laboratory. No tests carried out by an unapproved laboratory shall be accepted.

The Contractor shall be responsible for any subsidence or failure due, in the opinion of the Project Manager, to insufficient care having been taken in his examination of ground conditions or in installation of the foundations.

The results of all soil tests shall be submitted to the Project Manager in an approved manner together with proposals for each tower site for employment of a class of standard foundation as given under Specification of foundations or the need for a special or modified standard foundation design.  The class of foundation proposed for each tower site shall be approved by the Project Manager PRIOR TO commencement of foundation construction.

A record shall be kept of each foundation installed including details of the strata of the ground throughout the depth of excavation, the presence or not of water during construction and liability to seasonal flooding, together with results of tests carried out and all other relevant information.

When required by the Project Manager the Contractor shall plan for a comprehensive soil investigation to be carried out at any specified tower site, including deep borings and laboratory analysis of undisturbed soil samples and for a report and recommendation to be submitted as described under Special Foundation.  The Project Manager may require that this work shall be carried out by an approved sub-Contractor at rates to be agreed.

The Contractor’s costs for soil investigations are to be included in the prices for Foundation Works.

### 8.11.2	 Standard Penetration Test

This method shall be used for sub-soil test to the depth of not more than 5m from ground level, or otherwise approved by the Project Manager.  The test shall be performed in such a manner that the number of blows per foot of penetration can be obtained at every change in stratum but of interval not greater than 1.0m.  The data obtained shall be prepared in final approved form to show the penetration record including recommended bearing capacity of soil along the boring depth.

The recovered split spoon samples shall be described and classified in the field.  Selected samples shall be submitted to the laboratory for analysis as instructed by the Project Manager.

### 8.11.3	 Soil Augering and Sampling

Shallow boring by rotary drilling rig and soil auger to maximum 5m depth.  The soil shall be classified in the field.  Selected samples shall be submitted to the laboratory for analysis as instructed by the Project Manager.  When directed by the Project Manager large samples shall be taken from the excavated soil and submitted to the laboratory for analysis as instructed by the Project Manager.

### 8.11.4	 Chemical Analysis

At selected locations, the Contractor shall determine the concentration of sulphates, the degree of alkalinity in soil and ground water and chlorides as C1- at the depth specified by the Project Manager or his representative.  The values of sulphate concentration shall be expressed in per cent of S04 for sulphates in soils and in parts of S04 per million for sulphates in ground water.  Alkalinity shall be expressed as a pH and parts CaC03 per million and the C1- content of water in soil as parts per million (ppm).

### 8.11.5	 Data obtained.

The data obtained from each sub-soil test shall include date of test, structure number, station, ground level and surface condition, test method, sample description, limit of strata, ground water level, soil classification and up to the depth of sub-soil test and results of any laboratory testing of samples.  The data thus obtained shall be prepared in final approved form to show the nature and extent of the soil strata over the area under consideration and submitted to the Project Manager.  Selection of foundation type shall be made for each tower foundation to suit its site conditions.  The Project Manager reserves the right to make final decision of foundation type for each tower site based upon his judgement of the nature of sub-soil conditions or other factors affecting construction or operation of the transmission line.  All the sub-soil tests described under this Clause shall be made as soon as possible after award of the Contract, and the submission of the test results shall be made within three months after award of the Contract.

8.12	Installation of Foundations

### 8.12.1 General

The Contractor shall determine the final location of each tower, survey the tower site, select the proper leg extensions necessary to provide tower height indicated in the plotting and select the type of foundation to be installed.

Details of the Contractor’s foundation classification, legs and foundations selection shall be submitted to the Project Manager for his approval.

The Contractor shall act as a complete construction organization furnishing all supervision, labour, tools, camps, storage yards, apparatus, equipment, and conveyances necessary for the specified works.

The Contractor shall furnish all the cement, aggregate, water, steel reinforcement, forms bitumastic coating, selected earth borrows, gravel or stone base, riprap material, foundation piling, welding rods and all other material required for the work covered by these Specifications.

The Contractor shall provide for storage of all materials to the extent required, shall haul, and distribute all materials to the points where they are to be erected in the transmission line and shall erect the materials in accordance with these Specifications and Drawings. Storage yards shall be kept neat and clean, and growth of grass and weeds shall be controlled.

The Contractor shall, without additional compensation therefore, coordinate and join all the various subdivisions of the work and produce complete erected foundations.

All works shall be done and completed in a thoroughly workmanlike manner in accordance with best modern practice for construction of transmission lines, notwithstanding any omissions from these Specifications or Drawings.

### 8.12.2	 Setting Out

Setting out of foundation positions shall be related to tower centre.  The Contractor shall provide necessary setting out data and ensure correct correlation between towers and foundations.

Towers on straight line shall be positioned with the crossarm perpendicular to the line direction.  Angle towers shall have the crossarm bisecting the line deviation angle.

The permitted tolerances for tower centre positioning are:

-	Longitudinal, relative to position plotted	:	1.0 - 2.0 m

-	Transversal, relative to centre line	:	0.05 m

### 8.12.3	 Excavation

During excavation, the Contractor shall take adequate precautions to prevent earth disturbances which might affect the safety of personnel and Site Works.

Before excavations are commenced the Contractor shall submit his proposals with regard thereto for the Project Manager’s approval.  Excavations shall be closed timbered or sheeted planked and strutted as and when necessary and kept free of water by pumping or other means during the work.  The sides of excavations shall normally be vertical unless otherwise specifically agreed with the Project Manager.  Where necessary or as directed by the Project Manager, adequate drainage shall be provided around the tower site.  Excavated materials shall be laid aside and shall be used for backfilling and embankment at the tower site from which it was excavated, and the excess materials shall be spread evenly around the site.  Where excavation is on farm or cultivated land, the topsoil should be carefully stripped and laid aside, separate from other excavated soil, and then later placed back on top of the backfill.

Foundations intended for soil shall not be placed directly on bare rock.  Minimum 10cm well compacted subgrade of sand or gravel shall be placed between the rock and the foundation base.

If excavations are deeper than required, only blind concrete shall be placed at the bottom of the pit to bring the excavation to the required elevation.

### 8.12.4	 Rock Excavation

Written approval shall be obtained from the Project Manager before explosives are used for excavating foundations with rock. The Contractor shall be responsible for complying with local Regulations concerning the use of explosives and for the safe-keeping and handling of explosives. During operations involving the handling or use of explosives, the Contractor shall be responsible for the safety of personnel, Site Works and people or properties in the vicinity of the Site.  The Contractor shall make good at his own expense any damage caused by the use or mishandling of explosives.

### Backfill

Backfilling shall not be carried out until the Project Manager, or his representative has inspected and approved the foundation. Any backfilling done without the said approvals shall be excavated for inspection at the Contractor’s own cost.

Only suitable excavated soil may be used as backfill material. Rock and soil not suitable for compacting shall be removed and replaced with a suitable backfill to the approval of the Project Manager. No additional claim of payment will be accepted for any type of backfilling. Organic matter, clay and silt SHALL NOT be used as backfill material. All temporary timbering shuttering, etc. and all decomposable or perishable material shall be removed from the excavations prior to backfilling.

Backfill shall be placed in layers of approximately 15cm thickness. The Contractor shall make certain that each layer is be carefully compacted. The material to be compacted shall contain no stones greater than 10 cm in diameter.

In backfilling for concrete footings, the pad of the footing shall be covered first with a 30 cm layer of fine material before any coarse material is deposited.

Prior to and during compacting operations, the backfill shall have the optimum practicable moisture content required for the purpose of compacting.

The material shall be compacted to 85 per cent of the maximum density obtainable in the Standard Proctor Density Test as specified in ASTM D698 (Method A).

The Project Manager will periodically order backfill soil density tests to ensure the desired degree of backfill compacting is achieved.

Backfill shall be carried out to a minimum height of 20cm above the original ground surface to compensate for future settlement of the filling.

All backfill of tower foundation shall be protected in an approved manner from being washed away by running water.  At all tower positions, the surface of the ground shall be sloping from the tower legs to provide drainage as required.

At certain places, additional protection against erosion may be required.  Any such work, when decided in agreement with and authorised by the Project Manager, will be paid for based on the Daywork rates.

### 8.12.6	Types of Foundations

The types of foundations shall be decided based on these Specifications, the specifications for the existing lines and the soil investigations and be to the approval of the Project Manager.

Where ground conditions are unsuitable for the installation of any one standard or modified standard class of foundation the Contractor will be required to plan to provide a piled or other special foundation as may be approved.

### 8.12.7	Stub Setting

Where stubs are used for tower foundations, they shall be set by the use of suitable templates or complete tower bases and leg extensions.  The templates must be sufficiently accurate and rigid to hold the stubs in the correct position while the concrete for the foundation structure is placed.  The templates shall not be struck until at least 24hours after foundations have been completed. The spacings and levels of the stubs after the templates have been struck shall be such as to ensure correct alignment of the towers without forcing or filing of members during erection.

8.13	Concrete Work

### 8.13.1	General

The Contractor shall supply all labour, materials and equipment required for the concrete work and all tests required and shall:

1.	Mix, transport, place, compact, finish and cure all concrete

2.	Erect and dismantle all forms and formwork

3.	Fix all reinforcement, and

4.	Embed as required all items, whether supplied and erected by himself or by other Contractors, all in accordance with these specifications and approved drawings.

Centre foundations and guy anchor blocks for guyed V-towers shall be prefabricated in depots suitably located, to ensure correct and uniform quality.

All concrete for the work under this Contract shall conform to the requirements of the latest edition of the following reference Standards, except as otherwise specified:

- Aggregate:		BS 882 and BS 812

- Portland cement:	BS 12 Part 2

- Water:			BS 3148

- Admixtures:		BS 5075

- Concrete quality:	BS 8110

- Concrete tests:	BS 8110 and BS 1881

- Mixing:		BS CP 114 Part 2

- Reinforcing steel:	BS CP 114 Part 2, BS 4466 and BS 4449.

### 8.13.2	 Cement

The cement to be used shall be ordinary Portland cement meeting the requirements of BS 12 or equivalent and shall be approved by the Project Manager.  It shall be delivered to the site in bulk cement containers or in sealed bags clearly marked with the maker’s name and shall be carefully stored in a waterproof shed with a raised floor or in a silo of approved design.  Each consignment of cement shall be stored apart from earlier consignment and the cement shall be used in the order in which it is delivered.  Any consignment which has become caked or otherwise adversely affected, shall not be used, and shall be removed from site immediately.

Where Portland cement concrete may be liable to chemical attack, sulphate resistant cement to BS 4027 may be used where approved.

If required by the Project Manager, samples from the cement to be used on Site are to be taken to a laboratory or testing station approved by the Project Manager to demonstrate compliance with BS 12 or BS 915 or BS 4027 as applicable.

### 8.13.3	 Aggregates

All aggregates shall be obtained from sources approved by the Project Manager, and shall be clean and free of clay, earth, organic matter, salt or other impurities.  The aggregate shall comply generally with the requirements of BS 882.

For both the fine and coarse aggregates proposed to be used for the works, the Contractor shall furnish samples to the Project Manager together with such full details and test results as the Project Manager may require.  No aggregates may be used in the works until they have been approved by the Project Manager.

During the work the Project Manager shall order such tests as he may consider necessary on the aggregates and any aggregates found to have unsuitable characteristics at any time shall not be used in the work and shall be removed from the site, at no extra costs for the Employer.

The various fractions of fine and coarse aggregates shall be stored separately and in such a manner as to avoid the admixture of dirt in the concrete.  Aggregates shall be handled in such a way that separation is avoided.

The grading of the fine and coarse aggregates shall be such that when they are mixed in the proportions decided for the required class of concrete, the grading of the combined aggregate shall be suitable for making a dense concrete of appropriate workability, containing the proportions of cement and water prescribed.

The proportions of fine and coarse aggregates and the maximum size of coarse aggregates to be used shall be approved by the Project Manager.

The Contractor shall be responsible for mixing the aggregates in the proportions approved by the Project Manager.  He shall submit samples of the concrete material to the Project Manager well in advance of commencing any concrete work, and also have test cubes made and tested for the aggregates and the cement he intends to use.  Concrete works must not commence until such samples and tests are to the Project Manager’s approval.

### 8.13.4	 Water

The water to be used for mixing and curing of concrete shall at all times be kept clean and free from deleterious matters such as oil, acid, alkali, silt, salts, organic materials, etc., and shall be obtained only from sources approved by the Project Manager.

### 8.13.5	 Admixtures

The Contractor shall use admixture, if required, listed below in order to improve the quality of concrete or mortar such as workability and finish and water tightness as per Manufacturer’s instructions only with the approval of the Project Manager.

1.	Water-reducing and set-retarding agent to ASTM C494.

2.	Plasticizer.

### 8.13.6	 Steel Reinforcement

The steel reinforcement shall consist of hot rolled deformed bars conforming to the requirement of BS 4461 or BS 4449 or another equivalent standard approved by the Project Manager.

The number, placing and fixing of bars shall be in accordance with approved drawings and approved bar bending schedules.

All steel rod reinforcement shall be clean and free from loose mill scale, loose rust, oil and grease or other harmful matter and except at bends shall be truly straight before being surrounded with concrete.  Evidence of steel quality shall be provided.  The numbers, lengths, diameters, forms and positions of all reinforcing bars shall be in accordance with approved drawings.

The steel reinforcement shall be so connected as to form a rigid cage or mat.  To prevent displacement before or during concreting, the bars shall be secured one to the other with 18 gauge soft iron wire.  Sufficient precast rings or distance blocks shall be used between the reinforcement and the bottom and sides of the excavations to ensure the correct cover of concrete round the bars.  (The distance blocks shall be made of concrete of not less strength than of the concrete in which they occur).

Steel rod reinforcement shall be bent cold in a manner which will not injure the material.

Bends, cranks or other operation on reinforcing bars shall be in accordance with approved drawings.  Where splices or overlapping in reinforcement are required the rods shall, unless otherwise approved, have an overlap of not less than the following:

| Mild Steel Reinforcement |  | High Tensile Steel Reinforcement |  |
| --- | --- | --- | --- |
| Bars with U-hooks | Bars without U-hooks | Bars with U-hooks | Bars without U-hooks |
| 29 x d | 45 x d | 34 x d | 50 x d |

where d = diameter of rod.

### 8.13.7	 Concrete Mixing

Cement shall be measured by weight, either by use of one or more complete bags or by weighing on Site.  Other ingredients shall be measured by weight or by volume, and concrete shall be mixed in batches using one or more complete bags of cement.  When mixing by volume is adopted, suitable batch boxes of approved dimensions shall be made and used for the measurement of coarse and fine aggregates.  A suitable container for the measurement of water shall also be used.

All concrete shall be thoroughly mixed by machine with only sufficient water to ensure a workable mix.  Consistency tests shall be made when required by the Project Manager.  The slump in a truncated cone 300 mm high and of standard dimensions shall be between 25 and 50 mm, corresponding to a stiff plastic consistency.

### 8.13.8	 Formwork

All formworks shall be accurately constructed to prevent loss of concrete and to produce the correct foundation shape.  Formwork shall be sufficiently strong to withstand the pressure arising from the concrete during compacting and shall be capable of removal without undue disturbance to the concrete.  Wooden formers shall be kept wet if necessary to prevent shrinkage.  Formwork shall not be removed before the concrete has sufficiently hardened and in no case less than 36 hours after pouring.

### 8.13.9	 Placing and Compacting

Concrete shall be transported from the mixer to the place of casting in such a manner that separation of the aggregates does not occur.

The concrete shall be placed in its final position as soon as possible and in no case more than half an hour after mixing.  The method of placing shall be such as to ensure that the concrete in its final position may be dense and homogenous.

Compacting shall be carried out in a manner approved by the Project Manager, and vibrators and other Compacting equipment shall be to the approval of the Project Manager.

Joints in concrete foundation are to be avoided as much as possible.  Where the construction of the foundation is such that joints are unavoidable adequate bond between the old and new concrete shall be ensured by chipping the old concrete to a rough, clean surface free from loose particles.  Immediately before placing the new concrete, this cleaned surface shall be primed with a layer approximately 15 mm thick of a wet mix of cement and fine sand in equal proportions.

The Project Manager can stop any concrete work whenever weather conditions are unfavourable and the Contractor has not taken necessary precautions.

### 8.13.10 Surface Finish

Unless otherwise shown on the drawings, all permanently visible concrete surfaces shall have a regular finish of uniform texture, free from holes, pins and formwork.

Concrete that is damaged or honeycombed must be removed by chipping to sound concrete and replaced with mortar or concrete.  If major defects occur, the Project Manager has the right to refuse the defective parts, if necessary a whole foundation, which should then be removed.

The upper surface of the concrete of foundations shall be sloped in an approved manner to prevent accumulation of water and the whole exposed surface shall be rendered with concrete composed of one part of cement to two parts of sand.

### 8.13.11 Curing

All concrete shall be cured by being kept continuously moist for a period of at least 10 days after casting, though in certain cases the Project Manager may vary this period.

The curing shall be affected by covering all concrete surfaces with Hessian or a layer of sand, to be kept wet by continuous watering.

Curing compounds shall not be used without the permission of the Project Manager.

### 8.13.12 Testing of Concrete

All testing of concrete shall be carried out in accordance with the requirements of BS CP 114, clause 601 and BS 1881.  During mixing of concrete for each section of the work and at such other times as directed by the Project Manager, 3 sets of test cubes, size 15x15x15 cm shall be taken, each set consisting of 6 cubes.  From each set 3 cubes shall be tested after 7 days and the remaining 3 cubes after 28 days.  The compressive strength of the cubes shall not be less than 20000 kN/m2 after 28 days

Consistency and bleeding tests and such other preliminary tests as the Project Manager may direct, shall be taken as often as directed by the Project Manager.  No concrete of any type or class shall be used in the works before the preliminary tests have shown specified compressive strength and workability.

All test cubes shall be well marked and cured as specified.

Testing of reinforcement steel and concrete materials shall be carried out in accordance with the relevant British Standard as directed by the Project Manager. The Contractor shall be responsible for providing such samples as may be required by the Project Manager for such testing.

8.14	Rock Anchors

### 8.14.1	Drilling in Rock

All drilling operations shall be carried out by fully qualified personnel, using only approved methods and equipment.  Flushing with water when drilling shall be employed whenever possible.  Drilling mud and lubricants on drill rods shall be used only were permitted by the Project Manager.

The drilling of holes in rock for anchors, drainage and grouting may be carried out by means of percussion rock drilling machines.  The diameter of holes for anchors shall be 1.5 times the diameter of the steel bar.

When holes are completed, they shall be temporarily plugged, until they are used for their purpose.

### 8.14.2	Anchors

Anchor bolts may be used for anchoring concrete structures to rock.  Strengthening of the rock may be affected by means of grouted in bolts.

Anchors in rock shall be of a quality approved by the Project Manager.  They shall consist of deformed steel bars meeting the requirements of type “High Yield” according to BS 4449:1969.  The bars shall be thoroughly cleaned before they are placed in position.

Anchors in rock shall be grouted in either by the Perfo method or the SN method.  The Perfo method implies that the two halves of a perforated steel tube of the same length as the hole are first to be filled with a still sand-cement mortar.  They shall then be put together and inserted right to the bottom of the drill hole.  Immediately afterward the bar shall be driven into the tube by means of a pneumatic hammer so that the mortar, pressed through the perforations of the tube, completely fills the space between the bar and the rock.  According to the SN method the holes shall first be filled with mortar through a hose inserted to the bottom of the hole and successively pulled out as the mortar fills the hole.  The bar is then driven into the hole by means of a pneumatic hammer.

The holes shall be thoroughly cleaned with water and air immediately before they are filled with mortar.

The grout may either be cement grout or sand-cement mortar.  The consistency and composition thereof shall be approved by the Project Manager.

Where shown on the drawings or as directed by the Project Manager the protruding ends of the bars shall be bent.

Where directed by the Project Manager testing of the anchors shall be carried out.  The protruding ends of the bars shall then be given a sufficient length from the surface of the rock to allow the fixing of a hydraulic jack provided by the Contractor.  The matrix of the jack shall be designed to ensure a satisfactory grip up to stresses of 300 N/mm2 in the bar.  It is envisaged that in case the number of failures is found to be five per cent or less, normally not more than five per cent of the total number of anchorage’s will be tested as above prescribed. The cost of such testing is deemed to be included in the price for rock foundations.

8.15	Foundations Located in Slopes

If the cross profile, taken for hillside extensions, shows insufficient earth weight against uplift, tower footings must be extended.  Tower hillside extensions should be in steps by one meter.  Care shall be taken to avoid unnecessary removal of topsoil and platforms shall be avoided.

Where towers are in hillsides where erosion must be expected, special precautions shall be taken by pitching after backfilling of foundations or other method approved by the Project Manager.

8.16	Time for Foundations to Set

Unless otherwise approved, towers within situ cast concrete foundations shall not be modified or erected until the foundations have had fourteen days in which to set, or such longer or shorter time as may be approved, depending on the type of cement used and on local conditions.

8.17	Foundation Tolerances

All foundations shall be accurately placed in their specific positions, and within the following tolerances:

Tolerance of horizontal level of the four stub joints		3 mm

Tolerance for adjustment of tower base between two stubs:

-	in diagonal						 10 mm

-	in tower face						 5 mm

Approved setting templates for footings and stubs shall be supplied by the Contractor.

8.18	Tower Earthing

### 8.18.1	 General

All towers shall be permanently and effectively earthed.

The individual tower footing resistance shall be less than 10 ohm.

Individual tower earthing shall be made with radial counterpoise.  In area having high earth resistivity, such as in sand, gravel, or rock formation a supplementary radiating counterpoise may be employed.

All towers, including the terminal towers, shall be connected by continuous counterpoise cable, which also shall be connected to the substation earthing grid.

### 8.18.2	 Installation of Counterpoise

The counterpoise shall be placed in radial formation within the wayleave.

Radial counterpoise shall be buried to a minimum depth of 800mm.  Shallower installation shall be avoided. If solid rock is encountered at a lesser depth than required, the counterpoise shall be laid on top of the solid rock and covered with soil.  Where solid rock is encountered on the surface the wire shall be laid on the surface aside from the rock.  In case of laying aside is not possible, the wire shall be laid in cracks with loose rocks placed on the wire and anchored with rock anchors to prevent displacement.  The wire shall be laid in a straight line as possible without sharp bends. Sharp bends shall be positively avoided.

### 8.18.3	 Measurement of Earthing Resistance

To be carried out on all tower footings to the satisfaction of the Employer/Project Manager. Earth wire must be absent or insulated during test. No chlorides or conducting salts will be permitted.

8.19	Tower and Steel Erection Works

### 8.19.1	Erection

Towers and steel may be erected by any suitable method, provided that no overstressing of any component parts occurs.  Horizontal loads on foundations shall be avoided or reduced to a minimum during tower erection.

Prior to commencing any erection, the Contractor shall submit for the approval of the Project Manager a written account of the method(s) of erection and the erection plant proposed for use. If because of failure to submit and seek approval of erection methods, the Employer rejects the works, the resultant delays and repetitions shall be at the Contractor’s cost.

All necessary tools and equipment shall be provided by the Contractor.  Erection shall be performed with first-class workmanship and under the supervision of well qualified Site Project Managers and Foremen.

Whichever the method of erection, it is imperative:

- To avoid excessive straining of the metal.

- To brace the legs so that they remain correctly placed.

- To avoid damaging the galvanisation.

Joints shall be thoroughly cleaned before assembly.

Bolts shall be tightened to correct torque and all nuts locked in an approved manner.  Only suitable wrenches which have been approved by the Project Manager shall be used.

Washers shall be used on all bolts.  Bolts shall project through the tightened nuts with a minimum of 3.0mm or three and half threads (whichever is greater) and a maximum of 10 mm.  The threads shall not be exposed to shear forces.  All bolts and nuts shall be securely tightened.  It is the responsibility of the Contractor to ensure that no steel members shall be forced into position.

The Contractor shall establish his own checking routine to be performed prior to the Project Manager’s final checking.

All bolts and nuts installed upto about 1m above the anti-climbing device, shall all be of the approved anti-vandal type. Drawings of proposed antivandal bolts shall be included in the bid.

After erection, the steelworks within 150 mm of the upper surface of the concrete, and the upper surface of the concrete itself within 150 mm of the projecting steel shall be painted with two coats of bituminous or other approved paint.  This also applies to all steel embedded in soil.

Suitable ladders shall be used whenever necessary during erection of the towers.  All ladders shall be removed when erection work is not in progress.

At the end of the twelve-month maintenance period, the Contractor shall adjust the guy wire tensions of towers, if applicable, to the satisfaction of the Project Manager and there shall be an adequate amount of capability remaining at the end of the maintenance period for future adjustment.

At each tower the Contractor shall install the relevant tower signs as specified.

Handling and storage of all material shall be such as to prevent injury to members or damage to the zinc-coating.  Steel in storage shall be lifted off ground so as not to touch the soil below.

Distinct, legible, and durable marking of parts shall be the responsibility of the Contractor.

After erection all towers shall be cleaned of all foreign matter.

### 8.19.2	 Repair of Damage

Deformed members shall be straightened in a manner approved by the Project Manager or replaced.  Members which may have suffered a strength reduction by deformation shall be replaced.  If fabrication errors are discovered, the Contractor shall notify the Project Manager who will decide whether the errors may be corrected in the field or if the member shall be replaced.

Repair and means of repair of damaged zinc coating, including white rust, shall be subject to the approval of the Project Manager.

### 8.19.3	 Anti-climbing Guard

All towers shall be equipped and erected with anti-climbing guards according to approved drawing. The anti-climbing guards shall be such that it will prevent the device from being grapped by hand at any point including the device’s own support steel brackets or members.

### 8.19.4	 Guard Against Birds

All towers shall be equipped with an approved device immediately above each suspension insulator string attachment, to prevent perching of birds.

### 8.19.5	 Erection Tolerances

All towers shall be vertical within a tolerance at the tower top of 0.3 per cent of the tower height after conductors and earthwires have been clamped in.

### 8.19.6	 Final Tightening of Bolts

The final tightening of all bolts shall be carefully and systematically carried out by a special crew not later than a few days after erection of towers.

This operation also includes the punching of threads of all bolts (at 3 points) to prevent loosening or theft.

8.20	Installation of Insulators, Conductors and Earthwires

### 8.20.1	 Insulators and Fittings

Insulators shall be handled with the utmost care to avoid damage or deformations.  Insulators shall remain in their shipping crates until required for assembly at the tower site.

Before installation all units shall be closely inspected and rejected if damaged or deformed.

Prior to installation and immediately before installation, the insulators shall be thoroughly cleaned.

All bolts, nuts and pins shall be installed so as to facilitate easy inspection and live line maintenance work.

It is the Contractor’s responsibility to ensure that all insulators are assembled in accordance with approved drawings, and supplier’s instructions if any.

The Contractor shall at his own expense collect information from manufacturers on the correct and safe handling of insulators. The Contractor shall demonstrate to the Employer that all staff carrying out the insulator erection have been fully informed and trained in the correct and safe handling of insulators.

The contractor shall be required to submit for approval the methodology for insulator installation and clamping in of conductors. At no time will workmen be allowed to climb on the insulators. The contractor shall observe all precautions associated with the handling of silicon rubber insulators.

### 8.20.2	 Conductor Joints and Tension Assemblies

Compression joints and tension clamps shall be installed in accordance with good engineering practice.  The Contractor shall submit detailed written instructions for the complete installation procedure for the approval of the Project Manager.

The man appointed by the Contractor to be responsible for the installation of the joints and tension assemblies shall punch his identification sign on each assembly.

All installation of joints and clamps shall be made in the presence of the Project Manager or his representative and shall be punched with his identification sign.

Wherever possible full use shall be made of maximum drum lengths of conductors and earth wires to reduce the number of joints.

The number of joints and their location in the spans shall be approved by the Project Manager.

No joints shall be made in spans which cross main roads, power lines, or in the major river crossings, nor, whenever conductor drum lengths permit, in spans immediately adjacent thereto.

The distance between joints of the same conductor shall in no case be less than 100 m.  Joints shall in no case be installed closer than 15 m to the centre of suspension clamps or closer than 40 m to tension clamps.

The Contractor shall keep a record of all joints and tension clamps giving the location, type, and date of each assembly. This record shall form part of the As-build documentation.

### 8.20.3	 Earth-wire Joints and Tension Assemblies

Earth wire joints and tension clamps shall also be installed in accordance with the requirements of the previous clause where applicable. The procedure to be followed shall be as recommended by the manufacturer.

### 8.20.4	 Repair Sleeves

In the case of damage to the conductor aluminium strand an approved repair sleeve shall be installed provided the damage consists of not more than 2 strands broken or knocked deeper than one half of their diameter.  When more than 2 strands are so damaged, the damaged section of the conductor shall be cut out.

Repair sleeves shall be installed in the presence of the Project Manager or his representative.

### 8.20.5	 Tools and Equipment to be Used.

Tools and equipment shall conform to IEEE Standard 524, Guide to the Installation of Overhead Transmission Line Conductors.

Stringing pulleys shall have adequate strength and be of approved design.  They shall be equipped with ball or roller bearings.  The sheave diameter measure at the bottom of the groove shall not be less than 18 times the outside diameter of the conductor or earth wire.  The groove shall be wide enough for the passage of compression joints.  Stringing pulleys for the conductors and earth wires shall have the sheave grooves lined with electrically conductive neoprene or equivalent.

Pulleys shall be inspected daily for proper operation. The use of defective pulleys will not be permitted.

Running out blocks shall have grooves of a shape and size in accordance with the requirements of IEEE Standard 524.  The sheave shall be lined with boned neoprene or equivalent.  Unlined sheaves made of aluminium or magnesium alloy may be used for installation of galvanised steel stranded overhead ground wire.

Come-along clamps shall be of the type that grip the conductor more firmly as the tension of the conductor increases.

Suitable hydraulic compressors equipped with pressure gauge and dies or other approved types shall be used for tension joints and compression dead-end connector assemblies.

Length meter for measuring the conductor during paying out shall be provided.

### 8.20.6	 Stringing

Conductors and earth wires shall be run out from drums mounted on trailers or drum stands.

Conductors and earth wires shall be pulled out and strung by an approved stringing method. Conductors shall as a principle never be allowed to touch ground. Therefore, the Contractor shall, as far as possible, provide ground mounted running blocks for this purpose.

The Contractor shall submit in writing, for the approval of the Project Manager, a complete and detailed stringing plan, description of the stringing equipment and the stringing and sagging procedure intended for use.

Unless otherwise approved by the Project Manager the stringing procedure shall be in strict conformity with the recommendations of the manufacturer of the stringing equipment.  Only specially trained linesmen must be employed who are well acquainted with the handling and running of the equipment to be used.

Reliable means of instantaneous two-way communication must be available between the stringing crews and between these crews and any observation posts that may be placed along the stringing section.

The stringing equipment shall be set up so as not to cause excessive vertical loads on the towers.  The distance to the nearest tower through which the cables are being strung shall be selected with due regard to the relative levels of the pulleys on the tower and the stringing equipment.  A reasonable allowance should also be made for possible accidental over-tensioning of the cables.

Tools for stringing of conductors, earth wires, clamps and joints shall be subject to approval by the Project Manager. Stringing shall be executed in such a manner that destruction, over tensioning of individual wires or layers, or other deformation or damage to the conductors shall not occur.  The use of ‘service’ compression joints for the purpose of pulling out conductors during erection, the use of insulators and line materials in general for erection purposes will NOT be allowed.  Auxiliary erection clamps, or hauling devices shall be of approved design, and shall under erection conditions allow no relative movement of strands or layers of the conductors.  Cutting of layers of ACSR conductors shall be carried out with tools designed not to damage underlying strands.  Cropping or shearing of complete conductors shall not be permitted.  The cut ends of the conductors and the joints, clamps and fittings attached to the conductor themselves shall be treated in an approved manner to prevent ingress of moisture.

Stringing pulleys shall preferably be located at approximately the same levels as the conductors and earth wires will occupy when installed.

At all times during stringing the conductors and earth wires shall be handled and protected so as not to be scratched, nicked, abraded, kinked, or damaged in any way.  If during stringing it should prove inevitable to lower the conductors to the ground, suitable non-metallic lagging shall be placed underneath.

Conductors which have been subject to bird-caging during stringing will not be accepted, and care shall be taken to position equipment in such a manner that the chances for bird-caging to occur are significantly minimised.

Stringing tensions shall at no times exceed corresponding sagging tensions by more than 20%.

If, for any reason, stringing operations in progress must be interrupted, the conductors and earth wires may be left in the stringing pulleys, but their tension shall be reduced as far as possible.  In all cases, however, the cables must be kept sufficiently far away from any obstacles which might cause abrasion of the cables if touched by them.  If the conductors and earth-wire have to be left in the pulleys during night-time the cables must be guarded to prevent safe passage of possible off-road vehicles which may operate in the area during night-time.

If the interruption lasts for more than 40hours or if stormy weather has prevailed, the cables shall be closely inspected for damage.  Such inspection applies particularly to the suspension points where the cables have been resting in the pulley’s sheaves.

At all times during stringing, sagging and clamping operations, the conductors, earth wires, reels and hauling equipment shall be effectively grounded.

To prevent overstressing of towers, the Contractor shall make suitable arrangements for temporary staying of towers, where necessary.  Suitable plates (detachable or otherwise) shall be provided on the towers for attachment of any temporary guys.

Damages to the conductors or earth wires shall immediately be reported to the Project Manager who will instruct the Contractor how to proceed.

The Contractor shall make any necessary special arrangements for running out and sagging the conductors where the route crosses buildings, orchards, plantations, gardens, or other ground over which erection cannot be carried out in the normal manner.

The Contractor shall make such special arrangements as the Project Manager may approve where power lines are to be crossed.

No additional payment will be made for the erection of the conductors and earth wires over roads, rivers, navigable waterways, railways, and communication circuits, or over or under existing power lines which have been made dead for the time being.

Where the conductors and earth wires have to be erected whilst the power to be crossed is live, payment additional to the prices stated in the Bill of Quantities shall be at rates to be agreed and shall include any special scaffolding or equipment required.

### 8.20.7	 Sagging

The Contractor shall submit for approval longitudinal profiles with curves showing the correct initial and final sags and tensions of the conductors and earth wires at various temperatures and spans.  Allowance shall be made for permanent elongation of conductors and earth wires as may take place in service.

If applicable the Contractor shall provide three complete sets of sag templates in celluloid, perspex or similar material based on approved equivalent spans or other approved methods. The templates shall show the conductor sags at 80oC after permanent elongation and in still air, and the ground clearance line.  An additional curve is to be marked on the templates to enable the minimum weight condition at 15oC to be checked in accordance with the Specification.  Each template shall be clearly endorsed with the design loading conditions, type of conductor, basis of calculation, equivalent span or curve parameters and the scale appropriate to the scale of the relevant profile.

The Contractor shall submit for approval of the Project Manager, sag and tension charts for use during erection which shall be established with due regard to the specific stringing methods to be employed so that remaining creep after clamping may be assessed and considered with reasonable accuracy.

Erection sagging charts or tables shall show sag in still air against span length for temperatures between 0o and 80oC in increments of 5oC.

Sagging temperature shall be read from a certified thermometer, the bulb of which has been inserted in an approximately 50 cm long piece of conductor with the inner layers removed.  The thermometer so equipped shall be freely suspended in the air without any shielding and not less than 3m above ground.  Temperature readings will be taken only after 20 minutes’ exposure.

The Contractor shall provide suitable dynamometers, thermometers, sighting rods and other approved apparatus necessary for the proper checking of the work.  Dynamometers, if used, shall preferably read in kilograms or Newton’s, and, when required by the Project Manager, shall be tested and, if necessary, re-calibrated.

After completion of stringing operations the conductors and earth wires shall be sagged in accordance with agreed sagging procedure and relevant erection sagging chart or table.  It is essential that prescribed hold periods before definite sagging are rigorously observed.

The Contractor shall check the sag of each conductor and earth wire of a sagging section selecting one span near each end and one or two near the centre of the sagging section.  The sags shall also be checked in spans on each side of angle structures and sharp breaks in profile.  Intermediate spans shall be inspected for uniform sag.

Where and if the Project Manager wants to check sags himself, the Contractor shall furnish such assistance in equipment and personnel as may be required.

Sagging sections shall be limited to such length as can be sagged satisfactorily.

Final sagging of conductors shall not be made earlier than 8 hours, and not later than 48 hours after they have been taken up to approximate specific sag.  All conductors of a sagging section shall be sagged at the same time.

Conductor tension shall be equalised between sagging sections so that the insulator string will be vertical when successive sagging sections have been clamped in.

The Contractor shall keep a record on approved schedules of the particulars of the sagging of conductors and earth wires on each sagging section. This record shall form part of the As-build documentation.

At 80oC in still air, in any span, the earth wire sag shall be approximately 20 per cent less than the line conductor sag.

### 8.20.8	 Clamping In

After finishing sagging operations, the conductors and earth wires shall be clamped-in according to agreed procedure.  Tension clamps shall be installed and properly anchored in advance of clamping-in at suspension towers.  In order to make future adjustments possible, approximately ONE HALF of the available length adjustment of turn buckles shall remain after anchoring.

Clamping-in shall be effected within 48 hours after completion of sagging unless otherwise agreed.

In transferring the conductors from the stringing pulley to the suspension clamps the conductors shall be carried by neoprene lined hooks with a long enough saddle-shaped bearing surface not to injure the conductors or any part thereof, or by means as agreed by the Project Manager.  The neoprene lining shall be electrically conductive.

All marking of the conductors, eg. for the centering of clamps or armour rods shall be done with tape or other inoffensive means.  Scratch marks or similar will not be permitted.

Tightening torque of clamp bolts shall be as recommended by the manufacturer. The Contractor shall submit the torques to the Employer for information during erection works.

At suspension towers the earth conductor suspension clamp shall be securely bonded to the tower steelworks with a conductor having a cross-section area of not less than the earth conductor.  The bond shall be terminated with compression lugs and be flexible so as not to interfere with the suspension clamp movement.  At tension tower the earth conductor shall be securely bonded to the tower steelworks in an approved manner.

### 8.20.9	 Sagging Tolerances

Immediately after clamping-in, sag tolerances of plus or minus 2% of specified sag will be permitted, provided that all conductors in the span assume the same sag and specified clearance to ground will be obtained.

Suspension insulator strings shall be vertical within plus or minus 30mm longitudinally.

The maximum permissible difference in sag between any two phases, or conductors in different phases, shall not exceed 200mm.

The sag of the component conductors in any one phase shall not differ by more than 100mm.

### 8.20.10 Vibration Dampers

Vibration Dampers shall be installed as specified within 24 hours after clamping in.  Dampers shall be located, installed, and clamped in accordance with the manufacturer’s recommendations. Details of these recommendation shall be submitted to the Employer well before sagging is commenced.

Before installation all dampers shall be thoroughly cleaned and inspected for bent spring wires, distorted clamps, or other damage. Damaged dampers shall be replaced at no cost to Employer.

### 8.20.11	 Spacers

Spacers shall be installed in accordance with the Specifications and approved drawings as soon as possible after the conductors and earthwires have been clamped in, and at the latest within one week.

8.21	Plans and Schedules

Work plans (methods), programmes and reports shall be provided by the Contractor.

At the end of each month before the 5th day of the following month before the monthly meeting, the Contractor shall submit suitable written progress reports to the Project Manager. The report shall without fail show the progress of design, manufacture, transport, surveying, bush clearing, foundation works, steel erection and conductor stringing during the period and the total completed to date. The report shall show the commercial and financial progress in the invoices, with values, submitted, invoices paid and outstanding and other related but pertinent issues like status of LOC payments and claims. The monthly progress report will also show the levels and types staffing at site. Contractor shall provide information on the availability of all major equipment and machinery at site(s).

9. 330kV TECHNICAL SCHEDULES

GENERAL

| The Bidders shall fill in and submit with their Bids all the Guaranteed Technical Particulars |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| listed in these Technical Schedules. Failure to do so will result in rejection of |  |  |  |  |  |  |
| the Bid. |  |  |  |  |  |  |

9.1 Tension Insulators

| Ser. No. | Particulars | Unit | ZESCO Minimum specs | Bidder To Fill In |
| --- | --- | --- | --- | --- |
|  |  |  | BISON | BISON |
|  | INSULATOR UNITS |  |  |  |
| 1 | Type and IEC designation |  |  |  |
| 2 | Maker's name |  |  |  |
| 3 | Standard to which complied |  | IEC 61109 |  |
| 4 | (a) Material from which insulator sheds are manufactured |  | Silicone |  |
|  | (b) Material from which insulator rod is manufactured |  | ECR Boron free glass |  |
| 5 | Weight of insulator | Kg | 15.8 |  |
| 6 | Number of sheds per insulator |  | 109 |  |
| 7 | Dry arc distance, minimum | mm | 2700 |  |
|  | INSULATOR SET COMPLETE |  |  |  |
| 8 | Number of Strings per phase | No. | 2 |  |
| 9 | Length of complete, without fittings | mm | 3083 |  |
|  | Length of complete, including fittings | mm | 4119 |  |
| 10 | Weight of insulator | kg | 15.8 |  |
| 11 | Breaking strength of complete set |  |  |  |
| 11.1 | Set with single insulator | kN | 160 |  |
| 11.2 | Set with double insulator | kN | 160 x 2 |  |
| 12 | Recommended maximum working load per set | kN | 160 |  |
| 13 | Overall creepage distance per string | mm | 11500 |  |
| 14 | Length of protected creepage per string |  |  |  |
|  | (a) Minimum | mm | 4481 |  |
|  | (b) Actual | mm | 11347 |  |
| 15 | Power frequency (50Hz) withstand voltage | kV |  |  |
| 15.1 | Dry, one minute | kV | 890 |  |
| 15.2 | Wet, one minute | kV | 730 |  |
| 16 | Dry lightning impulse withstand voltage |  |  |  |
| 16.1 | 1.2/50 Positive wave | kV | 1430 |  |
| 16.2 | 1.2/50 Negative wave | kV | 1530 |  |
| 17 | Wet switching impulse voltage |  |  |  |
| 17.1 | Positive wave | kV | 1050 |  |
| 17.2 | Negative wave | kV | 1050 |  |
| 18 | Corona voltage | kV | 245 |  |
| 19 | Physical Particulars |  |  |  |
|  | (a) Rod diameter | mm | 20 |  |
|  | (b) Whether coupling, interchangeable with IEC Publication No. 120, 20 mm, or 16 mm nominal shank diameter, as applicable | - |  |  |
|  | (c) Colour |  | Grey |  |
|  | (d) Material of housing including sheds |  | Resistant ECR |  |
|  | (e) Material of core |  | FRP Rod |  |
|  | (f) Material of socket type cap |  | Galvanized steel |  |
|  | (g) Material of ball type in. |  | Galvanized steel |  |
|  | (h) Whether galvanised or not |  | YES |  |
|  | (i) method of attachment of (f) and (g) to fibre rod |  | Crimping |  |
|  | (j) Method of sealing |  | Labyrinth |  |
|  | (k)Thickness of single shed | mm | 4 |  |
| 20 | Recommended maximum sustained load | kN | 160 |  |
| 21 | Mechanical Strength |  |  |  |
|  | (a) Breaking strength | kN | 160 |  |
|  | (b) Electromechanical strength | kN | 80 |  |
| 22 | Gap between arcing horns | mm | 2645 |  |
| 23 | Whether complete drawings of insulator assemblies are submitted with bid |  | YES |  |
| 24 | Whether the insulator is complete in every respect |  | YES |  |

9.2 Suspension Insulators

| Ser. No. | Particulars | Unit | ZESCO minimum specs | Bidder To Fill In |
| --- | --- | --- | --- | --- |
|  |  |  | BISON | BISON |
|  | INSULATOR UNITS |  |  |  |
| 1 | Type and IEC designation |  |  |  |
| 2 | Maker's name |  |  |  |
| 3 | Standard to which complied |  | IEC 61109 |  |
| 4 | Material from which insulator is manufactured |  | ECR Boron free |  |
| 5 | Weight of insulator | Kg | 15 |  |
| 6 | Number of sheds per insulator | No. | 109 |  |
| 7 | Dry arc distance, minimum | mm | 2700 |  |
|  | INSULATOR SET COMPLETE |  |  |  |
| 8 | Number of Strings per phase | No. | 1 |  |
| 9 | Length of complete, without fittings | mm | 3000 |  |
|  | Length of complete, including fittings |  | 3395 |  |
| 10 | Weight of insulator | kg | 15 |  |
| 11 | Breaking strength of complete set | kN | 120 |  |
| 12 | Recommended maximum working load per set | kN | 120 |  |
| 13 | Overall creepage distance per string | mm | 11500 |  |
| 14 | Length of protected creepage per string |  |  |  |
|  | (a) Minimum | mm | 4481 |  |
|  | (b) Actual | mm | 11347 |  |
| 15 | Power frequency (50Hz) withstand voltage |  |  |  |
| 15.1 | Dry, one minute | kV | 890 |  |
| 15.2 | Wet, one minute | kV | 730 |  |
| 16 | Dry lightning impulse withstand voltage |  |  |  |
| 16.1 | 1.2/50 Positive wave | kV | 1430 |  |
| 16.2 | 1.2/50 Negative wave | kV | 1530 |  |
| 17 | Wet switching impulse voltage |  |  |  |
| 17.1 | Positive wave | kV | 1050 |  |
| 17.2 | Negative wave | kV | 1050 |  |
| 18 | Corona voltage | kV | 245 |  |

| Ser. No. | Particulars | Unit | ZESCO minimum specs |  |  |  | Bidder to Fill In |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | BISON |  |  |  | BISON |
| 19 | Physical Particulars |  |  |  |  |  |  |
|  | (a) Rod diameter | mm | 20 |  |  |  |  |
|  | (b) Whether coupling, interchangeable with IEC Publication No. 120, 20 mm or 16 mm nominal shank diameter, as applicable | - |  |  |  |  |  |
|  | ( c) Colour |  | GREY |  |  |  |  |
|  | (d) Material of housing including sheds |  | Resistant ECR |  |  |  |  |
|  | (e) Material of core |  | FRP Rod |  |  |  |  |
|  | (f) Material of socket type cap |  | Galvanized steel |  |  |  |  |
|  | (g) Material of ball type in. |  | Galvanized steel |  |  |  |  |
|  | (h) Whether galvanised or not |  | Yes |  |  |  |  |
|  | (i) method of attachment of (d) and (e) to fibre rod |  | Crimping |  |  |  |  |
|  | (j) Method of sealing |  | Labyrinth |  |  |  |  |
| 20 | Recommended maximum sustained load | kN | 120 |  |  |  |  |
| 21 | Mechanical Strength |  |  |  |  |  |  |
|  | (a) Breaking strength | kN | 120 |  |  |  |  |
|  | (b) Electromechanical strength | kN | 60 |  |  |  |  |
| 22 | Gap between arcing horns | mm | 2684 |  |  |  |  |
| 23 | Whether complete drawings of insulator string assemblies are submitted with bid |  | Yes |  |  |  |  |
| 24 | Whether the insulator strings are complete in every respect |  | Yes |  |  |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |
|  | Date: _________________________ Signature of Bidder: _________________ |  |  |  |  |  |  |

9.3 Hardware and Fittings for Conductors - ACSR

| Ser. No. | Particulars | Unit | ZESCO minimum specs | Bidder To Fill In |
| --- | --- | --- | --- | --- |
|  |  |  | BISON | BISON |
| 1 | Tension Clamp: |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type of clamp |  | Compression type |  |
|  | (c) Breaking strength | N | 95% of conductor UTS |  |
|  | (d) Slipping strength | N | 95% of conductor UTS |  |
|  | (e) Whether dimensioned drawing submitted |  | Yes |  |
| 2 | Suspension Clamp: |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type of clamp |  |  |  |
|  | (c) Breaking strength | kN | 70 |  |
|  | (d) Slipping strength | N | 8% - 15% of conductor UTS |  |
|  | (e) Whether dimensioned drawing submitted |  |  |  |
| 3 | Tension Joint: |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type of (single or two piece) |  | Two pieces |  |
|  | (c) Tensile strength | N | 95% of conductor UTS |  |
|  | (d) Slipping strength | N | 95% of conductor UTS |  |
|  | (e) Whether dimensioned drawing submitted |  | Yes |  |
| 4 | Repair Sleeves: |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type of clamp |  | Compression type |  |
|  | (c) Whether dimensioned drawing submitted |  | Yes |  |
| 5 | Armour Rod: |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Material |  | High strength Aluminium Alloy |  |
|  | (d) Dimensions |  |  |  |
|  | (e) Whether dimensioned drawing submitted |  | Yes |  |
| 6 | Arcing Horns |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type |  | ROD and pipe type |  |
|  | (c) Whether dimensioned drawing submitted |  | Yes |  |
| 7 | Vibration Dampers: |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Weight | kg |  |  |
|  | (d) Type of attachment to Conductor |  | Bolted type |  |
|  | (e) Whether dimensioned drawing submitted |  | Yes |  |
| 8 | Whether all details of fittings and hardware are submitted with Bid |  | Yes |  |
|  | Whether all fittings supplied are: |  |  |  |
|  | (a) Suitable for specified insulators and conductor |  |  |  |
|  | (b) Complete in all respects |  |  |  |
|  | (c) Galvanised |  |  |  |

| Ser. No. | Particulars | Unit | ZESCO's minimum specs | Bidder To Fill In |
| --- | --- | --- | --- | --- |
|  |  |  | BISON | BISON |
| 9 | Flexible Spacers |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type of clamp |  | Twin bundle type |  |
|  | (c) Weight | Kg |  |  |
|  | (d) Whether dimensioned drawing submitted |  | Yes |  |
| 10 | Rigid spacers (for jumpers) |  |  |  |
|  | (a) Manufacturer's name |  |  |  |
|  | (b) Type of clamp |  | Bolted type |  |
|  | (c) Weight including counterweight | Kg |  |  |
|  | (d) Whether dimensioned drawing submitted |  | Yes |  |
| 11 | Whether all details of arcing horns and all other fittings and hardware are submitted with the Bid. |  |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |
|  | Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |

9.4 Hardware and Fittings for Earthwire - OPGW and ACS

| Ser. No. | Particulars | Unit | ZESCO’s specs | Minimum | Bidder To Fill In |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | OPGW | ACS7 No.6 | OPGW | ACS7 No.6 |
| 1 | Tension Clamp: |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |
|  | (b) Type of clamp |  |  |  |  |  |
|  | (c) Breaking strength | N | Mini. 95% UTS of OPGW | Mini. 95% UTS of ACS |  |  |
|  | (d) Slipping strength | N | Mini. 95% UTS of OPGW | Mini. 95% UTS of ACS |  |  |
|  | (e) Whether dimensional drawing submitted |  | Yes | Yes |  |  |
| 2 | Suspension Clamp: |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |
|  | (b) Type of clamp |  |  |  |  |  |
|  | (c) Material |  | Aluminium alloy for rods | Aluminium alloy for rods |  |  |
|  | (d) Breaking strength | kN | 70 | 70 |  |  |
|  | (e) Slipping strength | N | 14% - 20% of UTS for OPGW | 14% - 20% of UTS for ACS |  |  |
|  | (f) Whether dimensioned drawing submitted |  | Yes | Yes |  |  |
| 3 | Joint Boxes |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |
|  | (c) Weight | kg |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |
| 4 | Vibration Dampers: |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |
|  | (c) Weight | kg |  |  |  |  |
|  | (d) Type of attachment to OPGW or ACS |  | Armor rods | Armor rods |  |  |
|  | (e) Whether dimensioned drawing submitted |  | Yes | Yes |  |  |
| 5 | Bonding Wire |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |
|  | (b) Type |  | Aluminium alloy | Aluminium alloy |  |  |
|  | (c) Weight | kg | 1 | 1 |  |  |
|  | (d) Whether dimensioned drawing submitted |  | Yes | Yes |  |  |
| 6 | Lead-down Clamps for OPGW |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |
|  | (c) Weight | kg |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |
| 7 | Repair Sleeves |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |
|  | (c) Weight | kg |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |
| 8 | Tension Joints: |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |
|  | (c) Tensile strength | N | Mini. 95% UTS of OPGW | Mini. 95% UTS of ACS |  |  |
|  | (d) Breaking strength | N | Mini. 95% UTS of OPGW | Mini. 95% UTS of ACS |  |  |
|  | (e) Slipping strength | N |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |
| 9 | Whether all details of fittings and hardware are submitted with Bid including drawings |  |  |  |  |  |
| 10 | Whether bonding between tower and earthwire/OPGW is provided |  |  |  |  |  |

|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |

9.5 Conductors - ACSR

| Ser. No. | Particulars | Unit | ZESCO specs | Bidder To Fill In |
| --- | --- | --- | --- | --- |
|  |  |  | BISON | BISON |
| 1 | Manufacturer’s Name |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Standard to which complied |  | BS-215 (part 2):1970 |  |
| 4 | Composition of Conductor |  |  |  |
| 4.1 | Aluminium: |  |  |  |
|  | (a) Strands | Nos. | 54 |  |
|  | (b) Layers | Nos. | 3 |  |
|  | (c) Strand diameter | mm | 3 |  |
| 4.2 | Steel Core: |  |  |  |
|  | (a) Strands | Nos. | 7 |  |
|  | (b) Strand diameter | mm | 3 |  |
|  | (c) Diameter of Steel Core | mm | 9 |  |
| 5 | Diameter of Complete Conductor | mm | 27 |  |
| 6 | Cross section of Aluminium | mm2 | 381.7 |  |
| 7 | Cross section of Steel Core | mm2 | 49.5 |  |
| 8 | Total Cross Section | mm2 | 431.2 |  |
| 9 | Nominal Copper equivalent area | mm2 | 232.84 |  |
| 10 | Ultimate breaking strength of stranded conductor | kN | 120.9 |  |
| 11 | Ultimate breaking strength of steel core | kN | 55.27 |  |
| 12 | DC resistance at 20oC | - | - |  |
| 13 | Weight of conductor | kg/km | 1450 |  |
| 14 | Modulus of elasticity |  |  |  |
|  | (a) Initial | N/mm2 | 51000 |  |
|  | (b) Final | N/mm2 | 69000 |  |
| 15 | Coefficient of Expansion | /oC | 19.3 x 10-6 |  |
| 16 | Packing |  |  |  |
|  | (a) Length of conductor per drum | m | 2000 ± 2% |  |
|  | (b) Net weight per drum | kg | 2920 |  |
|  | (c) Gross weight per drum | kg | 3220 |  |
| 17 | Whether all tests in relevant IEC standard specification will be carried out |  | YES |  |

9.6 Foundation Design Particulars

| Ser. No. | Particulars |  | Unit |  |  | Bidder To Fill In |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Maximum ultimate stresses allowable in concrete for |  |  |  |  |  |  |  |  |  |  |
|  | foundation design: |  |  |  |  |  |  |  |  |  |  |
|  | Tensile stress due to bending |  | kN/m2 |  |  |  |  |  |  |  |  |
|  | Bond stress, galvanized steel/concrete |  | kN/m2 |  |  |  |  |  |  |  |  |
|  | Bearing stress |  | kN/m2 |  |  |  |  |  |  |  |  |
|  | Punching shear stress |  | kN/m2 |  |  |  |  |  |  |  |  |
|  | 28-day strength of concrete |  | kN/m2 |  |  |  |  |  |  |  |  |
|  | Maximum angle between base and side of a pyramidal part of concrete foundation |  | degree |  |  | 70 |  |  |  |  |  |
|  | Minimum proportion of stub load to be allowed for in design of stub flats (cleats) |  | % |  |  | 50 |  |  |  |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |  |  |  |  |
|  | Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |  |  |

9.7 Soil Foundation Classification

| The soil conditions have been classified as shown in this schedule for bidding purposes. Should the Bidder, after the contractual soil testing, wish to adjust these parameters, his proposal, including documentation of the technical and economic advantages arising from such adjustment, shall be submitted to the Project Manager for approval. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Soil Classification number | Unit | 1 | 2 | 3 | 4 | 5 |
| Assumed angle to the vertical sides of frustum of earth resisting uplift | Degrees | 30 | 25 | 20 | 10 | 0 |
| Assumed density of soil | Kg/m3 | 2000 | 1600 | 1600 | 1600 | 1000 |
| Assumed density of concrete | Kg/m3 | 2200 | 2200 | 2200 | 2200 | 2200 |
| Admissible soil pressure under specified ultimate loading: |  |  |  |  |  |  |
| a) Bearing pressure | KN/m2 | 750 | 350 | 200 | 100 | 90 |
| Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |
| Date: ___________________________ Signature of Bidder: _______________________ 9.8 Quality of Materials |  |  |  |  |  |  |

| Type of Material | Standard Employed |  |  |  |
| --- | --- | --- | --- | --- |
| Steel tower members |  |  |  |  |
| Steel nuts and bolts |  |  |  |  |
| Steel washers |  |  |  |  |
| Galvanizing |  |  |  |  |
| Portland cement |  |  |  |  |
| Sulphate resistant cement |  |  |  |  |
| Aggregate |  |  |  |  |
| Earthing Materials: |  |  |  |  |
| a) |  |  |  |  |
| b) |  |  |  |  |
| c) |  |  |  |  |
| d) |  |  |  |  |
| e) |  |  |  |  |
| Zinc Paint |  |  |  |  |
| Bituminous Paint |  |  |  |  |
| Note: The schedule shall be completed and submitted with the bid |  |  |  |  |
| Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |  |

9.9 	Earthing Materials

| Ser. No. | Particulars | Unit | Bidder To Fill In |  |
| --- | --- | --- | --- | --- |
| 1 | Counterpoise Cable |  |  |  |
|  | (a) Appropriate Standard |  |  |  |
|  | (b) Material of Counterpoise cable |  |  |  |
|  | (c) Number of wires and diameter of wires | No./mm |  |  |
|  | (d) Overall diameter | mm |  |  |
|  | (e) Weight | kg/km |  |  |
|  | (f) Length per drum | m |  |  |
|  | (g) Gross weight per drum | kg |  |  |
| 2 | Clamp or lug including bolt for connection to tower |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Hole diameter for attachment | mm |  |  |
|  | (d) Suitable for conductor diameter | mm |  |  |
|  | (e) Whether dimensioned drawing submitted |  |  |  |
| 3 | Clamps for connecting counterpoise to guy wire rods |  |  |  |
|  | (a) Manufacturers name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c)Whether dimensioned drawing submitted |  |  |  |
|  | (d) Material of clamp |  |  |  |
| 4 | Counterpoise compression joint |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Whether dimensioned drawing submitted |  |  |  |
| 4 | Parallel groove clamps for counterpoise Tee joints (where applicable) |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Whether dimensioned drawing submitted |  |  |  |
| 5 | Earthing rods |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Whether dimensioned drawing submitted |  |  |  |
| 6 | Single to twin connector |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Whether dimensioned drawing submitted |  |  |  |
| Note: The schedule shall be completed and submitted with the bid |  |  |  |  |
| Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |  |

9.10 Overhead Earthwires - ACS

| Ser. No. | Particulars | Unit | Bidder To Fill In |  |
| --- | --- | --- | --- | --- |
| 1 | Maker’s name |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Standard Specification applied |  |  |  |
| 4 | Material of wire |  |  |  |
| 5 | Composition of Earthwire |  |  |  |
|  | (a) Strands | Nos. |  |  |
|  | (b) Layer | Nos. |  |  |
|  | (c) Strand diameter | mm |  |  |
|  | (d) Thickness of aluminium | mm |  |  |
|  | (e) Diameter of complete Earthwire | mm |  |  |
| 6 | Total cross-section | mm2 |  |  |
| 7 | Ultimate breaking strength of stranded earthwire | kN |  |  |
| 8 | Resistance of earthwire per km at 20oC | Ohms |  |  |
| 9 | Weight per km of earthwire | Kg |  |  |
| 10 | Modulus of elasticity |  |  |  |
|  | (a) Initial | N/mm2 |  |  |
|  | (b) Final | N/mm2 |  |  |
| 11 | Coefficient of expansion per degree celsius |  |  |  |
| 12 | Packing: |  |  |  |
|  | (a) Length of conductor per drum | m |  |  |
|  | (b) Net weight per drum | kg |  |  |
|  | (c) Gross weight per drum | kg |  |  |
| 13 | Short time current (1 sec) | kA |  |  |
| 14 | Whether all tests in relevant standard specification will be carried out |  |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |
| Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |  |

9.11 	Overhead Earthwire – OPGW

| Ser. No. | Particulars |  | Unit | Bidder to Fill In |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Manufacturer’s Name |  |  |  |  |  |
| 2 | Country of Origin |  |  |  |  |  |
| 3 | Standard to which complied |  |  |  |  |  |
| 4 | Composition of OPGW |  |  |  |  |  |
| 5 | Overall diameter |  | mm |  |  |  |
| 6 | Weight |  | kg/km |  |  |  |
| 7 | Minimum static bend diameter |  | mm |  |  |  |
| 8 | Ultimate strength |  | kN |  |  |  |
| 9 | Thermal elongation coefficient |  | /oC |  |  |  |
| 10 | Maximum permissible stress |  | N/mm2 |  |  |  |
| 11 | Mean permissible stress |  | N/mm2 |  |  |  |
| 12 | Young’s modulus |  | N/mm2 |  |  |  |
| 13 | DC resistance at 20oC |  | /km |  |  |  |
| 14 | Short time current (1 sec) |  | kA |  |  |  |
|  | Fibre Cable |  |  |  |  |  |
| 15 | Coating diameter |  | m |  |  |  |
| 16 | Coating concentricity error |  | m |  |  |  |
| 17 | Coating non-circularity |  | % |  |  |  |
| 18 | Cladding diameter |  | m |  |  |  |
| 19 | Cladding diameter deviation |  | m |  |  |  |
| 20 | Mode field diameter @1550 nm |  | m |  |  |  |
| 21 | Mode field diameter deviation |  | m |  |  |  |
| 22 | Finished cable attenuation @ 1310 nm |  | dB/km |  |  |  |
|  | @ 1550 nm |  | dB/km |  |  |  |
| 23 | Chromatic dispersion @1228-1399 nm |  | ps/nm.km |  |  |  |
|  | @1550 nm |  | ps/nm.km |  |  |  |
| 24 | Cut-off Wavelength @2 m fibre |  | nm |  |  |  |
|  | @22 m fibre |  | nm |  |  |  |
| 25 | Number of fibres – minimum 48 cores |  | No. |  |  |  |
| 26 | Normal temperature range |  | oC |  |  |  |
| 27 | Lifetime expected |  | Years |  |  |  |
| 29 | Maximum joint loss |  | dB/splice |  |  |  |
|  | Packing |  |  |  |  |  |
| 30 | Length of conductor per drum |  | m |  |  |  |
| 31 | Net weight per drum |  | kg |  |  |  |
| 32 | Gross weight per drum |  | kg |  |  |  |
|  | Tests |  |  |  |  |  |
| 33 | Whether all tests in relevant standard specification will be carried out. |  |  |  |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |
| Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |  |  |

  - Deviation from Specifications

| Ser. No. | Section and Paragraph | Details of Deviation showing resultant advantages in economic performance or operating facilities |  |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |
|  | Note: Unless deviations are specifically stated in this schedule, the equipment offered shall comply in every respect with terms and conditions of this specification. |  |  |
| Date: __________________ Signature of Bidder: _______________________ |  |  |  |

9.13 	Minimum Factors of Safety at Assumed Maximum Simultaneous   Working Loads

| Ser No. | Materials/Construction | Guarantee |  |
| --- | --- | --- | --- |
| 1 | Steel towers and foundation steelwork based on elastic limit of tensioning members and on crippling strength of compression members: |  |  |
| 2 | Worst Normal Loading Condition | 2.1 |  |
|  | Exceptional Loading Condition (unbalanced load) | 1.5 |  |
| 3 | Guy wire and guy wire fittings based upon ultimate tensile strength: |  |  |
| 3.1 | Worst Normal Loading Condition | 2.5 |  |
| 3.2 | Exceptional Loading Condition (unbalanced load) | 1.5 |  |
| 4 | Foundation against overturning or uprooting |  |  |
| 4.1 | Worst Normal Loading Condition: | 2.5 |  |
| 4.2 | Exceptional Loading Condition (unbalanced load) | 1.5 |  |
| 5 | Horizontal grillage foundation steelwork on assumption of uniform earth pressure: |  |  |
| 5.1 | Worst Normal Loading Condition | 3.0 |  |
| 5.2 | Exceptional Loading Condition (unbalanced load) | 2.0 |  |
| 6 | Earth anchor against uprooting: |  |  |
| 6.1 | Worst Normal Loading Condition | 2.5 |  |
| 6.2 | Exceptional Loading Condition (unbalanced load) | 1.5 |  |
| 7 | Insulators and fittings based on minimum failing load: |  |  |
| 7.1 | Worst Normal Loading Condition | 3.0 |  |
| 7.2 | Exceptional Loading Condition (unbalanced load) | 2.0 |  |
| Date: __________________ Signature of Bidder: _______________________ |  |  |  |

9.14 Assumed Maximum Working Conditions

| Ser No | Section and Paragraph |  |  | Unit | Guarantee |
| --- | --- | --- | --- | --- | --- |
| 1 | Minimum temperature of conductors and earthwires |  |  | oC | -1 |
| 2 | Maximum temperature of conductors and earthwires |  |  | oC | +80 |
| 3 | Wind pressure per square meter on projected area of conductors and earthwires (using wind span x reduction factor = 0,8) insulator sets and guy wires |  |  |  |  |
|  | All loading cases |  |  | N/m2 | 430 |
| 4 | Wind pressure per square meter on one-and-a-half times projected area of members of one face of towers: |  |  |  |  |
|  | All loading cases |  |  | N/m2 | 820 |
| 5 | Mass of insulator set: |  |  |  |  |
|  | Suspension string, jumper string, 330 kV |  |  | Kg | 110 |
|  | Tension string (per conductor), 330 kV |  |  | Kg | 120 |
| 6 | Site altitude above sea level |  |  | m | 1000-1500 |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |  |
| Date: __________________ Signature of Bidder: _______________________ |  |  |  |  |  |

9.15 Line Conductor Data and Loads

| Ser. No. | Particulars | Unit | Bidder to Fill In |
| --- | --- | --- | --- |
|  |  |  | BISON |
| 1 | COMPLETE LINE CONDUCTOR |  |  |
| 2 | Number of conductors per phase | no. | 2 |
| 3 | Distance between conductor centres of one phase | mm | 450 |
| 4 | EACH SINGLE CONDUCTOR |  |  |
| 5 | Code Name |  | Bison |
| 6 | Appropriate IEC Recommendation |  | 209 |
| 7 | Materials of Conductors |  | ACSR |
| 8 | Number and diameters, mm, of wire: |  |  |
|  | Aluminium |  | 54/3.0 |
|  | Steel |  | 7/3.0 |
| 9 | Minimum stress of steel at 1 per cent elongation | N/mm2 | 1,138 |
| 10 | Overall diameter of conductor | mm | 27.0 |
| 11 | Mass of conductor per kilometre: |  |  |
|  | without grease | kg/km | 1,444 |
|  | with grease | kg/km | 1,451 |
| 12 | Tension of conductor in still air at +15oC at erection | N | 23,300 |
| 13 | Maximum working tension of conductor | N | 31,100 |
| 14 | Maximum working tension of downlead conductor | N | 6,500 |
| 15 | Rated breaking strength of conductor | N | 120,900 |
| 16 | Assumed equivalent modulus of elasticity of conductor |  |  |
| 16.1 | Initial | Mpa | 51,000 |
| 16.2 | Final | MPa | 69,000 |
| 17 | Assumed equivalent coefficient of linear expansion of conductor | per oC | 19.3x10-6 |
| 18 | Permanent elongation due to creepage | m/m | 0.00038 |

|  | Note: The schedule shall be completed and submitted with the bid |  |  |
| --- | --- | --- | --- |
| Date: __________________ Signature of Bidder: _______________________ |  |  |  |

9.16	Earth wire Data and Loads

| Ser. No. | Particulars | Unit | Bidder To Fill In |  |
| --- | --- | --- | --- | --- |
| 1 | Appropriate Standard |  | BS 183 |  |
| 2 | Materials of Conductor |  | Galvanised Steel |  |
| 3 | Cross section | mm2 | 104 |  |
| 4 | Number and diameters of wire: |  | 19 x 2.64 |  |
| 5 | Overall diameter of conductor | mm | 13.2 |  |
| 6 | Mass of conductor per kilometre | Kg/km | 821 |  |
| 7 | Tension of conductors in still air at 15oC at erection | N | 16,500 |  |
| 8 | Maximum working tension of earth conductor | N | 20,500 |  |
| 9 | Maximum working tension of earth conductor downlead |  | 4000 |  |
| 10 | Rated breaking strength of conductor | N | 96,200 |  |
| 11 | Assumed equivalent modulus of elasticity of conductor |  |  |  |
|  | Initial | Mpa | 193,000 |  |
|  | Final | MPa | 193,000 |  |
| 12 | Assumed equivalent coefficient of linear expansion of conductor | per oC | 11.5x10-6 |  |
| 13 | Permanent elongation due to creepage | m/m | 0 |  |
|  | Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |

9.17 	330KV Single and Double Tower Design Particulars

|  | Particulars |  | Unit | Guarantee |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Maximum working tension of conductors for purposes of tower design and application: |  |  |  |  |  |  |
|  | Conductors per phase |  | N | 62,200 |  |  |
|  | Earth wire |  | N | 20,500 |  |  |
|  | Down leads conductors, per phase |  |  | 13,000 |  |  |
|  | Down leads earth wire |  | N | 4,000 |  |  |
| Maximum working uplift per phase for tension tower design |  |  | N | 20,700 |  |  |
| Maximum working uplift per earth wire for tension tower design |  |  | N | 6,800 |  |  |
| Earth wire maximum protected angle from vertical at the tower attachment point |  |  | degree | 20 |  |  |
| Minimum clearance between live metal and earthed tower steelwork: |  |  |  |  |  |  |
|  | a) By still air |  | mm | 2,800 |  |  |
|  | b) By 35o swing out angle |  | mm | 2,500 |  |  |
| Insulator suspension set, allowable swingout angle by maximum wind load |  |  | degree | 45 |  |  |
| Earth wire suspension clamps, unobstructed transverse swing angle from vertical |  |  | degree | 0-45 |  |  |
| Jumper loop, allowable maximum swing out angle by maximum wind load |  |  | degree | 20 |  |  |
| Quality of steel in structures: |  |  |  |  |  |  |
| Relevant standards |  |  |  |  |  |  |
|  | Mild steel |  |  |  |  |  |
|  | High tensile steel |  | - | - |  |  |
| Maximum yield stress |  |  |  |  |  |  |
|  | Mild steel |  | N/mm2 |  |  |  |
|  | High tensile steel |  | N/mm2 |  |  |  |
| Maximum elongation of breaking |  |  |  |  |  |  |
|  | Mild steel |  | % |  |  |  |
|  | High tensile steel |  | % |  |  |  |
|  |  | Particulars | Unit | Guarantee |  |  |
| Modulus of elasticity |  |  |  |  |  |  |
|  |  | Mild steel | Mpa |  |  |  |
|  |  | High tensile steel | Mpa |  |  |  |
| Quality of steel in bolts and nuts |  |  |  |  |  |  |
|  |  | Relevant standard |  |  |  |  |
|  |  | Minimum yield stress | N/mm2 |  |  |  |
|  |  | Minimum breaking stress | N/mm2 |  |  |  |
| Minimum ratios of slenderness assumed in design: |  |  |  |  |  |  |
|  |  | Main members |  | 250 |  |  |
|  |  | Stressed bracings |  | 200 |  |  |
|  |  | Unstressed bracings |  | 120 |  |  |
| Minimum thickness of material |  |  | mm | 4 |  |  |
| Minimum bolt diameter |  |  | mm | 12 |  |  |
| Maximum thickness of members for which holes punched |  |  |  |  |  |  |
| Minimum Zinc coating |  |  |  |  |  |  |
|  |  | For members | g/m2 |  |  |  |
|  |  | For bolts and nuts | g/m2 |  |  |  |
|  |  |  | - | - |  |  |
| Guy Wires |  |  |  |  |  |  |
|  |  | Appropriate standards |  | BS183 |  |  |
|  |  | Material |  | Galvanised steel |  |  |
|  |  | Number and diameter of wires | No./mm |  |  |  |
|  |  | Overall diameter | mm |  |  |  |
|  |  | Mass of wire per kilometre | Kg/km |  |  |  |
|  |  | Minimum tensile breaking strength of complete guy wire | kN |  |  |  |
|  |  | Maximum tension in guy wire in worst loading case | kN |  |  |  |
|  |  | Assumed equivalent coefficient of linear expansion of guy wire | per oC |  |  |  |
| Date: ____________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |

9.18 Particulars of Tension Towers

| TYPE OF TOWER |  | BT | C | D | DE | 300T10 | 300T30 | 300T70 | 300T90 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | UNIT | Tension | Tension | Tension | Terminal | Tension | Tension | Tension | Tension |
| Minimum ground clearance of conductor at +80o, level ground | m | 7,6 | 7,6 | 7,6 | 7,6 |  |  |  |  |
| Maximum angle of deviation | degree | 0-10 | 10-30 | 30-60 | 0-30 |  |  |  |  |
| Standard span length | m | 450 | 450 | 450 | 450 |  |  |  |  |
| Sag of conductor in standard span length | m |  |  |  |  |  |  |  |  |
| Height above ground of conductor crossarm | m |  |  |  |  |  |  |  |  |
| Height of earthwire above conductor | m |  |  |  |  |  |  |  |  |
| Overall standard tower height | m |  |  |  |  |  |  |  |  |
| Horizontal spacing between phases | m |  |  |  |  |  |  |  |  |
| Horizontal distance from tower centre line of outer insulator attachment | m |  |  |  |  |  |  |  |  |
| Horizontal distance from tower centre line of earth conductor | m |  |  |  |  |  |  |  |  |
| Overall tower base dimension at ground level | m |  |  |  |  |  |  |  |  |
| Mass of complete standard tower above ground line | Kg |  |  |  |  |  |  |  |  |
| Mass of extended tower above ground line: |  |  |  |  |  |  |  |  |  |
| 3 m extended tower | Kg |  |  |  |  |  |  |  |  |
| 6 m extended tower | Kg |  |  |  |  |  |  |  |  |
| Maximum transverse overturning moment at ground level of standard height tower | kNm |  |  |  |  |  |  |  |  |
| Date:___________________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |  |  |  |

9.19	Particulars of Suspension Towers

| TYPE OF TOWER |  |  | AS | 300S |
| --- | --- | --- | --- | --- |
|  | UNIT |  | Suspension | Suspension |
| Minimum ground clearance of conductor at +80o, level ground | m |  | 7.6 |  |
| Maximum angle of deviation | degree |  | 0 |  |
| Standard span length | m |  | 450 |  |
| Sag of conductor in standard span length | m |  |  |  |
| Height above ground of conductor crossarm | m |  |  |  |
| Height of earthwire above conductor | m |  |  |  |
| Overall standard tower height | m |  |  |  |
| Horizontal spacing between phases | m |  |  |  |
| Horizontal distance from tower centre line of outer insulator attachment | m |  |  |  |
| Horizontal distance from tower centre line of earth conductor | m |  |  |  |
| Overall tower base dimension at ground level | m |  |  |  |
| Mass of complete standard tower above ground line | Kg |  |  |  |
| Mass of extended tower above ground line: |  |  |  |  |
| 3 m extended tower | Kg |  |  |  |
| 6 m extended tower | Kg |  |  |  |
| Maximum transverse overturning moment at ground level of standard height tower | kNm |  |  |  |

9.20 	Insulator Sets

| Ser.No. | Particulars |  | Unit | Bidder to Fill in |  |
| --- | --- | --- | --- | --- | --- |
|  | Complete Insulator For 330 kV Twin Conductor, ACSR-BISON or AERO Z 455 |  |  | 330 kV | 330 kV |
|  |  |  |  | Suspension Insulator, arcing horn both ends | Tension Insulator, arcing horn both ends |
| 1 | Number of insulators per phase |  |  | 1 | 2 |
| 2 | Length of complete set, including fittings |  | mm |  |  |
| 3 | Weight of complete insulator |  | kg |  |  |
| 4 | Breaking strength of insulator set: |  |  |  |  |
|  | a) Set with single insulator string |  | N |  |  |
|  | b) Set with double insulator set |  | N |  |  |
| 5 | Overall leakage distance per insulator |  | mm |  |  |
| 6 | Length of protected leakage path per insulator: |  |  |  |  |
|  | a) Minimum |  | mm |  |  |
|  | b) Actual |  | mm |  |  |
| 7 | Gap between arcing horns |  | mm |  |  |
| 8 | Power frequency (50 Hz) withstand voltage: |  |  |  |  |
| 8.1 | Dry 1 minute | kV |  |  |  |
| 8.2 | Wet 1 minute | kV |  |  |  |
| 9 | Dry lightning impulse withstand voltage: |  |  |  |  |
| 9.1 | 1.2/50 Positive wave | kV |  |  |  |
| 9.2 | 1.2/50 Negative wave | kV |  |  |  |
| 10 | Wet switching impulse voltage: |  |  |  |  |
| 10.1 | Positive wave | kV |  |  |  |
| 10.2 | Negative wave | kV |  |  |  |
| 11 | Dry flashover of complete set | kV |  |  |  |
| 12 | Wet flashover of complete set | kV |  |  |  |
| 13 | Corona voltage | kV |  |  |  |
| 14 | Whether complete drawings of insulator string assemblies are submitted with Tender |  |  |  |  |
| 15 | Whether the insulator string assemblies are complete in every respect |  |  |  |  |
| Date: _________________________Signature of Bidder: _____________________ |  |  |  |  |  |

| 9.24 Drawings, calculations and Information to be submitted with the Bid |  |
| --- | --- |
| 1. Foundations |  |
| General outline drawings showing the following |  |
| - Outline and general arrangement of foundations |  |
| - Description of soil testing method |  |
| - Drawing list |  |
| Drawings need have leading dimensions only. |  |
| Foundation drawings shall have the dimensions for excavation depths, reinforcement and concrete quantities |  |
| 2. Towers |  |
| General outline drawings showing the following |  |
| - Outline and general arrangement for all Standard towers, showing the position of main joints, positions of step bolts and notice plates |  |
| - Electrical clearance diagrams for all tower types. |  |
| - Arrangement of conductor and earth wire attachment point for all tower types. |  |
| - Loading diagrams for all tower types |  |
| - Weights of individual tower components (basic body, body extension, leg extensions and stubs) |  |
| - Danger/ownership plates, aerial number signs, line designation/tower number plates and phase plates. |  |
| - Drawing list. |  |
| Tower drawings shall have dimensions of main members. |  |
| Date: ___________________ Signature of Bidder: _______________________ |  |

9.25 	Drawings and Information to be submitted with the Bid

| 1. Dimensioned drawings of complete insulator and earthwire attachment assemblies |  |
| --- | --- |
| 2. Detail drawings of: |  |
| - all connectors |  |
| - all clamps |  |
| - vibration dampers |  |
| - repair sleeves |  |
| - armour rods |  |
| - OPGW joint boxes including downlead clamps |  |
| - other hardware |  |
| 3. Drawings of insulators |  |
| 4. Drawing list |  |
| 5. Test reports |  |
| 6. Supply reports |  |
| Date: ________________________ Signature of Bidder: _______________________ |  |

9.26 	Drawings and Information to be submitted after Award of Contract

| 1. Detailed, dimensioned drawings of complete insulator and earthwire attachment assemblies |  |
| --- | --- |
| 2. Detailed, dimensioned drawings of all parts of which the insulator and earthwire attachment assemblies are completed. |  |
| 3. Detailed, dimensioned drawings of all other hardware for conductors and earthwires |  |
| 4. Drawing list |  |
| Note: All drawings shall be submitted within 6 weeks after contract award, in 4 copies, for examination and approval by the Project Manager. |  |
| Date:________________________ Signature of Bidder: _______________________. |
| Drawings, Calculations and Information to be submitted after Award of Contract continued |
| - Tower base dimensions for all towers including leg extensions, complete setting out data. |  |
| - Detailed calculations of all foundations including a detailed technical description of the proposed type(s) |  |
| -Templates showing the initial and final sag curves, sags and tensions of the conductors and the and temperatures, in accordance with the Specification. |  |
| -Longitudinal profiles with towers and sags plotted. |  |
| Date:___________________ Signature of Bidder: _______________________ |  |

| Drawings, Calculations and Information to be submitted after Award of Contract continued |  |
| --- | --- |
| Within 10 weeks from award of contract the Contractor shall submit to the Project Manager 4 copies as listed below, for examination and approval. |  |
| List of documents to be examined and approved: |  |
| - Completely dimensional general arrangement drawing of each tension tower super-structure with each body extension. Diagram of external loads and wind loads on the towers at each point of application. Total weight of each tower type, including zinc coatings, bolts and all appurtenances. |  |
| - Erection drawings of tower super-structures and body extensions showing the members in place, clearly indicating all dimensions, the number, dimensions and strength class of bolts required, the identification number of each member. |  |
| - Live parts to metal clearance diagrams for each type of tension tower. |  |
| A tabulation of the calculations showing the design of each tower member, i.e. steel quality, angle size, unsupported length, slenderness ratio, member, size and strength, class of connection bolts required, ultimate strength of each member in compression, tension, shear and bearing and maximum design load from the loading conditions. |  |
| A tabulation form showing the design of the redundant members. |  |
| Calculation of foundation loadings. |  |
| Complete drawings and calculations of special towers and extensions as required. |  |
| Counterpoise connections. |  |
| Danger and property, route and tower number, phase and aerial number plates. |  |
| Updated work plans and schedules. |  |
| Detailed, dimensioned drawings of all complete insulator and earthwire attachment assemblies, and all fittings and hardware for conductors and earthwires. |  |
| Date:___________________ Signature of Bidder: _____________________ |  |

9.27 	As Built Documentation To Be Submitted By The Contractor

| After completion of works, the following documentation shall be submitted to the Project Manager, two reproducible hard copies, five black on white paper copies AND an electronic copy in AutoCAD 2000 format on Hard drive, within one month after taking over: |  |  |
| --- | --- | --- |
| - All foundation drawings, and |  |  |
| - All longitudinal profiles and route maps with towers plotted, and |  |  |
| - All drawings pertaining to earthing |  |  |
| - All tower drawings, including attachment to and/or anchoring in foundations. |  |  |
| - All drawings of insulators and fittings |  |  |
| In addition: |  |  |
| - 5 copies of earth resistance measurement results, and |  |  |
| - 5 copies of all OPGW tests carried out |  |  |
| - 5 copies of manufacturers specifications and brochures for supplied items |  |  |
| - 5 copies of other relevant technical documentation |  |  |
| Date: ___________________ Signature of Bidder: _______________________ |  |  |

10. 132KV TECHNICAL SCHEDULES

10.1 Preliminary Information – Insulators, Vibration dampers and Tower Monopoles

| Ser. No. | Particulars | Unit | Bison 132kV |  |
| --- | --- | --- | --- | --- |
|  |  |  | ZESCO Minimum Spec | Bidder to Fill In |
| 1.1 | Post Insulators 132kV (Rated 145kV) |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |
| 1.2 | Strain Insulators 132kV (Rated 145kV) |  |  |  |
|  | Name of Manufacturer/Supplier |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |
| 1.3 | Stockbridge Vibration dampers |  |  |  |
|  | Name of Manufacturer/Supplier |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |
| 1.4 | Spiral Vibration dampers |  |  |  |
|  | Name of Manufacturer/Supplier |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |
| 1.5 | Steel Monopoles Tower |  |  |  |
|  | Name of Manufacturer/Supplier |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |
| 1.6 | Tension End Clamp |  |  |  |
|  | Name of Manufacturer/Supplier |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |
| 1.7 | Inline Tension Clamps |  |  |  |
|  | Name of Manufacturer/Supplier |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |
| 1.8 | Repair Sleeves |  |  |  |
|  | Name of Manufacturer/Supplier/Supplier |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |
| 1.9 | Armour Rods |  |  |  |
|  | Name of Manufacturer/Supplier |  |  |  |
|  | Country of Origin |  |  |  |
|  | Does equipment comply with the specification |  |  |  |
|  | Type (if applicable) |  |  |  |

10.2 Technical Insulators, Vibration dampers and Tower Monopoles

| Ser. No. | Particulars | Unit | Bison 132kV |  |
| --- | --- | --- | --- | --- |
|  |  |  | ZESCO Minimum Spec | Bidder to Fill In |
| 2 | Detail Material Specification |  |  |  |
| 2.1 | Insulators |  |  |  |
| 2.1.1 | Post Insulator |  |  |  |
| a | Type of Insulators |  | Silicon Rubber |  |
| b | Mechanical Strength including fittings |  |  |  |
| b1 | Failing Load | kN | 13.25 |  |
| b2 | Cantilever Strength (40% of failing) | kN | 5.3 |  |
| c | Nominal Voltage | kV | 132 |  |
| d | Maximum Operating Voltage | kV | 145 |  |
| e | Power Frequency Withstand Voltage | kV | 275 |  |
| f | Basic Insulation Level (BIL) | kV | 650 |  |
| g | Number of Sheds |  | Specify |  |
| h | Length | mm | Specify |  |
| i1 | Dry Arcing Distance |  | Specify |  |
| i2 | Creepage Distance |  | Specify |  |
| k | Medium - High Pollution | mm/kV | 25 |  |
| l | Mass per Insulator | kg | Specify |  |
| 2.1.2 | Strain/Suspension Insulator |  |  |  |
| a | Type of Insulators |  | Silicon rubber |  |
| b | Mechanical Strength including fittings |  |  |  |
| c | Failing Load | kN | 120 |  |
| d | Nominal Voltage | kV | 132 |  |
| e | Maximum Operating Voltage | kV | 145 |  |
| f | Power Frequency Withstand Voltage | kV | 275 |  |
| g | Basic Insulation Level (BIL) | kV | 650 |  |
| h | Number of Sheds |  | Specify |  |
| i | Length | mm | Specify |  |
| J | Dry Arcing Distance | mm | specify |  |
| k | Creepage Distance |  |  |  |
| l | Medium - High Pollution | mm/kV | 25 |  |
| m | Mass per Insulator | kg | Specify |  |
| 2.2 | Tension Clamps (Conductor) |  |  |  |
| 2.2.1 | Tension End Clamp (Bison) |  |  |  |
| a | Aluminum Outer (Inside Diameter) | mm |  |  |
| b | Galvanized Forged Steel Inner (Inside Diameter) | mm |  |  |
| c | Overall Length | mm | Specify |  |
| d | Compression Type |  | Hexagon ‘ALCAN’ Range |  |
| e | Breaking Force | kN |  |  |
| f | Current Transfer Through Jumper Terminal Lug Min | A |  |  |
| g | Jumper Attachment |  | 2xM12 bolted |  |
| 2.2.2 | Inline Full tension joint (Bison) |  |  |  |
| a | Aluminum Outer (Inside Diameter) | mm |  |  |
| b | Galvanized Forged Steel Inner (Inside Diameter) | mm |  |  |
| c | Overall Length | mm | Specify |  |
| d | Compression Type |  | Hexagon ‘ALCAN’ Range |  |
| e | Breaking Force | kN |  |  |
| f | Current Transfer Min | A |  |  |
| 2.3 |  | Armour Rods |  |  |  |
| 2.3.1 |  | Phase Conductor |  |  |  |
| a |  | Type |  | Spiral |  |
| b |  | Size | mm | 23.9 |  |
| c |  | Length | mm | 1,425 |  |
| d |  | Wire Diameter | mm | 5.18 |  |
| 2.4 |  | Repair Sleeves |  |  |  |
| 2.4.1 |  | Phase Conductor |  |  |  |
| a |  | Compression Type |  | Hexagon Alcan |  |
| b |  | Aluminum Outer (Inside Diameter) | mm |  |  |
| c |  | Length | mm | 200 |  |
| 2.5 Dampers |  | Vibration Dampers |  |  |  |
| a |  | Type |  | Stockbridge |  |
| b |  | Size |  | To fit conductor |  |
| 2.5.2 |  | EARTH WIRE/OPGW |  |  |  |
| a |  | Type |  |  |  |
| b |  | 7/3.35 |  | Spiral |  |
| c |  | OPGW |  | Specify |  |
| 2.6 |  | Steel Monopole |  |  |  |
| 2.6.1 |  | Intermediate Single circuit |  |  |  |
| a |  | Steel Structure |  | Tubular Monopole |  |
| b |  | Type |  | Hot Dipped, Galv,355JR |  |
| c |  | Minimum tube thickness | mm | 4.5mm |  |
| d |  | No of Sections |  | Specify |  |
| e |  | Foundation (Planted/Flanged) |  | Specify |  |
| f |  | Conductor Configuration |  |  |  |
| f.1 |  | Suspension |  | Delta |  |
| f.2 |  | Conductors Per Phase |  | 1(2) |  |
| g |  | No of Earth Conductors |  | 1 |  |
| h |  | Tip Load (Min) | kN | > 27 |  |
| i |  | Safety Factor |  |  |  |
| i.1 |  | On Calculated Strength |  | 2.5 |  |
| i.2 |  | On Type Tested Breaking Strength |  | 2.2 |  |
| J |  | Minimum Conductor Attachment Height (Shortest Pole) |  |  |  |
| j.1 |  | Suspension | m | Specify |  |
| 2.6.2 |  | Strain Single Circuit |  |  |  |
| a |  | Steel Structure |  | Tubular Monopole |  |
| b |  | Type |  | Hot Dipped, Galv,355JR |  |
| c |  | Minimum tube thickness |  | 4.5mm |  |
| d |  | No of Sections |  | Specify |  |
| e |  | Foundation (Planted/Flanged) |  | Specify |  |
| f |  | Conductor Configuration |  |  |  |
| f1 |  | Terminal/Strain |  | 1xVertical |  |
| f.2 |  | Conductors Per Phase |  | 1 |  |
| g |  | No of Earth Conductors |  | 1 |  |
| h |  | Tip Load 0-30-degree angle (min) | kN | > 56 |  |
| I |  | Tip Load 30-60-degree angle (min) | kN | > 110 |  |
| J |  | Tip Load 60-90-degree angle (min) | kN | > 155 |  |
| K |  | Safety Factor |  |  |  |
| k.1 |  | On Calculated Strength |  | 2.5 |  |
| k.2 |  | On Type Tested Breaking Strength |  | 2.2 |  |
| l |  | Minimum Conductor Attachment Height (Shortest Pole) |  |  |  |
| l.1 |  | Terminal/Strain | m | Specify |  |
| m |  | Insulator |  |  |  |
| m.1 |  | Suspension (Jumpers) |  | Plate or angle bracket |  |
| m.2 |  | Terminal/Strain |  | Plate bracket |  |
| 2.6.3 |  | Intermediate Double circuit |  |  |  |
| a |  | Steel Structure |  | Tubular Monopole |  |
| b |  | Type |  | Hot Dipped, Galv,355JR |  |
| c |  | Minimum tube thickness | mm | 4.5mm |  |
| d |  | No of Sections |  | Specify |  |
| e |  | Foundation (Planted/Flanged) |  | Specify |  |
| f |  | Conductor Configuration |  |  |  |
| f.1 |  | Suspension |  | 2x Vertical |  |
| f.2 |  | Conductors Per Phase |  | 1 (2) |  |
| g |  | No of Earth Conductors |  | 1 |  |
| h |  | Tip Load (min) | kN | > 37 |  |
| i |  | Safety Factor |  |  |  |
| i.1 |  | On Calculated Strength |  | 2.5 |  |
| i.2 |  | On Type Tested Breaking Strength |  | 2.2 |  |
| j |  | Minimum Conductor Attachment Height (Shortest Pole) |  |  |  |
| j.1 |  | Suspension | m | Specify |  |
| 2.7.4 |  | Strain Double Circuit |  |  |  |
| a |  | Steel Structure |  | Tubular Monopole |  |
| b |  | Type |  | Hot Dipped, Galv,355JR |  |
| c |  | Minimum tube thickness |  | 4.5mm |  |
| d |  | No of Sections |  | Specify |  |
| e |  | Foundation (Planted/Flanged) |  | Specify |  |
| f |  | Conductor Configuration |  |  |  |
| f.1 |  | Suspension (Jumpers) |  | 2x Vertical |  |
| f.2 |  | Terminal/Strain |  | 2x Vertical |  |
| g |  | Conductors Per Phase |  | 1 |  |
| h |  | No of Earth Conductors |  | 1 |  |
| i |  | Tip Load 0-30-degree angle (min) | kN | > 101 |  |
| j |  | Tip Load 30-60-degree angle (min) | kN | > 193 |  |
| k |  | Tip Load 60-90-degree angle (min) | kN | > 272 |  |
| l |  | Safety Factor |  |  |  |
| l.1 |  | On Calculated Strength |  | 2.5 |  |
| l.2 |  | On Type Tested Breaking Strength |  | 2.2 |  |
| m |  | Minimum Conductor Attachment Height (Shortest Pole) |  |  |  |
| m.1 |  | Terminal/Strain | m | Specify |  |

Note: The schedule shall be completed and submitted with the bid

Date: ___________________________            Signature of Bidder:  _______________________

10.3 Hardware and Fittings for Conductors - ACSR

| Ser. No. |  | Particulars | Unit | Bison 132KV |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | ZESCO Minimum Spec | Bidder To Fill In |
| 1 |  | Tension Clamp: |  |  |  |
|  |  | (a) Manufacturer's name |  | Specify |  |
|  |  | (b) Type of clamp |  | Compression |  |
|  |  | (c) Breaking strength | kN | 90.8 |  |
|  |  | (d) Slipping strength | kN |  |  |
|  |  | (e) Whether dimensioned drawing submitted |  |  |  |
| 2 |  | Suspension Clamp: |  |  |  |
|  |  | (a) Manufacturer's name |  | Specify |  |
|  |  | (b) Type of clamp |  | Compression |  |
|  |  | (c) Breaking strength | kN | 90.8 |  |
|  |  | (d) Slipping strength | kN |  |  |
|  |  | (e) Whether dimensioned drawing submitted |  |  |  |
| 3 |  | Tension Joint: |  |  |  |
|  |  | (a) Manufacturer's name |  | Specify |  |
|  |  | (b) Type of (single or two piece) |  | Compression |  |
|  |  | (c) Tensile strength | N | 90.8 |  |
|  |  | (d) Slipping strength | N |  |  |
|  |  | (e) Whether dimensioned drawing submitted |  |  |  |
| 4 |  | Repair Sleeves: |  |  |  |
|  |  | (a) Manufacturer's name |  | Specify |  |
|  |  | (b) Compression Type (c)Aluminium Outer (Inside Diameter) | mm | Hexagonal |  |
|  |  | (d) Length | mm | 200 |  |
| 5 |  | Armour Rod: |  |  |  |
|  |  | (a) Manufacturer's name |  | Specify |  |
|  |  | (b) Type |  | Spiral |  |
|  |  | (c) Material |  |  |  |
|  |  | (d) Dimensions | mm | To fit conductor |  |
|  |  | (e) Whether dimensioned drawing submitted |  |  |  |
| 6 |  | Arcing Horns |  |  |  |
|  |  | (a) Manufacturer's name |  |  |  |
|  |  | (b) Type |  |  |  |
|  |  | (c) Whether dimensioned drawing submitted |  |  |  |
| 7 |  | Vibration Dampers: |  |  |  |
|  |  | (a) Manufacturer's name |  | Specify |  |
|  |  | (b) Type |  | Stockbridge |  |
|  |  | (c) Weight | kg | 7.5 |  |
|  |  | (d) Conductor Diameter Range | mm | 25-32 |  |
|  |  | (e) Whether dimensioned drawing submitted |  |  |  |
| 8 |  | Whether all details of fittings and hardware are submitted with Bid |  |  |  |
|  |  | Whether all fittings supplied are: |  |  |  |
|  |  | (a) Suitable for specified insulators and conductor |  |  |  |
|  |  | (b) Complete in all respects |  |  |  |
|  |  | (c) Galvanised |  |  |  |
| 9 | Flexible Spacers |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |
|  | (b) Type of clamp |  |  |  |  |
|  | (c) Weight |  | Kg |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |
| 10 | Rigid spacers (for jumpers) |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |
|  | (b) Type of clamp |  |  |  |  |
|  | (c) Weight including counterweight |  | Kg |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |
| 11 | Whether all details of arcing horns and all other fittings and hardware are submitted with the Bid. |  |  |  |  |

| Note: The schedule shall be completed and submitted with the bid |  |  |  |
| --- | --- | --- | --- |
| Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |

10.4 Hardware and Fittings for Earthwire - OPGW and ACS

| Ser. No. | Particulars |  |  | Unit |  | OPGW |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | ZESCO Minimun Spec |  | Bidder To Fill In |
| 1 | Tension Clamp: |  |  |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |  |  |
|  | (b) Type of clamp |  |  |  |  |  |  |  |
|  | (c) Breaking strength |  |  | N |  |  |  |  |
|  | (d) Slipping strength |  |  | N |  |  |  |  |
|  | (e) Whether dimensional drawing submitted |  |  |  |  |  |  |  |
| 2 | Suspension Clamp: |  |  |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |  |  |
|  | (b) Type of clamp |  |  |  |  |  |  |  |
|  | (c) Material |  |  | N |  |  |  |  |
|  | (d) Breaking strength |  |  | N |  |  |  |  |
|  | (e) Slipping strength |  |  |  |  |  |  |  |
|  | (f) Whether dimensioned drawing submitted |  |  |  |  |  |  |  |
| 3 | Joint Boxes |  |  |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |  |  |
|  | (c) Weight |  |  | kg |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |  |  |
| 4 | Vibration Dampers: |  |  |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |  |  |
|  | (c) Weight |  |  | kg |  |  |  |  |
|  | (d) Type of attachment to OPGW or ACS |  |  |  |  |  |  |  |
|  | (e) Whether dimensioned drawing submitted |  |  |  |  |  |  |  |
| 5 | Bonding Wire |  |  |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |  |  |
|  | (c) Weight |  |  | kg |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |  |  |
| 6 | Lead-down Clamps for OPGW |  |  |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |  |  |
|  | (c) Weight |  |  | kg |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |  |  |
| 7 | Repair Sleeves |  |  |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |  |  |
|  | (c) Weight |  |  | kg |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |  |  |
| 8 | Tension Joints: |  |  |  |  |  |  |  |
|  | (a) Manufacturer's name |  |  |  |  |  |  |  |
|  | (b) Type |  |  |  |  |  |  |  |
|  | (c) Tensile strength |  |  | N |  |  |  |  |
|  | (d) Breaking strength |  |  | N |  |  |  |  |
|  | (e) Slipping strength |  |  | N |  |  |  |  |
|  | (d) Whether dimensioned drawing submitted |  |  |  |  |  |  |  |
| 9 | Whether all details of fittings and hardware are submitted with Bid including drawings |  |  |  |  |  |  |  |
| 10 | Whether bonding between tower and earthwire/OPGW is provided |  |  |  |  |  |  |  |
| Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |  |
| Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |  |

10.5 Conductors - ACSR

| Ser. No. | Particulars | Unit | Bison 132KV |  |
| --- | --- | --- | --- | --- |
|  |  |  | ZESCO Minimum Spec | Bidder To Fill In |
| 1 | Manufacturer’s Name |  |  |  |
| 2 | Country of Origin |  |  |  |
|  | Designation/Name |  | Bison |  |
| 3 | Standard to which complied |  | BS 215; EN 50182 |  |
| 4 | Composition of Conductor |  | Hard-drawn aluminium with galvanized steel core reinforcement |  |
| 4.1 | Current rating | Amp | 470 |  |
|  | Stranding-Aluminium | mm | 30/3 |  |
|  | Stranding-Steel | mm | 7/2.59 |  |
| 4.2 | Approximate overall diameter | mm | 18.13 |  |
|  | Nominal breaking load | KN | 70 |  |
|  | DC Resistance @ 20 0C | Ohms/km | 0.1828 |  |
|  | Operating ambient temperature | 0C | -1 to 40 |  |
|  | Minimum humidity | % | 85 |  |
|  | Altitude above sea level | m | 1500 |  |
| 5 | Diameter of Complete Conductor | mm | 18.13 |  |
| 6 | Material for drums |  | Treated wooden drums with steel tapes |  |
| 7 | Previous Type Test certificate to be provide with bid | Yes/No | Yes |  |
| 14 | Routine Test results/certificate to be provided on delivery | Yes/No | Yes |  |
|  | Quality Assurance certificate/manuals to be provided with bid | Yes/No | Yes |  |
| 16 | Packing |  |  |  |
|  | (a) Minimum length of conductor per drum | m | 2000 |  |
|  | (b) Net weight per drum | kg |  |  |
|  | (c) Gross weight per drum | kg |  |  |
| 17 | Whether all tests in relevant IEC standard specification will be carried out |  | YES |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |
|  | Date: ___________________________ Signature of Bidder: _______________________ |  |  |  |

10.6 Foundation Design Particulars

| Ser. No. | Particulars | Unit |  |  |
| --- | --- | --- | --- | --- |
|  |  |  | ZESCO Minimun Spec | Bidder To Fill In |
|  | Maximum ultimate stresses allowable in concrete for |  |  |  |
|  | foundation design: |  |  |  |
| 1 | Tensile stress due to bending | kN/m2 |  |  |
| 2 | Bond stress, galvanized steel/concrete | kN/m2 |  |  |
| 3 | Bearing stress | kN/m2 |  |  |
| 4 | Punching shear stress | kN/m2 |  |  |
| 5 | 28-day strength of concrete | kN/m2 |  |  |
| 6 | Maximum angle between base and side of a pyramidal part of concrete foundation | degree |  |  |
| 7 | Minimum proportion of stub load to be allowed for in design of stub flats (cleats) | % |  |  |

| Note: The schedule shall be completed and submitted with the bid |  |
| --- | --- |
| Date: ___________________________ Signature of Bidder: _________________ |  |

10.7 Soil Foundation Classification

| The soil conditions have been classified as shown in this schedule for bidding purposes. Should the Bidder, after the contractual soil testing, wish to adjust these parameters, his proposal, including documentation of the technical and economic advantages arising from such adjustment, shall be submitted to the Project Manager for approval. |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Soil Classification number | Unit | 1 | 2 | 3 | 4 | 5 |
| Assumed angle to the vertical sides of frustum of earth resisting uplift | Degrees | 30 | 25 | 20 | 10 | 0 |
| Assumed density of soil | Kg/m3 | 2000 | 1600 | 1600 | 1600 | 1000 |
| Assumed density of concrete | Kg/m3 | 2200 | 2200 | 2200 | 2200 | 1200 |
| Admissible soil pressure under specified ultimate loading: |  |  |  |  |  |  |
| a) Bearing pressure | KN/m2 | 750 | 350 | 200 | 100 | 90 |
| b) Bearing pressure for net horizontal area for grillage foundation | KN/m2 |  |  | 200 | 100 |  |
| Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |
| Date:___________________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |

10.8 Quality Of Materials

| Type of Material | Standard Employed |
| --- | --- |
| Steel tower members |  |
| Steel nuts and bolts |  |
| Steel washers |  |
| Galvanizing |  |
| Portland cement |  |
| Sulphate resistant cement |  |
| Aggregate |  |
| Earthing Materials: |  |
| a) |  |
| b) |  |
| c) |  |
| d) |  |
| e) |  |
| Zinc Paint |  |
| Bitumenous Paint |  |
| Note: The schedule shall be completed and submitted with the bid |  |

Date:___________________________            Signature of Bidder:  _______________________

10.9 Earthing Materials

| Ser. No. | Particulars | Unit | Bidder To Fill In |  |
| --- | --- | --- | --- | --- |
| 1 | Counterpoise Cable |  |  |  |
|  | (a) Appropriate Standard |  |  |  |
|  | (b) Material of Counterpoise cable |  |  |  |
|  | (c) Number of wires and diameter of wires | No./mm |  |  |
|  | (d) Overall diameter | mm |  |  |
|  | (e) Weight | kg/km |  |  |
|  | (f) Length per drum | m |  |  |
|  | (g) Gross weight per drum | kg |  |  |
| 2 | Clamp or lug including bolt for connection to tower |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Hole diameter for attachment | mm |  |  |
|  | (d) Suitable for conductor diameter | mm |  |  |
|  | (e) Whether dimensioned drawing submitted |  |  |  |
| 3 | Clamps for connecting counterpoise to guy wire rods |  |  |  |
|  | (a) Manufacturers name |  |  |  |
|  | (b) Type |  |  |  |
|  | ( c) Whether dimensioned drawing submitted |  |  |  |
|  | (d) Material of clamp |  |  |  |
| 3 | Counterpoise compression joint |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Whether dimensioned drawing submitted |  |  |  |
| 4 | Parallel groove clamps for counterpoise Tee joints (where applicable) |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Whether dimensioned drawing submitted |  |  |  |
| 5 | Earthing rods |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Whether dimensioned drawing submitted |  |  |  |
| 6 | Single to twin connector |  |  |  |
|  | (a) Manufacturer’s name |  |  |  |
|  | (b) Type |  |  |  |
|  | (c) Whether dimensioned drawing submitted |  |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |
|  | Date:___________________________ Signature of Bidder: _______________________ |  |  |  |

10.10 Overhead Earthwires - ACS

| Ser. No. | Particulars | Unit |  |  |
| --- | --- | --- | --- | --- |
|  |  |  | ZESCO Minimun Spec | Bidder To Fill In |
| 1 | Maker’s name |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Standard Specification applied |  |  |  |
| 4 | Material of wire |  |  |  |
| 5 | Composition of Earthwire |  |  |  |
|  | (a) Strands | Nos. |  |  |
|  | (b) Layer | Nos. |  |  |
|  | (c) Strand diameter | mm |  |  |
|  | (d) Thickness of aluminium | mm |  |  |
|  | (e) Diameter of complete Earthwire | mm |  |  |
| 6 | Total cross-section | mm2 |  |  |
| 7 | Ultimate breaking strength of stranded earthwire | kN |  |  |
| 8 | Resistance of earthwire per km at 20oC | Ohms |  |  |
| 9 | Weight per km of earthwire | Kg |  |  |
| 10 | Modulus of elasticity |  |  |  |
|  | (a) Initial | N/mm2 |  |  |
|  | (b) Final | N/mm2 |  |  |
| 11 | Coefficient of expansion per degree celsius |  |  |  |
| 12 | Packing: |  |  |  |
|  | (a) Length of conductor per drum | m |  |  |
|  | (b) Net weight per drum | kg |  |  |
|  | (c) Gross weight per drum | kg |  |  |
| 13 | Short time current (1 sec) | kA |  |  |
| 14 | Whether all tests in relevant standard specification will be carried out |  |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |
| Date:___________________________ Signature of Bidder: _______________________ |  |  |  |  |

10.11 Overhead Earth wire - OPGW

| Item |  | Attribute | Minimum Requirement |  | Bidder To Fill In |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | Cable Type | ITU-T G.652D |  |  |  |  |
| 2 |  | Max Cable length | 5000m |  |  |  |  |
| 3 |  | Cable weight | 240 ± 10 Kg/Km |  |  |  |  |
| 4 |  | Fibre count (Cores) | 24 |  |  |  |  |
| 5 |  | Mode | Single Mode |  |  |  |  |
| 6 |  | Buffer Type | Loose Tube |  |  |  |  |
| 7 |  | Buffer Material | Polybutylene Terephthalate (PBT) |  |  |  |  |
| 8 |  | Strength Member | Central Glass Reinforced plastic |  |  |  |  |
| 9 |  | Tube Filling compound | Thixotropic jelly |  |  |  |  |
| 10 |  | Flooding Compound | Water blocking jelly |  |  |  |  |
| 11 |  | Inner Sheath | LLDPE (Linear Low Density Poly-Ethylene) |  |  |  |  |
| 12 |  | UV Outer Jacket | HDPE (high density polyethylene) |  |  |  |  |
| 13 |  | Overall Diameter | 17 ± 0.5 mm |  |  |  |  |
| 14 |  | Tensile Strength | 33 KN |  |  |  |  |
| 15 |  | Minimum bend radius during installation | 300 mm |  |  |  |  |
| 16 |  | Cable life span | 30 years |  |  |  |  |
| 17 |  | Operating temperature | -40 to 70˚C |  |  |  |  |
| 18 |  | Storage temperature | -50 to 70˚C |  |  |  |  |
| 19 |  | Installation temperature | -30 to 70˚C |  |  |  |  |
| S/N |  | Attribute | Minimum Requirement |  |  |  |  |
| 1 |  | Standards |  |  |  |  |  |
| 2 |  | Stranding Direction of outer layer | Right-hand |  |  |  |  |
| 3 |  | Fibre Count |  |  |  |  |  |
| 4 |  | Cable outer diameter | 15 mm |  |  |  |  |
| 5 |  | Supporting Cross Section |  |  |  |  |  |
| 6 |  | Section of AS wire | 42 mm2 |  |  |  |  |
| 7 |  | Section of AA wire | 84 mm2 |  |  |  |  |
| 8 |  | Mass | 450 kg/km |  |  |  |  |
| 9 |  | Rated Tensile Strength (RTS) | 50 kN |  |  |  |  |
| 10 |  | Maximum Allowable Tension (40% of RTS) | 159 N/mm2 |  |  |  |  |
| 11 |  | Everyday Stress (20%RTS) | 79 N/mm2 |  |  |  |  |
| 12 |  | Strain Margin Stress (70%RTS) | 279 N/mm2 |  |  |  |  |
| 13 |  | Modulus of Elasticity | 80 GPa |  |  |  |  |
| 14 |  | Thermal Elongation Coefficient | 19 x 10-6/oC |  |  |  |  |
| 15 |  | Calculated DC Resistance at 20oC | 0.3 Ω/km |  |  |  |  |
| 16 |  | Short Circuit Current (1 sec, 40 - 180oC) | 11 kA |  |  |  |  |
| 17 |  | Short Circuit Current Capacity (40 - 180oC) | 124 kA2.s |  |  |  |  |
| 18 |  | OPGW minimum bend radius | 300 mm |  |  |  |  |
| 19 |  | Fibre Strand minimum bend radius | 30 mm |  |  |  |  |
| 20 |  | Ratio between pull and weight | 11 |  | ITU-T G.652D |  |  |
| 1 | Cladding diameter deviation |  | m |  |  |  |  |
| 20 | Mode field diameter @1550 nm |  | m |  |  |  |  |
| 21 | Mode field diameter deviation |  | m |  |  |  |  |
| 22 | Finished cable attenuation @ 1310 nm |  | dB/km |  |  |  |  |
|  | @ 1550 nm |  | dB/km |  |  |  |  |
| 23 | Chromatic dispersion @1228-1399 nm |  | ps/nm.km |  |  |  |  |
|  | @1550 nm |  | ps/nm.km |  |  |  |  |
| 24 | Cut-off Wave Length @2 m fibre |  | nm |  |  |  |  |
|  | @22 m fibre |  | nm |  |  |  |  |
| 25 | Number of fibres |  | No. |  | 24 |  |  |
| 26 | Normal temperature range |  | oC |  | from -40 to 70 |  |  |
| 27 | Lifetime expected |  | Years |  | 30 |  |  |
| 29 | Maximum joint loss |  | dB/splice |  |  |  |  |
|  | Packing |  |  |  |  |  |  |
| 30 | Length of conductor per drum |  | m |  |  |  |  |
| 31 | Net weight per drum |  | kg |  |  |  |  |
| 32 | Gross weight per drum |  | kg |  |  |  |  |
|  | Tests |  |  |  |  |  |  |
| 33 | Whether all tests in relevant standard specification will be carried out. |  |  |  |  |  |  |
|  | Attribute |  | Detail |  | Minimum Required Value |  |  |
|  | Mode field diameter |  | Wavelength |  | 1310 nm |  |  |
|  |  |  | Range of nominal values |  | 8.6-9.5 μm |  |  |
|  |  |  | Tolerance |  | ±0.6 μm |  |  |
|  | Cladding diameter |  | Nominal |  | 125.0 μm |  |  |
|  |  |  | Tolerance |  | ±1 μm |  |  |
|  | Core concentricity error |  | Maximum |  | 0.6 μm |  |  |
|  | Cladding non-circularity |  | Maximum |  | 0.01 |  |  |
|  | Cable cut-off wavelength |  | Maximum |  | 1260 nm |  |  |
|  | Macro-bend loss |  | Radius |  | 30 mm |  |  |
|  |  |  | Number of turns |  | 100 |  |  |
|  |  |  | Maximum at 1625 nm |  | 0.1 dB |  |  |
|  | Proof stress |  | Minimum |  | 0.69 GPa |  |  |
|  | Chromatic dispersion coefficient |  | λ0min |  | 1300 nm |  |  |
|  |  |  | λ0max |  | 1324 nm |  |  |
|  |  |  | S0max |  | 0.1 ps/nm2 × km |  |  |
|  | Cable attributes |  |  |  |  |  |  |
|  | Attenuation coefficient |  | Maximum from 1310 nm to 1625 nm |  | 0.4 dB/km |  |  |
|  |  |  | Maximum at 1383 nm ±3 nm |  | 0.4 dB/km |  |  |
|  |  |  | Maximum at 1550 nm |  | 0.3 dB/km |  |  |
|  | PMD coefficient |  | M |  | 20 cables |  |  |
|  |  |  | Q |  | 0.0001 |  |  |
|  |  |  | Maximum PMDQ |  | 0.20 ps/ km1/2 |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |
| Date:___________________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |  |

  - Deviation From Specifications

| Ser. No. | Section and Paragraph | Details of Deviation showing resultant advantages in economic performance or operating facilities |  |
| --- | --- | --- | --- |
|  | Note: Unless deviations are specifically stated in this schedule, the equipment offered shall comply in every respect with terms and conditions of this specification. |  |  |
| Date:__________________ Signature of Bidder: _______________________ |  |  |  |

  - Minimum Factors Of Safety At Assumed Maximum Simultaneous Working Loads

|  |  | Materials/Construction |  | Guarantee |  |  |  | Bidders to fill in |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 |  | Steel towers and foundation steelwork based on elastic limit of tensioning members and on crippling strength of compression members: |  |  |  |  |  |  |  |  |  |
| 1.1 |  | Worst Normal Loading Condition |  | 2.1 |  |  |  |  |  |  |  |
| 1.2 |  | Exceptional Loading Condition (unbalanced load) |  | 1.5 |  |  |  |  |  |  |  |
| 2 |  | Guy wire and guy wire fittings based upon ultimate tensile strength: |  |  |  |  |  |  |  |  |  |
| 2.1 |  | Worst Normal Loading Condition |  | 2.5 |  |  |  |  |  |  |  |
| 2.2 |  | Exceptional Loading Condition (unbalanced load) |  | 1.5 |  |  |  |  |  |  |  |
| 3 |  | Foundation against overturning or uprooting |  |  |  |  |  |  |  |  |  |
| 3.1 |  | Worst Normal Loading Condition: |  | 2.5 |  |  |  |  |  |  |  |
| 3.2 |  | Exceptional Loading Condition (unbalanced load) |  | 1.5 |  |  |  |  |  |  |  |
| 4 |  | Earth anchor against uprooting: |  |  |  |  |  |  |  |  |  |
| 4.1 |  | Worst Normal Loading Condition |  | 2.5 |  |  |  |  |  |  |  |
| 4.2 |  | Exceptional Loading Condition (unbalanced load) |  | 1.5 |  |  |  |  |  |  |  |
| 5 |  | Insulators and fittings based on minimum failing load: |  |  |  |  |  |  |  |  |  |
| 5.1 |  | Worst Normal Loading Condition |  | 3.0 |  |  |  |  |  |  |  |
| 5.2 |  | Exceptional Loading Condition (unbalanced load) |  | 2.0 |  |  |  |  |  |  |  |
| Date:__________________ Signature of Bidder: _______________________ 10.14 Assumed Maximum Working Conditions |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Section and Paragraph |  | Unit |  | Guarantee |  | Bidders to fill in |  |
| 1 |  | Minimum temperature of conductors and earthwires |  | oC |  | +2 |  |  |  |
| 2 |  | Maximum temperature of conductors and earthwires |  | oC |  | +80 |  |  |  |
| 3 |  | Wind pressure per square meter on projected area of conductors and earthwires (using wind span x reduction factor = 0,8) insulator sets and guy wires |  |  |  |  |  |  |  |
| 3.1 |  | All loading cases |  | N/m2 |  | 430 |  |  |  |
| 4 |  | Wind pressure per square meter on one-and-a-half times projected area of members of one face of towers: |  |  |  |  |  |  |  |
| 4.1 |  | All loading cases |  | N/m2 |  | 820 |  |  |  |
| 5 |  | Mass of insulator set: |  |  |  |  |  |  |  |
| 5.1 |  | Suspension string, jumper string, 132kV |  | Kg |  |  |  |  |  |
| 5.2 |  | Tension string (per conductor), 132kV |  | Kg |  |  |  |  |  |
| 6 |  | Site altitude above sea level |  | m |  | 1000-1500 |  |  |  |
|  |  | Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |  |
| Date:__________________ Signature of Bidder: _______________________ |  |  |  |  |  |  |  |  |  |

10.15 Earthwire Data and Loads

| Ser. No. | Particulars | Unit | Bidder To Fill In |  |
| --- | --- | --- | --- | --- |
|  |  |  | Employer's Requirements | Bidder's Specifications |
| 1 | Appropriate International Standard |  | BS 183 |  |
| 2 | Materials of Conductor |  | Galvanised Steel |  |
| 3 | Cross section | mm2 | 104 |  |
| 4 | Number and diameters of wire: |  | 19 x 2.64 |  |
| 5 | Overall diameter of conductor | mm | 13.2 |  |
| 6 | Mass of conductor per kilometre | Kg/km | 821 |  |
| 7 | Tension of conductors in still air at 15oC at erection | N | 16,500 |  |
| 8 | Maximum working tension of earth conductor | N | 20,500 |  |
| 9 | Maximum working tension of earth conductor downlead |  | 4000 |  |
| 10 | Rated breaking strength of conductor | N | 96,200 |  |
| 11 | Assumed equivalent modulus of elasticity of conductor |  |  |  |
|  | Initial | Mpa | 193,000 |  |
|  | Final | MPa | 193,000 |  |
| 12 | Assumed equivalent coefficient of linear expansion of conductor | per oC | 11.5x10-6 |  |
| 13 | Permanent elongation due to creepage | m/m | 0 |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |
|  | Date:___________________________ Signature of Bidder: ___________________ |  |  |  |

10.16 Tower Design Particulars

| Ser. No. |  | Particulars | Unit |  |
| --- | --- | --- | --- | --- |
| s/n | Particulars | Unit | ZESCO Minimum Specs | Biddder to fill in |
|  |  |  | 132kV Towers |  |
| 1 | Maximum Working Conditions |  |  |  |
| 1.1 | Minimum temperature of conductor and OPGW | Deg. | -1 |  |
| 1.2 | Maximum temperature of conductor and OPGW | Deg. | 80 |  |
| 1.3 | Site altitude asl. | M | 850-1200 |  |
| 1.4 | Wind pressure on projected area of conductors, OPGW & insulator sets |  |  |  |
|  | - Loading cases except erection |  |  |  |
|  | - Loading case erection | N/m2 | 430 |  |
|  | Wind pressure on towers | N/m2 | 130 |  |
| 1.5 | - Loading case except erection |  |  |  |
|  | - Loading case erection | N/m2 | 820 |  |
|  | Mass of insulator sets (set is for all phases) | N/m2 | 250 |  |
| 1.6 | - Suspension |  |  |  |
|  | - Tension |  |  |  |
| 2 | Factors of Safety |  |  |  |
| 2.1 | Tower foundation steel work |  |  |  |
|  | - Normal load conditions |  | 2.5 |  |
|  | - Unbalanced load conditions |  | 1.5 |  |
| 2.2 | Foundations against overturning and uprooting |  |  |  |
|  | - Normal loading conditions |  | 2.5 |  |
|  | - Unbalanced loading conditions |  | 1.5 |  |
|  | - Bearing capacity, all loading conditions |  | 2.5 |  |
| 3 | Conductor data for tower design |  |  |  |
| 3.1 | Number of conductors per phase |  | 1 |  |
| 3.2 | Code Name |  | Bison |  |
| 3.3 | Appropriate IEC Standard |  |  |  |
| 3.3 | Materials of conductor |  | ACSR |  |
| 3.4 | Number and diameter of wires |  |  |  |
|  | - Aluminium |  | 30/3.0 |  |
|  | - Steel |  | 7/3.0 |  |
| 3.5 | Mass of conductor per km |  |  |  |
|  | - Without grease | Kg | 974 |  |
|  | - With Grease | Kg | 986 |  |
| 3.6 | Maximum working tension of conductor |  |  |  |
| 3.7 | Rated breaking strength of conductor | kN | 92 |  |
| 3.8 | Assumed modulus of elasticity of conductor |  |  |  |
|  | - Initial |  |  |  |
|  | - Final | kN |  |  |
| 3.9 | Assumed equivalent coefficient of linear expansion of conductor |  |  |  |
| 4 | Earthwire Data for Tower Design (OPGW) |  |  |  |
|  | Maximum overall diameter | mm |  |  |
|  | Maximum weight per kilometre | kg |  |  |

10.17 Tower Design Particulars

| Ser. No. |  | Particulars | Unit |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | Employer's Requirements | Bidders to fill in |
| 5 | Modulus of elasticity |  |  |  |  |
|  |  | a) Mild steel | Mpa |  |  |
|  |  | b) High tensile steel | Mpa |  |  |
| 6 | Quality of steel in bolts and nuts |  |  |  |  |
|  |  | a) Relevant International Standard |  |  |  |
|  |  | b) Minimum yield stress | N/mm2 |  |  |
|  |  | c) Minimum breaking stress | N/mm2 |  |  |
| 7 | Minimum ratios of slenderness assumed in design: |  |  |  |  |
|  |  | a) Main members |  | 250 |  |
|  |  | b) Stressed bracings |  | 200 |  |
|  |  | c) Unstressed bracings |  | 120 |  |
| 8 | Minimum thickness of material |  | mm | 4 |  |
| 9 | Minimum bolt diameter |  | mm | 12 |  |
| 10 | Maximum thickness of members for which holes punched |  | mm |  |  |
| 11 | Minimum Zinc coating |  |  |  |  |
|  |  | a) For members | g/m2 |  |  |
|  |  | b) For bolts and nuts | g/m2 |  |  |
|  |  | Note: The schedule shall be completed and submitted with the bid |  |  |  |
|  |  | Date:___________________________ Signature of Bidder: _______________________ |  |  |  |

10.18 Particulars of Suspension and Tension Towers

| SN | Particulars | Unit |  | Guarantees for 132kV tower |  |  |  | Bidders to fill in for all tower types |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | A | B | C | D | E |  |
|  | Tower Type |  | Suspension | Tension | Tension | Tension | Tension |  |
| 1 | Type of insulator sets |  | Suspension | Tension | Tension | Tension | Tension |  |
| 2 | Min. ground clearance at 80oC | m | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 |  |
| 3 | Maximum angle of deviation | Deg. | 0-2 | 0-10 | 10-30deg | 30-60 | 60-90 |  |
| 4 | Design span length | m | 250 | 250 | 250 | 250 | 250 |  |
| 5 | Sag in design span | m |  |  |  |  |  |  |
| 6 | Height above ground of lowest conductor attachment point | m | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 |  |
| 7 | Min. height of earth wire above upper conductor |  |  |  |  |  |  |  |
|  |  | m |  |  |  |  |  |  |
| 8 | Vertical spacing between phase conductors |  |  |  |  |  |  |  |
| 9 | Min. overall standard tower height above ground level | m |  |  |  |  |  |  |
| 10 | Horizontal distance from tower centre to phase attachment | m | specify | specify | specify | specify | specify |  |
| 11 | Mass of complete tower of basic height |  |  |  |  |  |  |  |
|  | (+/- 0) | m |  |  |  |  |  |  |
|  |  | Kg |  |  |  |  |  |  |
| 12 | Quality of Materials |  |  |  |  |  |  |  |
| 13 | Tower steel members standard |  |  | EN 10025 |  |  |  |  |
|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |  |  |  |  |

|  | Date:__________________________ Signature of Bidder: ___________________ 10.19 Insulator Sets |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Ser.No. | Particulars | Unit | M |  |  |
|  | Complete Insulator For 132kV Single Conductor, ACSR-BISON |  | 132kV | 132kV |  |
|  |  |  | Suspension Insulator, arcing horn both ends | Tension Insulator, arcing horn both ends |  |
| 1 | Number of insulators per phase |  |  |  |  |
| 2 | Length of complete set, including fittings | mm |  |  |  |
| 3 | Weight of complete insulator | kg |  |  |  |
| 4 | Breaking strength of insulator set: |  |  |  |  |
|  | a) Set with single insulator string | N |  |  |  |
|  | b) Set with double insulator set | N |  |  |  |
| 5 | Overall leakage distance per insulator | mm |  |  |  |
| 6 | Length of protected leakage path per insulator: |  |  |  |  |
|  | a) Minimum | mm |  |  |  |
|  | b) Actual | mm |  |  |  |
| 7 | Gap between arcing horns | mm |  |  |  |
| 7 | Power frequency (50 Hz) withstand voltage: |  |  |  |  |
| 7.1 | Dry 1 minute | kV |  |  |  |
| 7.2 | Wet 1 minute | kV |  |  |  |
| 8 | Dry lightning impulse withstand voltage: |  |  |  |  |
| 8.1 | 1.2/50 Postive wave | kV |  |  |  |
| 8.2 | 1.2/50 Negative wave | kV |  |  |  |
| 9 | Wet switching impulse voltage: |  |  |  |  |
| 9.1 | Positive wave | kV |  |  |  |
| 9.2 | Negative wave | kV |  |  |  |
| 10 | Dry flashover of complete set | kV |  |  |  |
| 11 | Wet flashover of complete set | kV |  |  |  |
| 12 | Corona voltage | kV |  |  |  |
| 13 | Whether complete drawings of insulator string assemblies are submitted with Tender |  |  |  |  |
| 14 | Whether the insulator string assemblies are complete in every respect |  |  |  |  |

|  | Note: The schedule shall be completed and submitted with the bid |  |  |  |
| --- | --- | --- | --- | --- |
| Date:__________________________ Signature of Bidder: _____________________ |  |  |  |  |

10.19 132kV Cable Particulars

| S/N | Particulars | ZESCO Minimum Requirement | Bidder to Fill In |
| --- | --- | --- | --- |
| 1 | No. of cores | 1 |  |
| 2 | Size( in mm2) | 630 |  |
| 3 | Voltage Grade (in kV) | 76/132(145kV) |  |
| 4 | Name of manufacturer |  |  |
| 5 | Applicable standard | Generally to IEC 60840 |  |
| 6 | Permissible voltage & frequency variation for satisfactory operation |  |  |
| 7 | Max. rated conductor temperature | 900°C |  |
| 8 | Max. allowable conductor temp. during short circuit | 2500°C |  |
| 9 | Continuous Current carrying capacities of single circuit for conditions, | Single End Bonding / Cross Bonding |  |
|  |  | Trefoil Formation |  |
| 10 | (a) In air • ...... ...(A) at 30 0C | 1145 |  |
| 10 | (b) In ground...(A) at 200 C Thermal resistivity 1.5 K.m/W Depth : 1500mm | 705 |  |
| 11 | CONDUCTOR |  |  |
|  | Material | Aluminium (Water Tight) |  |
| (ii) | Shape | Stranded compacted circular class 2 to IEC: 60228 |  |
| (iii) | Nominal cross sectional area (mm 2 ) | 630 |  |
| (iv) | Approximate diameter of conductor (mm) | 29.6 |  |
| 12 | CONDUCTOR SCREEN |  |  |
|  | Material | Extruded semiconducting compound |  |
| (ii) | Minimum thickness (mm) | 0.8 |  |
| (iii) | Nominal thickness (mm) | 1.0 |  |
| 13 | INSULATION |  |  |
|  | Material | Cross linked Polyethylene |  |
| (ii) | Nominal thickness (mm) | 18.0 |  |
| (iii) | Minimum thickness (mm) | 16.2 |  |

| Date: ___________________ Signature of Bidder: ___________________ |  |
| --- | --- |

10.20 Drawings, calculations and Information to be submitted with the Bid.

| 1. Foundations |  |
| --- | --- |
| General outline drawings showing the following |  |
| - Outline and general arrangement of foundations |  |
| - Description of soil testing method |  |
| - Drawing list |  |
| Drawings need have leading dimensions only. |  |
| Foundation drawings shall have the dimensions for excavation depths, reinforcement and concrete quantities |  |
| 2. Towers |  |
| General outline drawings showing the following |  |
| - Outline and general arrangement for all Standard towers, showing the position of main joints, positions of step bolts and notice plates |  |
| - Electrical clearance diagrams for all tower types. |  |
| - Arrangement of conductor and earth wire attachment point for all tower types. |  |
| - Loading diagrams for all tower types |  |
| - Weights of individual tower components (basic body, body extension, leg extensions and stubs) |  |
| - Danger/ownership plates, aerial number signs, line designation/tower number plates and phase plates. |  |
| - Drawing list. |  |
| Tower drawings shall have dimensions of main members. |  |
| Date: ___________________ Signature of Bidder: _____________ |  |

10.21 Drawings and Information to be submitted with the Bid

| 1. Dimensioned drawings of complete insulator and earthwire attachment assemblies |  |
| --- | --- |
| 2. Detail drawings of: |  |
| - all connectors |  |
| - all clamps |  |
| - vibration dampers |  |
| - repair sleeves |  |
| - armour rods |  |
| - OPGW joint boxes including downlead clamps |  |
| - other hardware |  |
| 3. Drawings of insulators |  |
| 4. Drawing list |  |
| 5. Test reports |  |
| 6. Supply reports |  |
| Date: ________________________ Signature of Bidder: ___________________ |  |

Drawings and Information to be submitted after Award of Contract

1. Detailed, dimensioned drawings of complete insulator and earthwire attachment assemblies

2. Detailed, dimensioned drawings of all parts of which the insulator and earthwire attachment assemblies are completed.

3. Detailed, dimensioned drawings of all other hardware for conductors and earthwires

4. Drawing list

Note: All drawings shall be submitted within 6 weeks after contract award, in 4 copies, for examination and approval by the Project Manager.

10.22 Drawings, Calculations and Information to be submitted after Award of Contract

- Tower base dimensions for all towers including leg extensions, complete setting out data.

- Detailed calculations of all foundations including a detailed technical description of the proposed type(s)

-Templates showing the initial and final sag curves, sags and tensions of the conductors and the and temperatures, in accordance with the Specification.

-Longitudinal profiles with towers and sags plotted.

Date: ___________________ Signature of Bidder: _______________________

10.23 Drawings, Calculations, and Information to be submitted after Award of Contract

Within 10 weeks from award of contract the Contractor shall submit to the Project Manager 4 copies as listed below, for examination and approval.

List of documents to be examined and approved:

- Completely dimensional general arrangement drawing of each tension tower super-structure with each body extension. Diagram of external loads and wind loads on the towers at each point of application. Total weight of each tower type, including zinc coatings, bolts and all appurtenances.

- Erection drawings of tower super-structures and body extensions showing the members in place, clearly indicating all dimensions, the number, dimensions and strength class of bolts required, the identification number of each member.

- Live parts to metal clearance diagrams for each type of tension tower.

A tabulation of the calculations showing the design of each tower member, i.e. steel quality, angle size, unsupported length, slenderness ratio, member, size and strength, class of connection bolts required, ultimate strength of each member in compression, tension, shear and bearing and maximum design load from the loading conditions.

A tabulation form showing the design of the redundant members.

Calculation of foundation loadings.

Complete drawings and calculations of special towers and extensions as required.

Counterpoise connections.

Danger and property, route and tower number, phase and aerial number plates.

Updated work plans and schedules.

Detailed, dimensioned drawings of all complete insulator and earthwire attachment assemblies, and all fittings and hardware for conductors and earthwires.

Date: ________________________   Signature of Bidder:  ___________________

10.24 As Built Documentation to Be Submitted by The Contractor

After completion of works, the following documentation shall be submitted to the Project Manager, two reproducible hard copies, five black on white paper copies AND an electronic copy in AutoCAD 2000 format on Hard Drive, within one month after taking over:

- All foundation drawings, and

- All longitudinal profiles and route maps with towers plotted, and

- All drawings pertaining to earthing

- All tower drawings, including attachment to and/or anchoring in foundations.

- All drawings of insulators and fittings

In addition:

- 5 copies of earth resistance measurement results, and

- 5 copies of all OPGW tests carried out

- 5 copies of manufacturers specifications and brochures for supplied items

- 5 copies of other relevant technical documentation

Date: ___________________ Signature of Bidder: ______________________

Tensile stress

PART 3B: EMPLOYERS REQUIREMENTS:  DISTRIBUTION LINES

# WORKS REQUIREMENTS

- WORKS REQUIREMENTS

  - Background

The main objective of the project is to increase the power transfer capacity to Chingola, Lufwanyama, Chililabombwe, Kalulushi, Mufulira and Kitwe Districts by reinforcing the existing transmission and distribution network. This reinforcement will allow ZESCO Limited to supply power to customers whose power supply applications have been pending for some time. This is a turnkey contract and the Contractor’s duties as described in these bidding documents.

In execution of this contract the Contractor shall carry out all works in conformity with ZESCO’s Health and Safety minimum standards. The contractor is advised to acquaint him/herself with the Health and Safety policy requirements of ZESCO. Copies of the policy documents are attached in the Appendices.

  - General

The Bidder shall examine the requirements of this section in close connection with the other documents and particulars forming these Bid Documents. Special attention shall be paid to the General Specifications, the Particular Technical Specifications, and the Drawings.

Where the Specifications and/or Drawings do not contain specific materials or works which are necessary for the proper and safe completion, operation, and maintenance of the equipment in question, all such materials and works shall be deemed to be included in the supply for the turn-key based substation.

In the event of any difference between the Drawings and the Specifications, the latter shall prevail.

Should the Bidder find discrepancies in or omissions from these Specifications or from the other Documents, or should he be in doubt as to their meaning, he should immediately contact the Project Manager for interpretation, clarification, or correction thereof before submitting his Bid. Such action shall, however, in no case be considered as a cause for altering the closing date of the Bid.

  - Extent of Supply

The works called for here-in cover engineering design, manufacture, factory testing, seaworthy packaging or otherwise as required, shipment, inland transport, and delivery to site (DDP), erection, installation, testing and commissioning of all equipment to achieve a complete, safe, and fully operational overhead and underground lines.

  - Scope Of Works

This contract will involve the construction of 11kV and 33kV overhead and underground lines. The 33kV overhead lines shall be designed and constructed on H-Pole structure (intermediate and strain structures), using 350mm2 ACSR conductor, silicone rubber insulators and all other line accessories complete with aerial earth earthed at every span.

The following works will be carried out on the below-mentioned lines:

- Carry out detailed survey for all the distribution line routes outlined in the route maps under drawings section.

- Carry out bush (vegetation, trees, and anthills) clearing, route survey and profiling, pole spotting, conductor profiling

- Construction of access roads complete with culverts where necessary.

- Supply and installation of insulators, fittings, and hardware

- Supply and stringing of conductors.

- Supply and stringing of earth wires and OPGW complete with vibration dampers.

- Supply and installation of earthing counterpoise wire

- Supply and installation of bolts, nuts, washers, and other materials as specified in Bill of Quantities, to the extent required to complete the line installation.

- Terminate the lines to the line bays in the respective substations.

- Carry out works to restore existing feeder roads to their original condition or better.

- Carry out environmental restoration works as per Environmental Management Plan.

Additional scope includes:

  - Cable terminations of 11kV and 33kV overhead lines,

  - Cable terminations of 11kV and 33kV on cable take-off structures

  - Construction of strain/tension structures to link into the existing 11kV and 33kV.

For the 33kV OHL, the line shall have open points every 1km using complete assemblies of try links to ease troubleshooting in times of faults.

The scope of works that must be executed by the Contractor are design, manufacture, factory testing, delivery to site, installation, site testing and commissioning to the entire satisfaction of the Employer of the following 11kV and 33kV lines scope of works: -

    - Chingola District

      - 33kV Distribution Lines

- Construction of 8km 33kV double circuit line from Chingola 330/132/33kV substation to Lulamba 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 8km 33kV line from Kabundi 132/33/11kV substation to Mulonga 33/3.3kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 5km 33kV line from Mulonga 33/3.3kV substation to Fitobaula 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

      - 11kV Distribution Power Evacuation

- Construct 3000m of 11kV overhead line using 100mmsq ACSR from Kabundi 132/33/11kV substation and link into Soweto (sub 18)

- Construct 5500m of 11kV overhead line using 100mmsq ACSR from Kabundi 132/33/11kV substation to sub 31.

- Construct 3500m of 11kV overhead line using 100mmsq ACSR from Kabundi 132/33/11kV substation and link into the existing overhead line at Kabuta market.

- Excavate, lay and terminate 2No. 800m of 185mmsq 3C 11kv XLPE cable from Nchanga 132/33/11kV substation to Nchanga north hospital.

- Excavate, lay and terminate 800m of 185mmsq 3C 11kV XLPE cable from Nchanga 132/33/11kV substation to sub 106.

- At Refractory 132/33/11kV, Link the existing 11kV lines into the new 11kV board

- Excavate, lay and terminate 2No. 3500m of 185mmsq 3C 11kV XLPE cables from Refractory 132/33/11kV substation to E1.

- At Refractory 132/33/11kV, Excavate, lay and terminate 50m of 185mmsq 3C 11kV XLPE cable to Chiwempala overhead line

- At Lulamba 33/11kV Substation, Link the existing 11kV lines into the new 11kV board.

- Construct 1200m of 11kV overhead line using 100mmsq from Fitobaula 33/11kV substation to Fitobaula rural health centre

    - Chililabombwe District

      - 33kV Distribution Lines

- Construction of 7km 33kV double circuit line from Chililabombwe 132/33/11kV substation to Chililabombwe North 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 6km 33kV double circuit line from Chililabombwe 132/33/11kV substation to Chililabombwe Central 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 9km 33kV double circuit line from Chililabombwe 132/33/11kV substation to Kakoso 132/33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 5km 33kV double circuit line from Chililabombwe North 33/11kV substation to Chililabombwe Central 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 10km 33kV double circuit line from Chililabombwe North 33/11kV substation to Kasumbalesa 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 5km 33kV double circuit line from Chililabombwe North 33/11kV substation to Kawama 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 5km 33kV double circuit line from Kakoso 132/33/11kV substation to Kawama 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 11km 33kV double circuit line from Kakoso 132/33/11kV substation to Fitobaula 33/11kV substation. Construction of 11km 33kV double circuit line from Kakoso 132/33/11kV substation to Fitobaula 33/11kV substation.

      - 11kV Distribution Power Evacuation

- Construct 5000m of 11kV overhead line using 100mmsq ACSR from Kasumbalesa 33/11kV substation to link into the Konkola township 11kV overhead line.

- Construct 200m of 11kV overhead line using 100mmsq ACSR from Kasumbalesa 33/11kV substation to link into Kasumbalesa 11kV overhead line.

- Construct 6000m of 11kV overhead line using 100mmsq ACSR from Kasumbalesa 33/11kV substation to Kasumbalesa tollgate.

- Construct 1500m of 11kV overhead line using 100mmsq ACSR from Kawama 33/11kV substation to Kawama township.

- Construct 1500m of 11kV overhead lone using 100mmsq ACSR from Kawama 33/11kV substation to Kameza east township.

- Construct 1000m of 11kV overhead line using 100mmsq ACSR from Kakoso 132/33/11kV substation to Kakoso south township.

- Construct 5000m of 11kV overhead line using 100mmsq ACSR from Kakoso 132/33/11kV substation and link into Fitobaula 11kV line

- Construct 1800m of 11kV overhead line using 100mmsq ACSR from Kakoso 132/11kV substation to Chililabombwe district hospital.

- Excavate, lay and terminate 800m of 185mmsq 3C XLPE 11kV cable from Bancroft north 33/11kV substation to number 3 shaft gate.

- Excavate, lay and terminate 1500m of 185mmsq 3C XLPE 11kV cable from Bancroft north 33/11kV substation to A3 substation. [ 4-way RMU required]

- Construct 2No. 1000m of 11kV overhead lines from Chililabombwe 132/33/11kV substation to the switching station

- At Chililabombwe 132/33/11kV Substation, excavate, lay and terminate 1200m of 185mmsq 3C XLPE 11kV cable from the switching station to sub 8.

- At Chililabombwe 132/33/11kV Substation, excavate, lay and terminate 200m of 185mmsq 3C XLPE 11kV cable from the switching station to water treatment substation

- At Chililabombwe 132/33/11kV Substation, excavate, lay and terminate 500m of 185mmsq 3C XLPE 11kV cable from the switching station to sub H (general offices)

- Construct 500m of 11kV overhead line using 100mmsq from Chililabombwe 132/33/11kV substation to link into Kameza overhead line

    - Kitwe District

      - 33kV Distribution Lines

- Construction of 19km 33kV double circuit line from New Kitwe 132/33/11kV substation to Mwambashi 132/33kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 8km 33kV double circuit line from New Kitwe 132/33/11kV substation to Nkana East 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 10km 33kV double circuit line from Nkana East 33/11kV substation to Luangwa 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 10km 33kV double circuit line from Luangwa 33/11kV substation to Nkana Mine 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 6km 33kV double circuit line from New Chimwemwe 33/11kV substation to New Scaw 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

      - 11kV Distribution Power Evacuation

- Construct 3500m of 11kV overhead line using 100mmsq ACSR from Chimwemwe 33/11kV substation to link into Chimwemwe district hospital overhead line

- At Chimwemwe 33/11kV Substation, construct 1000m of 11kV overhead line using 100mmsq ACSR to link into Mindola overhead line

- At Chimwemwe 33/11kV Substation, construct 1000m of 11kV overhead line using 100mmsq ACSR to link into Kafironda overhead line.

- Excavate, lay and terminate 2No. 500m of 185mmsq 3C 11kV cable from New Scaw 33/11kV substation to Scaw factory switching station.

- Excavate, lay and terminate 2No. 2000m of 185mmsq 11kV cables from New Scaw 33/11kV substation to UBZ switching station.

- Construct 3500m of 11kV overhead line using 100mmsq ACSR from New scaw 33/11kV substation to 6 Shaft substations.

- At New Scaw 33/11kV Substation, Excavate, lay and terminate 1500m of 185mmsq 11kV cable from Zambia Railways substation to Club Street substation.

- Construct 600m of 11kV overhead line using 100mmsq ACSR from William Street substation to N48

- Construct 1600m of 11kV overhead line from Luangwa 33/11kV substation to Chamboli extension (to link into existing Chibuluma overhead line)

- At Luangwa 33/11kV Substation, excavate, lay and terminate 50m of 185mmsq 3C 11kV XLPE cable and link into existing Chamboli 1 overhead line.

- At Luangwa 33/11kV Substation, excavate, lay and terminate 50m of 185mmsq 3C 11kV XLPE cable and link into existing Chibuluma overhead line.

- At Luangwa 33/11kV Substation, excavate, lay and terminate 50m of 185mmsq 3C 11kV XLPE cable and link into existing Ndeke township overhead line.

- At Luangwa 33/11kV Substation, Lay and terminate 2No. 50m of 185mmsq 3C 11kV XLPE cables from the 11kV board of 33/11kV to 11kV board of 66/11kV.

- Construct 2No. 5000m of 11kV overhead line using 100mmsq ACSR from Nkana 33/11kV substation to Women welfare.

- Construct 4500m of 11kV overhead line from Nkana 33/11kV substation to SOB main.

- At Nkana Mine 33/11kV Substation, excavate, lay and terminate 185mmsq 3C 11kV XLPE cable from SOB main to B6.

- Construct 6000m of 11kV overhead line from New Kitwe 132/33/11kV substation to Bulangililo waterworks

- Construct 4500m of 11kV overhead line from New Kitwe 132/33/11kV substation to Kitwe Industrial yard (CEEC)

- Construct 5700m of 11kV overhead line from New Kitwe 132/33/11kV substation to Mufuchani

    - Kalulushi District

      - 33kV Distribution Lines

- Construction of 5km 33kV line from Kalulushi 132/33/11kV substation to Kalulushi North 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 9km 33kV double circuit line from Kalulushi 132/33/11kV substation to Lwamisamba 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 14km 33kV double circuit line from Kalulushi 132/33/11kV substation to Nkana Mine 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 11km 33kV double circuit line from Kalulushi 132/33/11kV substation to New Scaw 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 6km 33kV double circuit line from Lwamisamba 33/11kV substation to Chibuluma 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 12km 33kV double circuit line from Lwamisamba 33/11kV substation to Kalulushi Airport 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 11km 33kV double circuit line from Kalulushi Airport 33/11kV to Nkana Mine 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 18km 33kV double circuit line from Kalulushi Airport 33/11kV to Luswishi T. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 22km 33kV line from Mufulira 132/33kV substation to New Chambishi Primary 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 13km 33kV line from Mufulira 132/33kV substation to Musonda 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 5km 33kV line from New Chambishi Primary 33/11kV substation to Musonda 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 10km 33kV line from Musonda 33/11kV substation to Nsato 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Integration at New Chambishi 33/11kV substation of the existing 33kV line from Kafironda substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

      - 11kV Distribution Power Evacuation

- Excavate, lay and terminate 2No. 1500m of 185mmsq 3C 11kV XLPE cable from 11kV board at Kalulushi 132/33/11kV to 11kV board at Kalulushi 66/11kV.

- Excavate, lay and terminate 100m of 185mmsq 3C XLPE cable from Kalulushi 132/33/11kV substation to link into Huifan overhead line.

- Excavate, lay and terminate 100m of 185mmsq 3C XLPE cable from Kalulushi 132/33/11kV substation to link into Kylin metals overhead line.

- At Lwamisamba 33/11kV Substation, construct 1000m of 11kV overhead line link into Makeni JVC

- At Lwamisamba 33/11kV Substation, construct 1000m of 11kV overhead line to link into Chapula

- At Lwamisamba 33/11kV Substation, construct 1000m of 11kV overhead line to link into Chief Nkana

- At Kalulushi Airport 33/11kV Substation, construct 1000m of 11kV overhead line using 100mmsq ACSR to MEF farms.

- At Kalulushi Airport 33/11kV Substation, construct 3000m of 11kV overhead line and link into Chibululuma from Luangwa

- At Kalulushi North 33/11kV Substation, excavate lay and terminate 50m of 185mmsq 3C 11kV XLPE cable from the 11kV board and link into waterworks feeder.

- At Kalulushi North 33/11kV Substation, excavate lay and terminate 50m of 185mmsq 3C 11kV XLPE cable from the 11kV board and link into Kalengwa north extension feeder.

- At Chibuluma 33/11kV Substation, excavate, lay and terminate 50m each of 185mmsq 3C 11kV XLPE cables for the following feeders; -

- Kalengwa south

- St. Marceline

- Kalengwa east

- Uprating of 3.3kV Network in Kalulushi-Replacement of 6km of 3.3kV cable with 70mmsq 3C 11kV XLPE cable

- Uprating of 3.3kV Network in Kalulushi-Provision and installation of 9No. 3-way ring main units and 2No. 4-way ring main units

- Uprating of 3.3kV Network in Kalulushi-Replacement of 14No. 3.3/0.4kV transformers with 1No. 100kVA, 3No. 200kVA, 2No. 315kVA, 4No. 500kVA and 1No. 750kVA 11/0.4kV transformers

- Uprating of 3.3kV Network in Kalulushi-Excavate, lay and terminate 800m of 70mmsq 3C 11kV XLPE cable from President substation to sub-2

    - Mufulira District

      - 33kV Distribution Lines

- Construction of 14km 33kV double circuit line from Mufulira 132/33kV substation to Ndeke 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 6km 33kV double circuit line from Mufulira 132/33kV substation to Mufulira West 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 16km 33kV double circuit line from Mufulira West 33/11kV substation to Ndeke 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 20km 33kV line from Mufulira West 33/11kV substation to Nsato 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Construction of 19km 33kV line from Ndeke 33/11kV substation to Mokambo 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

      - 11kV Distribution Power Evacuation

- Excavate, lay and terminate 2x1000m of 185mmsq 3C 11kV XLPE cable from Mufulira west 33/11kV substation to sub 50

- Construct 1000m of 11kV overhead line using 100mmsq ACSR from sub 50 to sub 67

- Construct 5000m of 11kV overhead line using 100mmsq ACSR from Mufulira west to sub 71

- Construct 1200m of 11kV overhead line using 100mmsq from Kankoyo Asphalt plant to link into Butondo 11kV network.

- At Kankoyo, Sub 94 & Muf West Substation, T-off from sub50/sub67 11kV overhead line and construct 1500m of 11kV overhead line using 100mmsq ACSR to sub 140.

- Excavate, lay and terminate 4000m of 185mmsq 3C 11kV XLPE cable from Ndeke 33/11kV substation to sub 36.

- Construct 2500m of 11kV overhead line using 100mmsq ACSR from Ndeke- 33/11kV substation to Kawama east

- Construct 6000m of 11kv overhead line using 100mmsq ACSR from Ndeke 33/11kV substation to link into Murundu Mokambo 11kV overhead line

    - Lufwanyama District

      - 33kV Distribution Lines

- Construction of 14km 33kV double circuit line from Mufulira 132/33kV substation to Ndeke 33/11kV substation. The line shall be on Wooden H pole structure with single Bison conductor per phase.

- Integration at Funda 33/11kV substation on the existing 14.4km 33kV Funda – Lusiwishi Farm Block 33kV overhead line

  - Project Milestones

The total project delivery time from manufacture, to installation, testing and commissioning, shall be 36 (thirty-six) months. The Bidder shall submit the project schedule together with the bid. With respect to the Contract Effective Date and Project Commencement Date, the following delivery times or project milestones shall apply: -

- Within 3 month: Detailed design drawings for all aspects of the works.

- Within 6 months: Delivery of materials commences.

- Within 8 months: Delivery of materials is completed, and installation commences.

- By end of month 36: Works completed, and overhead line handed over.

# TECHNICAL SPECIFICATIONS

- TECHNICAL SPECIFICATIONS

  - Preamble

The Bidder shall examine the specifications of this section in close connection with the other sections of this Bid Document. Special attention shall be paid to General Specification and Particular Technical Specifications and the Drawings.

If the Specifications and/or Drawings do not contain particulars of materials or works which are necessary for the proper and safe completion, operation and maintenance of the equipment in question, all such materials and works shall be deemed to be included in the supply for the turn-key based solution requested here-in.

In the event of any difference between the Drawings and the Specifications, the latter shall prevail.

Should the Bidder find discrepancies in or omissions from these Specifications or from the other Documents, or should he be in doubt as to their meaning, he should immediately contact the Employer for interpretation, clarification, or correction thereof before submitting his Bid. Such action shall, however, in no case be considered as a cause for altering the closing date of the Bid.

  - General Technical Requirements

    - Scope

This specification covers the general design requirements and technical parameters of system operation and environmental conditions.

    - Definitions and Terminology

Wherever the term standard is used in this specification, this shall mean the international / national standard issued at the date of tendering in the following order of priority.

Although IEC standards for workmanship, material and equipment have been selected in these specifications as a basis of reference, standards, specifications and recommendations of International Standardising Organisations (ISO) will be acceptable provided they ensure equal or higher quality than those specified and furthermore that the Contractor submits for approval detailed specifications which he proposes to use.

Except where modified by this Specification or other client specifications, equipment and materials shall be in accordance with IEC (International Electrotechnical Commission) and ISO (International Organisation for Standardisation) Recommendations. SABS standards shall also be acceptable. If relevant IEC and ISO Recommendations do not exist in a particular case or cases then relevant National Standards shall be applied, if available. Such National Standards shall be proposed by the Contractor for approval for the purpose by the Project Manager.

When IEC or ISO Recommendations or National Standards are referred to, the Edition shall be the one current at the Date of Bid together with any Amendments issued by that date. A list of national standards for equipment not complying with IEC standards to be used in the manufacture and construction of the equipment shall be given.

If requested by the Engineer, the Contractor shall supply three copies in English and one in the original language of any national standards which are applicable to the Contract. The cost shall be borne by the client.

All apparatus and material supplied, and all work carried out shall comply in all aspects with the requirements of the Contract Agreement and such regulations which may be in force.

    - DESIGN AND STANDARDISATION

The Contract Works shall be designed to facilitate inspection, cleaning, and repairs and for operation in which continuity of service is the first consideration. All apparatus shall be designed to ensure satisfactory operation under the atmospheric conditions prevailing at the Site and under such sudden variations of load and voltage as may be met with under working conditions of the system, and short circuits, including those due to faulty synchronising, within the rating of the apparatus. The general operating conditions are given in this specification.

All equipment offered shall be products of recognised and experienced manufacturers and shall be proven equipment of the same basic design and size similar to that which has been in successful continuous operation for at least three years preferably under similar climatic conditions. Proven plant reliability and high availability are of prime importance and the attention of the Bidder is drawn to these particular requirements.

The design shall incorporate every reasonable precaution and provision for the safety of all those concerned in the operation and maintenance of the Contract Works and of associated works supplied under other Contracts.

Materials which are susceptible to mould growth in the tropics shall be treated to exclude moisture and prevent growth of mould after all machining has been carried out.

All material used shall be of the best quality and of the class most suitable for working under the conditions specified and shall withstand the variations of temperature and atmospheric conditions arising under operating conditions without distortion or deterioration or the setting up of undue stresses in any part and also without affecting the strength and suitability of the various parts for the work which they have to perform. No welding, filling, or plugging of defective parts will be permitted without the sanction in writing of the Project Manager.

In no part of the equipment, including busbars, connections, disconnectors, fuses, contacts, and cable boxes shall the temperature rise exceed the values specified in the relevant IEC or equivalent Standards.

Corresponding parts liable to renewal shall be interchangeable. When required by the Project Manager, the Contractor shall demonstrate this quality. All apparatus shall operate without producing undue vibration and with the least practicable amount of noise.

Cast iron shall not be used for chambers of oil-filled apparatus or for any part of the equipment which is under over-pressure or subject to impact stresses except where it can be shown that service experience has been satisfactory with the grade of cast iron and the duty proposed.

Operating boxes, cubicles and similar enclosed compartments forming part of auxiliary equipment shall be adequately ventilated to restrict condensation, and suitable anti-condensation heaters shall be provided. All contactor and relay coils and other parts shall be suitably protected against corrosion.

Means shall be provided for the easy lubrication of all bearings and where necessary, of any mechanism or moving part. Grease lubricators shall be fitted with hexagon nipples. All mechanisms shall, when necessary, be constructed of stainless steel, brass or gunmetal to prevent sticking due to rust or corrosion.

All taper pins used in any mechanism shall be of the split type. All connections and contacts shall be of ample section and surface for carrying continuously the specified full load currents without undue heating and shall be secured by bolts or set screws of ample size fitted with locking devices of approved type and material.

All rubbing or wearing surfaces shall be machine surfaced. Joints employing a gasket material shall be so constructed that the packing is maintained under sufficient compression in all parts so that an efficient joint can be made without the use of jointing compounds. Gasket material shall be of the minimum thickness necessary and of applicable composition for the site conditions.

All apparatus shall be designed to exclude vermin and insects from entering the equipment.

      - Galvanising

Galvanising shall be applied by the hot dipped process. The preparation for galvanising and the galvanising process shall not affect the mechanical properties of the material being coated. Drilling, punching, cutting, bending, removal of burrs and all machining shall be completed before galvanising.

The zinc coating shall be smooth, clean and of uniform thickness and free from defects. The preparation for galvanising and the galvanising itself shall not adversely affect the mechanical properties of the coated material.

All galvanised steel which has been cut, drilled, or worked on site shall be painted with an approved zinc rich paint.

The average thickness of the zinc coating shall be equivalent to not less than 0.6 kg/m2 of zinc for all surfaces, except steel wires, bolts, and nuts. Galvanising will be tested in accordance with the appropriate ISO or equivalent standards in order to determine that it complies with this requirement.

The thickness of the zinc coating for steel wires shall be in accordance with BSS EN 792 standard and shall be approved by the Project Manager. All galvanised wires on which tools have been used or cut shall be treated with approved bitumastic paint.

All bolts and screwed rods for the connection of galvanised steel parts shall be galvanised including the threaded portion(s) to a minimum average coating weight of 305 g/m2. The threads of all bolts and screwed rods shall be cleared of spelter by spinning or brushing. A die shall not be used for cleaning the threads unless specially approved by the Project Manager. All nuts shall be galvanised except for the threads which shall be oiled.

White rust formation after galvanising must be inhibited using an approved inhibitor applied according to the manufacturer’s instructions.

Material on which galvanising has been damaged shall be re-dipped unless; in the opinion of the Engineer the damage is local and can be repaired by applying a coat of galvanising repair paint. Where such repair is authorised, the damaged area shall be cleaned by wiping with clean rags saturated with mineral spirits or xylene followed by wire brushing. After wire brushing, the area shall be re-cleaned with solvent to remove residue and shall be given a minimum of two coats of zinc rich paint in accordance with the manufacturer’s instructions.

      - Aluminium and Aluminium Alloys

Aluminium shall be of high commercial quality. The composition, including the percentage and nature of any impurities, shall be stated in the Schedules. All aluminium alloys shall be of approved compositions as stated in the Schedules.

Aluminium and alloy castings shall be sound and free from air pockets and pin holes.

      - Marking and Nameplate Labels

All equipment shall be clearly and permanently marked in English text, to the approval of the Project Manager. Where marking plates are provided for making clear the method of operation of equipment, they shall be concise and preferably diagrammatic in form.

Rating and diagram plates of all equipment shall specify the rating and data specified in the appropriate standards for the equipment. In addition to the rating plates all equipment shall be provided with marking plates indicating the function of the apparatus group (like” feeder xx”), the name of the equipment and the device code used in the drawings.

Danger warning plates in English shall have red lettering on a white background. All other marking plates shall have black lettering on a white background.

Control and relay panels, marshalling boxes, kiosks etc., shall be marked in a concise and comprehensive manner, making clear the function and the method of operation of the equipment. These labels shall be fitted to the front and back of all equipment.

Labels, marking and name plates, and their fixing screws for outdoor use shall be of stainless steel or other corrosion resistant material. Where the use of vitreous enamelled labels is approved, the whole surface including the back and edges shall be properly covered and protective washers shall be provided on the front and back fixing screws. The fixings shall prevent undue vibration in particular on the transformer name plates.

Marking for similar equipment shall be of uniform appearance and size, and the dimensions of the labels and size of the letters shall be to the approval of the Project Manager. Before production of marking plates and notices the Contractor shall submit to the Project Manager full scale drawing of the proposed markings.

| EQUIPMENT | LABEL SIZE mm | LETTERING SIZE and THICKNESS mm |
| --- | --- | --- |
| Main labels on panels, cubicles, kiosks, control & similar equipment | 150 x5 | 20 x 1.5 |
| Control, Selector, and change-over switches | 70 x 30 | 12 x 1.5 |
| Fuses and links | 35 x 15 | 5 x 1 |
| Relays & contactors | 60x20 | 5 x 1 |

      - Nuts, Bolts and Washers

Nuts and bolts in metric sizes shall be used. Bolts and studs for electrical connections shall preferably be of brass M6 size. Alternatively, size M5 may be used, but these must be of stainless steel, phosphor bronze or high tensile brass.

Nuts and pins shall be locked in position with lock nuts or lock washers, or other devices if approved. Lock washers shall not be used above M24 size except when a spring type is specially approved. In steel constructions no bolt or stud shall project through its nut by more than approximately 10 mm or four threads whichever is the less, except for terminals and relay stems.

Bolts, nuts and washers on outdoor equipment shall be of non-corroding material where they are in contact with non-ferrous parts in conductor clamps and fittings and elsewhere if specially required. Suitable special spanners shall be provided for bolts and nuts which are not properly accessible by means of an ordinary spanner.

All steel bolts of any one diameter on a structure shall be of the one grade of steel.

Split-pins shall be made of 315 stainless steel.  The nominal diameter of split-pins shall be a minimum of 3 mm for clevis pins up to and including 20 mm diameter.

Split-pin holes shall be 0.4 mm to 0.8 mm larger than the nominal diameter of the split-pin.

Split-pins shall have a length of 13 mm longer than the clevis pin diameter.

      - Cleaning and Painting

Before painting or filling with oil or compound all un-galvanised parts shall be thoroughly cleaned, free from rust, scale, burrs, grease and moisture and all external rough surfaces on castings shall be filled.

Successive coats of paint shall be applied to a clean, dry and properly prepared surface. Each coat shall be compatible with the preceding coat and the coat to follow. The colour and shade of all painted surfaces shall be to the approval of the Project Manager. All paintwork which has been damaged during transport or erection shall be made good to the approval of the Project Manager.

The following minimum painting requirement shall apply to all ferrous parts unless the Contractor can show, to the satisfaction of the Project Manager, that any alternative he proposes is in all respects equal or superior to the requirements specified below.

| APPARATUS | PAINTING |
| --- | --- |
| INTERNAL SURFACES |  |
| Kiosks and apparatus boxes for use outdoors | Three coats of paint, the final coat being an anti-condensation finish colored matt white. |
| Cubicles, kiosks and apparatus boxes for use indoors | Three coats of paint, the final coat being matt white. |
| EXTERNAL SURFACES |  |
| All ungalvanized surfaces other than nuts, bolts and washers which may be removed for maintenance purposes, for use outdoors | At the Manufacturer’s Works |
|  | (a) One priming coat of corrosion inhibiting paint applied immediately after cleaning (b) Two coats of non-glossy, oil and weather resisting paint applied after inspection and testing and before dispatch. |
|  | At Site One finishing coat of glossy, oil and weather resisting, non-fading paint applied after erection is complete. For equipment dispatched completely assembled, the final coat may be applied at the factory unless otherwise required by the Project Manager. |
| Exposed, ungalvanized nuts, bolts and washers which may be removed for maintenance purposes for use outdoors | One coat of oil and weather resisting, non-fading paint applied after erection. Dark Grey G12, SABS 1091-1975 |
| Panels, Cubicles, Kiosks and apparatus boxes for use indoors | Three coats of paint, the colour and finish of the final coat to be Light Grey G57 SABS 1091-1975 |

      - Insulating Oil and Gas

Sufficient oil or gas shall be supplied to fill all oil or gas filled equipment provided under this Contract. The oil or gas shall be of the appropriate type, compatible and suitable in all respects for use in the equipment when it is operated under the conditions laid down in this specification.

      - Prevention of Acidity

The design and all materials and processes used in the construction of the equipment shall be such as to reduce to a minimum the risk of development of acidity in the oil or gas. Special measures such as nitrogen sealing, or the use of inhibited oils are not required unless specified by the Project Manager.

      - Fire Protection

All apparatus, connections and cabling shall be designed and arranged to minimise the risk of fire and any damage which might be caused in the event of fire. In addition, a fire suppression system shall be installed.

      - Locking Devices and Padlocks

Facilities for applying safety or security padlocks to circuit-breaker operating mechanisms, disconnector and switch operating handles, control switches, control cubicles, marshalling boxes, substation gates and doors, etc. shall be provided. The facilities shall be suitable for padlocks having a hasp diameter of 10 mm. Wall mounting cabinets suitable for the accommodation of padlocks and keys while not in use shall be provided and mounted in approved positions in each substation and shall be suitably labelled.

      - Tools

The Contractor shall supply in lockable boxes, for the Employer’s use, all special tools that may be required for assembly, dismantling and adjustments to the equipment. The tools shall be unused and in new condition at the time of handover.

      - Power Cable Termination

All cable terminating boxes shall be complete with cable lugs to accept the cable sizes specified in the schedules or drawings, and sufficient quantities of tropical grade jointing compound where required.

      - Drawings

All working drawings shall be in English and shall be submitted to the Project Manager in triplicate for his approval. One copy shall be returned to the Contractor stamped “APPROVED” or APPROVED as NOTED” or RETURNED for CORRECTION. Approval of drawings shall not relieve the Contractor of any of his responsibility for correctness of design.

      - Spare Parts

Bidders shall submit a list of recommended spares to cover a five-year operation and maintenance period, together with a priced schedule. Some or all spares may be ordered at the prices in the schedule at any time during the contract period.

      - Erection Marks

All Plant that requires assembly at Site shall have distinguishing marks on it to facilitate erection and to identify the material in relation to drawings, material lists or shipping documents. All marks shall be legible and easily visible. Where relevant, erection marks shall be stamped before galvanising and shall be clearly visible after galvanising.

      - Packing of Material

Packing shall give adequate protection to the enclosed materials against mechanical damage during transport to its final destination, including rough handling during sea, rail and road transport and transition from one mode of transport to another.

Packing should preferably be stout close-boarded wooden cases of adequate thickness, suitably braced and banded and lined internally with water resistant material.  Cases transported or stored on open decks shall be roofed with asphalted felt.

Certain types of outdoor equipment may be crated, provided that adequate protection of vulnerable parts is assured. All pipe flanges shall be fitted with wooden covers not less than 40 mm larger in diameter than the flange.

Steelwork sections and similar items may be bundled provided that the ends are adequately protected, and the enclosing bands or wires are robust. Indoor electrical equipment must be enclosed in welded polythene envelopes inside packing cases and the envelopes shall be evacuated or have a desiccant inside.

All items in cases or crates shall be secured so that they are not free to move and cannot work loose in transport. If rotating parts are shipped within their bearings or mountings, they must be adequately braced and restrained to prevent relative movement. Loose items shall be placed in bags in a case, each bag having stitched onto it a metal label indicating the number and nature of its contents. Where a filler material is used in a case to restrict movement or provide additional protection it shall be non-hygroscopic.

All surfaces liable to corrosion shall be thoroughly cleaned and special steps adapted to the nature of the materials and the time interval between packing and unpacking shall be taken to prevent corrosion.

Steps shall be taken to ensure that insulated materials cannot be damaged by moisture, moulds, insects, or rodents. Items that include materials liable to be damaged by moisture shall be packed in hermetically sealed containers in which silica gel, or some other approved desiccant has been inserted.

Cases shall be marked with large lettering to show which side up the case is to be and if the contents are fragile, marked “FRAGILE” in large letters with the international wine glass symbol. Packages shall be marked with their place of destination in such a way that rough handling or the effect of weather cannot remove or obliterate the marking. Each item shall be marked with its gross weight. For all lifts over two tonnes, marks on the cases shall show where the weight is bearing and the correct positions for the slings.

The cases shall, whenever possible, be packed so that they can safely be placed any side uppermost and no reliance shall be placed on the ability of those who will handle the cases to read written instructions or to understand pictorial ones. Cases that have to be slung in a certain way shall, as far as possible, be so constructed that they cannot conveniently be slung in any other way and packages shall preferably be so large that they cannot be easily rolled over or thrown about; thus, when practicable small cases shall be crated together to form one larger one. Crates shall be sufficiently strong to be capable of being slung from the outside even when provision is also made for slings to be attached direct to a major article inside.

Special steps shall be taken to guard against theft during transport. No small items such as padlocks, nameplates and so forth which could be torn off or unscrewed shall be accessible.

Cases, crates, barrels, and drums shall be banded in such a manner as to obstruct the theft of any of the timber used for packaging and the bands shall be so secured that they are not rendered ineffective by shrinkage of the wood.

A descriptive and fully itemised list shall be prepared of the contents of each packing case. A copy of this list shall be placed in a waterproof envelope under a metal or other suitable plate securely fastened to the outside of one end of the case, and its position indicated by stencilling on the case. Where appropriate, drawings showing the erection markings of the items concerned shall be placed inside the case.

All stencilled markings on cases and crates, or other markings on descriptive metal tabs fixed to cable drums, bundles of structural steelwork and so forth, shall be applied in two places with a material which cannot wash off and shall be additional to any erection or other marks or impressions which may be specified elsewhere.

All packing cases shall become the property of the Employer.

      - Shipping Marks

Shipping marks are to be stencilled in oil-based paint in block letters and symbols. When unobstructed flat smooth surfaces of sufficient size are not available on the case for the shipping marks they are to be stencilled on marine-ply notice boards of adequate size and of at least 6 mm thickness securely fastened to the packing case.

      - Tests

As provided in the Conditions of Contract, the whole of the materials used in the Project shall be subject to such inspection and test at the manufacturer’s works as prescribed in the appropriate material standards, required in the specific clauses of the Contract or the Project Manager may direct from time to time as the work proceeds.

The manufacturer shall perform all tests as prescribed by IEC or other standards applicable to the equipment. In addition to these tests the manufacturer shall perform the tests specified in the manufacturer’s own factory standards for quality control.

The Project Manager reserves the right to witness any or all tests and the Contractor shall inform the Project Manager at least 14 days in advance of any tests which will be performed.  The cost of such inspection and tests, including the provision and use of test equipment, with a quantified number of visits by the Project Manager shall be agreed at contract negotiation and shall be included in the Contract Price.

If, due to the Contract work and/or component materials not complying with this specification, further tests are necessary, the Contractor shall pay all additional costs which may be incurred in re-testing. The approval by the Project Manager of the results of such inspection and tests shall not relieve the Contractor of his obligations under the Contract for the satisfactory performance of the plant and materials.

During the execution of the Contract, test specimens, if required by the Project Manager, shall be taken from the materials for the purpose of check tests or analyses by Independent Authorities. Such specimens shall be prepared for testing and forwarded at the expense of the Contractor to the Testing Authorities selected by the Project Manager.

The Contractor shall deliver to the Project Manager three copies of the test certificates covering all tests. In case the original certificate is not in the English language, three copies of a translation into English of the certificate plus one copy in the original language shall be delivered to the Engineer.

      - Type tests

Type tests shall have been carried out in the extent described in the relevant IEC or other standards applied to the equipment. New type tests will normally not be required for equipment which has been previously type tested by a recognised testing body and having test certificates certified by approved certifying bodies. For such type tests the Contractor shall submit to the Project Manager for his acceptance a copy of the test certificate as early as possible but at least 14 days before the time point when the equipment will be ready for testing. The Project Manager shall inform the Contractor at least 7 days before the above-mentioned time point, if he accepts the certificates as such or if additional testing is necessary.

      - Routine tests

Standard routine tests required by the product standards as well as manufacturer’s quality control tests shall be carried out on all materials.

      - Acceptance tests

Acceptance tests are tests which are separately specified in the product specifications of the document and shall be performed as described in these clauses. They may cover any specific test of the type, sample, routine, or other tests.

      - Site tests

Normal operating and functional tests shall be carried out by the Contractor on all operating mechanisms and electric circuits prior to handing over the installations. The Contractor shall inform the Project Manager of any site tests at least 7 days before the testing unless otherwise agreed between the Project Manager and the Contractor.

All electrical circuits installed at site and not having been tested at factory prior to delivery shall be subjected to insulation resistance test at appropriate voltage. Voltage tests with AC power frequency or DC voltage may be required, if specified in the equipment specifications or considered necessary be the Project Manager.

The Project Manager reserves the right to call for further tests which are in his opinion necessary to confirm satisfactory performance. Tests shall as far as possible, simulate site conditions.

      - Site Conditions

The site conditions shall be assumed to be as follows:

| DESCRIPTION | UNIT | VALUE |
| --- | --- | --- |
| 1. Altitude of site above sea level | m | 1400 |
| 2. Ambient Temps:- Maximum Minimum Shade (for cable rating purposes) Ground (for cable rating) | oC oC oC oC | + 40 - 1 30 20 |
| 3. Extreme Wind Speed | m/s | 28 |
| 4. Isokeraunic Level | d/y | 86 |
| 5. Pollution Type |  | Dust |
| 6. Relative Humidity Maximum Minimum | % % | 85 39 |
| 7. Annual Rainfall Average | mm | 880 |
| 8. Hail |  | Occasional |
| 9. Soil Thermal Resistivity | Km/W | 1.2 |
| 10. Maximum Solar Radiation | w/m2 | 1200 |

      - Overhead Line Clearances

Minimum Clearance from any point on or about the permanent equipment where a person may be required to stand (measured from the position of the feet).

| Normal Operating Voltage | To the nearest unscreened live conductor in air. (m) | To the nearest part, not at earth potential, of an insulator supporting a live conductor. (m) |
| --- | --- | --- |
| not exceeding 15 kV | 2.6 | 2.45 |
| above 15kV but not exceeding 33kV | 2.75 | 2.45 |
| above 33kV but not exceeding 66kV | 3.0 | 2.45 |
| above 66kV but not exceeding 88kV | 3.2 | 2.45 |
| above 88kV but not exceeding 132kV | 3.6 | 2.45 |
| above 132kV but not exceeding 275kV | 4.6 | 2.45 |

      - Ground Clearance

The following table of conductor clearances shown in bold type are compatible with the existing ZESCO practice and as provided for under the CAP.811 Electricity Law.

      - Roadways

| Normal Operating Voltage between Line Conductors | Over Road Vehicular Traffic (m) | Other Areas except where specified |
| --- | --- | --- |
|  | Zambia | Zambia |
| Not exceeding 650 V | 5.5 | 4.9 |
| Over 650 V but not exceeding 33 kV | 5.8 | 5.2 |
| Over 33 kV but not exceeding 88 kV | 6.1 | 6.1 |
| Over 88 kV but not exceeding 132 kV | 6.7 | 6.7 |
| Over 132 kV but not exceeding 275 kV | 7.0 | 7.0 |
| Over 275 kV | 7.3 | 7.3 |

      - Railways

| Nominal Operating Voltage between Line Conductors | Min Height above Rail (m) |
| --- | --- |
|  | Zambia |
| Not exceeding 33 kV | 7.65 |
| Exceeding 33 kV but not exceeding 88 kV | 7.95 |
| Exceeding 88 kV but not exceeding 132 kV | 8.55 |
| Exceeding 132 kV but exceeding 275 kV | 8.85 |
| Exceeding 275 kV | 9.15 |

  - Particular Technical Requirements

    - GENERAL DESIGN DATA

The general electrical design data for the plant and equipment shall be as follows:

| Item | Description | Unit | Nominal Voltage Level | Nominal Voltage Level |
| --- | --- | --- | --- | --- |
|  |  |  | 33kV | 11kV |
|  | Nominal system voltage phase to phase | kV | 33 | 11 |
|  | Highest system voltage phase - phase | kV | 36 | 12 |
|  | System Frequency | Hz | 50 | 50 |
|  | Method of System Earthing (on 11 kV level E/C limited 1000 A) |  | Solid | Solid |
|  | Impulse withstand voltage (1.2/50 sec wave) - Internal insulation - External insulation, sea level | kV peak kV peak | 170 185 | 95 95 |
|  | Power frequency withstand voltage 1 minute - Internal insulation - External insulation, sea level | kV peak kV peak | 70 80 | 28 32 |
|  | Assumed highest switching surge |  | N/A | N/A |
|  | Substation clearances for equipment not subject to impulse tests - Phase - earth - Phase - phase - Terminals across isolating distance | mm mm mm | 320 320 380 | 250 270 270 |
|  | Cable box clearances for fully insulated shrouded terminals |  |  |  |
|  | - Phase - earth | mm | 100 | 32 |
|  | - Phase - phase | mm | 125 | 45 |
|  | - Phase - earth over cable surface | mm | 250 | 125 |
|  | Transformers |  |  |  |
|  | Winding insulation |  | Full | full |
|  | - Max flux density at any ratio or tap position | T | 1.8 | 1.8 |
|  | - Acceptable noise levels (1) | dB | 65 | 65 |
|  | Insulation Distances for Equipment, Bushings and Insulators |  |  |  |
|  | - Min surface creepage distance measured from live metal to fixing base | mm | 828 | 275 |
|  | - Min protected surface creepage distance | mm | 289 | 97 |
|  | - Min number of 254 mm diameter disc insulators in tension strings |  | 3 | 2 |
|  | Surge Arresters |  |  |  |
|  | Min. rated voltage | kV | 39 | 15 |
|  | - Nominal discharge current (8/20 s) | kA | 10 | 10 |
|  | - Class Distribution Min. protective ratio |  | 1.2 | 1.2 |

  - 11kV and 33kV Overhead Line

    - Overhead Line and Earth Conductors

Supports:	Wood poles, 14 m, H-structure on both intermediate and strain sections, 33kV

Wood poles, 12 m, H-structure on both intermediate and strain sections, 11kV

Conductors:	Bison (BS 215) ACSR, Dog ACSR

Aerial earth:	2 x galvanized steel wire or

1 x galvanized steel wire and 1 x OPGW.

Insulators:	Silicone rubber, suspension/tension

      - Overhead Line Conductor

General

The line conductors shall consist of aluminium conductor, steel reinforced, (hereinafter referred to as ACSR) of the cross section and having the characteristics stated in the Technical Schedules.  The conductors shall comply in all aspects with the requirements of IEC 1089 or BS215, parts 1&2. The steel core wires shall be preformed so that they remain inert when the conductor is cut.  The steel core shall be covered with an approved grease of applied mass per unit length as stated in the Technical Schedules.

The stranding of each layer of the conductor shall be as close and even as possible.  The outermost layer shall be right-handed.

The aluminium shall be of the highest purity commercially obtainable and the Contractor shall submit certificates of analysis giving the percentage and nature of any impurities in the metal of which wires are made.  Precautions shall be taken during manufacture, storage and erection of ACSR conductors to prevent the possibility of contamination by copper or other materials which may adversely affect the aluminium.

The line conductors shall be supplied on drums which are constructed in accordance with BS 1559 or other equivalent standard so as to enable the conductors to be run out smoothly and in lengths as long as can be conveniently handled and erected.  Drums shall be marked with type, size and length of conductor on the drum and also with an arrow to show the correct direction for rolling.  Wooden drums and battens shall be constructed from seasoned woods and be impregnated with a preservative against fungal and termite attack.

The preservative shall not react with aluminium and the barrel and sides of drums shall be covered with a waterproof paper or equivalent so as to ensure no damage to the conductors.

Empty conductor drums, where not returnable to the Vendor’s Works, shall be deemed after use to be the property of the client who shall be responsible for their disposal.

In case of local damage of some strands of a conductor during erection the use of repair sleeves of approved type may be permitted at the discretion of the project manager.

Joints

Joints for connecting line conductors shall be of approved types.  Tension joints for ACSR conductor shall be of the compression type.  The design of the joint shall be such as to make it impossible to position the steel sleeve incorrectly.  The electrical conductivity and current carrying capacity of each joint under the test conditions specified in the Data Sheets, shall not be less than those of the line conductor.  Tension joints shall not permit slipping of or cause damage to or failure of the complete line conductor or any part thereof at a load less that 95 per cent of the ultimate strength of the line conductor stated in the Technical Schedules and when tested in accordance with the test requirements.

All joints shall consist of as few parts as possible and there shall be no relative movement between individual layers of the conductor during assembly.  All caps or nuts shall, unless otherwise approved, be locked in an approved manner so that normal adjustment or removal of the caps for inspection shall not adversely affect either the locking device itself or any part of the fitting to which it is attached.  Non-tension joints shall not permit any slip or damage of the jumper connection at a load of less than 25% of the ultimate strength of the conductor, and shall be designed so that no loosening of the jumper connections can occur in service. Erection tools and methods shall be to approval, and no alteration in methods or erection or tools shall be made, after approval, without the written sanction of the project manager.

Where mating surfaces and jumper terminals are to be compressed onto the conductor or bolted together, they are to be protected by the application, at the Vendor’s works, of a strippable plastic coating or other approved means.

Following the installation of compression joints the electrical resistance of the joints shall be measured by means of approved micro ohm metre equipment in accordance with the test requirements. The values of resistance measured shall be recorded on a schedule which shall be submitted to the as part of the final records.

Where download connections to substation equipment require aluminium-to-copper connections, the fittings shall be of the Bi-metallic clamp compression type.

Where electrical connections employing dissimilar materials are to be made suitable precautions shall be taken to ensure electrolytic action does not occur between the mating surfaces.

    - ACSR Earth Conductors

      - General

The earth conductor shall comply with BS 183 and be tested in accordance with IEC 1089 in so far as it applies to steel wire.  The individual wires shall be performed so that they remain inert when the conductor is cut.

The individual wires shall be galvanised in accordance with 3.1 above. The wires shall be of uniform circular section, smooth and free from surface imperfections.

The stranding of each layer of the conductor shall be as close and even as possible.

There shall be no joints in individual wires in a drum length.

The provisions of the Specification in relation to line conductors, to line conductor drums and to the use of line conductor repair sleeves shall also apply to the earth conductors.

      - Joints and Clamps

Joints and tension clamps for earth conductors shall comply with the specified mechanical requirements for line conductor joints and clamps.

    - OPTICAL OVERHEAD GROUND WIRE (OPGW) AND ACCESSORIES

      - General

This specification covers the detailed requirements for the design, fabrication, test and shipping of composite Overhead Ground Wire with Optical Fibre (OPGW) and hardware/fittings.

      - Standards

The materials covered under this specification shall confirm to the following standards except as noted:

| EN 50182 | Conductors for overhead lines – round wire concentric lay conductors |
| --- | --- |
| EN 50183 | Conductors for overhead lines - aluminium magnesium silicon alloy wires |
| EN 61232 | Aluminium-clad steel for electrical purposes |
| IEC 60793-1 | Optical Fibres Part 1 – Generic Specification |
| IEC 60793-2 | Optical Fibres Part 1 – Product Specification |
| ITU T G652 | Characteristics of a single-mode optical fibre and cable |
| IEC 60794-4 -10 | Optical fibre cables - Part 4-10: Family specification - Optical ground wires (OPGW) along electrical power lines |
| IEEE 1138 | Construction of composite fibre optic overhead ground wire (OPGW) for use in electric utility power lines |

      - OPGW Characteristics

The minimum requirement for the OPGW shall be:

| Description | Units | Data |
| --- | --- | --- |
| Type | - | OPGW |
| Overall diameter | mm | approx. 17 |
| Mass (dry) | kg/km | approx.680 |
| Ultimate tensile strength | kN | ≥105 |
| Modulus of elasticity | Mapa | ≥96400 |
| DC resistance at 20°C | Ohms/km | ≤0.258 |
| Coefficient of linear thermal expansion | 10-6/°C | ≤17.1 |
| Fault current capacity (20°C - 160°C) | kA2s | ≥200 |
| Lightning Class (IEEE1138) |  | Class 2 |
| Number of fibres | Nos. | 48 |
| Fibre type |  | ITU 652.D |

The OPGW earth conductor shall have the characteristics stated in the Technical Schedules and shall comply as far as possible with the requirements of IEC 60794-4-10 or IEEE 1138.

The fibres shall be Single-Mode type, suitable for operation at wavelengths of both 1310nm and 1550 nm and shall conform to ITU-T Recommendation G.652.D.

The number of fibres to be contained within the optical fibre cable shall be 48 as a minimum.

      - Fabrication

OPGW earth conductor shall consist of at least two layers of aluminium alloy/aluminium-clad steel wires with an optical fibre communication cable enclosed either in one or more stainless steel tubes or in the central aluminium alloy tube.

OPGW shall have a design service life of minimum 30 years and a warranty of at least 5 years.

Precautions shall be taken during manufacture, storage and erection of conductors to prevent the possibility of contamination by copper, iron or other materials that may adversely affect the aluminium or stainless steel.

Aluminium alloy wires shall be aluminium-magnesium-silicon grade in accordance with EN 50183.

Where aluminium-clad steel wires are used they shall be to EN 61232 class 20SA.

All wires, aluminium alloy and aluminium-clad, shall be of uniform circular section, smooth and free from surface imperfections.  Aluminium-clad steel wires shall be pre-formed so that they remain inert when the conductor is cut.  The outer layer shall be right-hand lay.  There shall be no joints in individual wires in a drum length unless specifically approved.

The optical fibres shall be housed in stainless steel tube inside the OPGW earth conductor and shall be protected from water ingress by the application of a waterproof gel, applied between the buffer tubes and the plastic sheath or seamless metallic tube during manufacture.

The OPGW shall be designed to withstand lightning strokes, short-circuit current, ambient and extreme temperatures and loadings as specified in the Technical Schedules with no effect on the attenuation of the optical fibres and no permanent damage to the data transmission characteristics of the fibre optic cable.

The optical fibre cable shall be of the loose tube type, with the fibres contained in a buffer or buffer tubes contained in the central core of the OPGW earth conductor.

The buffer tubes housing the optical fibres shall be coded for ready identification at either end.  Buffer tubes shall be filled with a compound to provide resistance to water penetration, vibration damping and for shock absorption.

Each individual fibre shall be colour coded for identification purposes and details of the colour coding scheme adopted shall be stated in the bid.

The optical fibre cable shall be designed so that the fibres shall be free from longitudinal strain under all conditions of loads and ambient temperatures specified.

The design of the fibre optic cable shall be such that a tension of 65% of the OPGW UTS will not produce strain in the fibres and will not result in an increase in attenuation.

The optical fibres shall be able to withstand temperature cycling in the range –5°C to +80°C without changing the optical values during installation, stocking and transportation.

The OPGW shall be rated to operate at 80°C continuously and at intermittent short-term temperatures up to 200°C without any degradation of performance.

      - Tests

          - Qualification tests

Tests on complete composite fibre optic earth conductor shall be carried out in general accordance with the IEEE 1138/2009 and other referenced standards. A lightning arc test shall be carried out for Class 2 requirements. Any deviation from these methods or any alternative methods proposed must have prior approval.

          - Field routine acceptance tests

The Contractor shall carry out attenuation tests to confirm the satisfactory condition of the optical fibres prior to erection.  These will be compared against the values obtained prior to shipment.

Once installation of the fibre optic cable is complete a series of tests to be agreed with the Employer shall be carried out to ensure the satisfactory operation of the cable.  The tests shall be carried out in both directions.

The tests, using an optical time domain reflectometer (OTDR), shall include but not be limited to:

- Optical attenuation on the terminated cable in both directions carried out at the wavelengths given in Technical Schedules.

- Loss distribution to measure the uniformity of loss in the fibre and joint losses.

- End to end attenuation tests including connectors at terminal stations prior to commissioning.

- Bit Error Rate (BER) test shall be carried out and the error rate shall not exceed 10-9.

On completion of the tests three copies of the test reports shall be supplied to the Employer.

At the end of the guarantee period the optical attenuation of the cable between terminal stations complete with end connectors shall be re-measured and recorded and it shall not be more than 102 per cent of the readings obtained at commissioning.  BER tests shall also be repeated.

          - Sample tests

Samples from 10% of lengths of the finished OPGW shall be taken, the metallic strands subjected to tests stated in relevant EN standard and optical fibres subjected to attenuation and dispersal tests in accordance with IEC.  In the event of a sample from any length not passing these tests a second and third sample shall be taken from the same length and if one of these also fails under test the length from which it has been taken shall be rejected.

          - OPGW Fittings

          - General

All fittings shall be designed in such a way that no degradation of the optical transmission in the fibres of the wire occur for all service conditions.  The optical fibres shall be freely moveable in the wire under service load.

Suspension towers shall be provided with the facility to accommodate suspension and tension clamps and bonds.

          - Tension Clamps

The tension set shall consist of a line guard and preformed dead end which is placed on the line guard.  The line guard shall be laid in the opposite direction to the outer layer on the OPGW and the dead end must be laid in the opposite direction to the line guard.

The length of the line guard shall be sufficient to install vibration dampers.  It shall protect the OPGW against concentrated radial forces in the region of contact between the dead end and the OPGW. All helical rods shall be made of aluminium or aluminium-clad steel.  The tension set shall withstand at least 95% of the OPGW’s rated ultimate strength.

At tension towers the earth conductor clamps shall each be securely bonded to the tower steelwork by means of suitable lengths of multistrand aluminium flexible bond wires having a cross-sectional area adequate to carry a current of 25 kA for not less than one second. The bond shall be terminated with compression lugs.

          - Suspension Clamp

Suspension clamps for optical fibre (OPGW) earth conductors shall be free to pivot in the vertical plane about a horizontal axis passing close to and transverse to the centre line of the conductor.  The conductor shall be mechanically clamped in an approved manner.  Suspension clamps shall permit controlled axial movement of the conductor through the clamp without causing damage to the conductor under unbalanced load conditions.  The tension unbalance at which this slippage can occur shall be approximately 15% of UTS.  Unless otherwise approved, the suspension clamp unit shall be designed such that there is progressive stiffening of the optical fibre conductor up to the suspension clamp, which is a point of maximum bending.  Complete protection of the optical fibres from damaging radial crushing loads under the clamp shall be ensured by the use of a suitable armoured suspension clamps, of either the Armour Grip Suspension (AGS type with Armour Rods and an internal elastomeric clamp liner) or an armoured metallic suspension clamp which is specially designed for the specific size OPGW and incorporates armour rods and positive metallic 'stops' in the suspension clamp body. Suspension clamps for OPGW earth conductors shall be designed for attachment of a required flexible earthing bond that is to be bolted between each suspension clamp and the tower steelwork.

At suspension towers the earth conductor suspension clamp shall be securely bonded to the tower steelwork by means of a multistrand aluminium flexible bond wire having a cross-sectional area adequate to carry a current of 25 kA for not less than one second. The bond shall be terminated with compression lugs and shall not interfere with the suspension clamp movement.

          - Dampers

The optical fibre earth conductor (OPGW) shall be fitted with approved vibration dampers, either Stockbridge type of four response format using 19 strand minimum messenger cable.

The earth conductor vibration dampers shall be designed to:

- introduce an additional damping effect to that of the earth conductor and to control aeolian vibration to ensure that the strain level in the earth conductors at the clamps, both suspension and tension, is below the fatigue limit of the earth conductor strands,

- guarantee that the earth conductor bending strain at suspension and tension clamps shall not exceed the limit of 150 microstrains.

Successful service history of the proposed damping system in environments at least as hostile as that for the present project shall be demonstrated and the efficacy of the proposed system for damping aeolian vibrations shall be demonstrated by calculation, as detailed below.

The metallic material of vibration damper clamp shall be aluminium alloy.  The clamp shall be provided with an adequate clamping surface secured by bolt and with a radius at the clamp mouth to prevent damage to the conductor. Alternative designs of clamping (armour grip) can be considered on evidence of satisfactory service experience.  All screws and nuts shall be of stainless steel and shall be locked in an approved manner.

The number of dampers per span of individual earth conductor shall be as stated in the Technical Schedules.

The approval of vibration dampers shall be conditional on the provision of evidence of satisfactory service life and performance.  Evidence must be provided in respect of fatigue resistance, clamp to conductor grip and damping of aeolian vibration with disposition along the span as recommended by the manufacturers.  Evidence shall be provided of resistance to ozone and the ultraviolet light as well as to aging in the case of spiral vibration dampers.

In order to evaluate the efficiency of the damping system the supplier must have developed suitable computer programmes that have been verified against experimental investigations and behaviour of actual transmission lines, so that he is able to simulate the behaviour of the earth conductor when subjected to wind-excited aeolian vibration.

Based on the type of conductor and its tensile load the supplier shall submit a damping study, with calculations of vibration amplitude and strain on earth conductors with and without vibration dampers.

Stockbridge type vibration dampers shall satisfy the requirements specified in the Tests section of the Technical Specification and in IEC 61897.

          - Joint Boxes and Splices for Optical Fibre

Each joint shall include its joint box and mounting hardware, optical fibre splice kits, entry seals and all accessories required to produce a permanent optical joint.  Details of the proposed optical fibre joints shall be submitted by the Contractor for the approval.

All fibre joints shall be individually mounted within the box.  Optical fibre splices shall be of the fusion type and optical attenuation of each splice shall be less than 0.1dB.

Variations in the quality of workmanship in making the fusion splice shall have a minimal effect on the efficiency and reliability of the joint.

Joint boxes designed to protect all optical fibre joints from the environment shall be provided and located on appropriate joint towers above the anti-climbing devices.  Joint towers may be either tension or suspension towers, the latter being specifically modified to accept the optical termination fittings.  Each joint box shall be capable of being hermetically sealed after jointing and hermetically resealed after reopening and reclosing.

The boxes, which shall be fitted with a bolted and lockable lid, shall be manufactured from stainless steel and shall provide protection to Class IP 66 of IEC 60947-1. Integral earth terminal shall be provided.  The box shall be made weatherproof by the use of corrosion-resistant sealing compound.

Access on the bottom edge of the box shall be by means of weather tight glands sized for the incoming and exiting OPGW earth conductor plus facility for one additional optical fibre cable.

The joint boxes shall provide adequate protection for splices and shall provide storage for sufficient length of fibre. The size of the boxes shall be sufficient to meet the minimum physical storage redundancy of 100% (up to 8 cassettes, 12 fibres each).

The boxes shall be securely clamped to the tower.  Due account shall be taken of the weight and wind area of the joint box and its effect on the design of the towers.

Each box shall be labelled “Keep Off – Danger of Death” in English language.

The OPGW earth conductor shall be supported on and electrically bonded to the structure by means of cleats at 1000 mm centres on vertical members and 600 mm centres on horizontal members.  The cleats shall be designed so that no damage during installation is caused to the galvanized surface of the steelwork.

The location of the boxes shall be 7.0 m above ground level.  To permit the joint box to be moved to the ground for jointing purposes a suitable length of OPGW earth conductor, minimum 20 m, is to be coiled and supported on the structure as specified before entering the joint box.

All required materials for fixing the OPGW earth conductor and for the installation of the joint boxes shall be supplied by the Contractor and the costs for these materials and joint boxes shall be deemed to be included in the cost of the OPGW earth conductor, as shall the costs for carrying out all the necessary jointing and splicing.

          - Marking

The following information shall be clearly marked in indelible paint on both flanges of every conductor drum in English:

- Type of OPGW and code name;

- Size of conductor + number of fibres;

- Exact length in meters;

- Serial number if applicable

- Net weight in kg;

- Gross weight in kg;

- Drum number;

- Manufacturer’s name and country of origin;

- Year of manufacture;

- Purchaser’s order number;

- Shipping destination;

- Rotation arrow

          - Packing

Packing and crating methods are the responsibility of the Contractor.

The conductor shall be shipped in matched sets of eight in nominal standard lengths on non-returnable wooden or steel reels.  The reels shall be designed for normal tension stringing operations.

The drums of the conductor reels shall be wrapped with a moisture resistant protective covering.  The inner flanges of the reels shall be lined with moisture resistant solid fibreboard.

The two outer layers of conductor shall be interleaved, and the outer layer covered with moisture resistant paper.  A protective covering of a single layer of moisture resistant solid fibreboard, secured with steel banding, shall be wrapped overall. The reels shall be so constructed to withstand normal loads due to tension stringing operations and they shall be sufficiently sturdy to withstand the additional handling inherent to ocean shipment.

The reels shall be wood lagged, the lagging to be secured with two steel bands.  The steel bands shall be intermittently stapled to the lagging. The Contractor shall submit drawings of reels for approval.

Hardware and fittings shall be packed in sturdy wooden cases suitable for both ocean and inland transportation and shall be clearly marked with the following information:

- Description of the items;

- Number of pieces;

- Net weight and gross weight;

- Manufacturer’s name and country of origin;

- Year of manufacture;

- Purchaser’s order number;

- Shipping destination;

          - Submittals

Submittals required with tender include:

- The Technical Data Schedules for conductor offered;

- Installation methods and materials.

- Jointing methods, materials and mounting arrangements.

- Physical protection against the ingress and transmission of moisture.

- Identification marking and fibre coding.

- The manufacturer's quality assurance program and/or manual together with a list of international/national standard specifications covering raw materials, components, processes, tolerances, test procedures, etc. and a list of tests normally carried out on raw materials and a description of test equipment used;

- A full list of routine and sample tests carried out during and after manufacture and a description of the test equipment used;

- A full list of all type tests performed and all relevant data confirming results;

- Detailed drawings of each type of drum that will be used for packing

Submittals required following award of the contract:

- Details of manufacturing, test and shipping schedules and transportation/delivery proposals;

- Certificates covering raw materials used in the manufacture of conductors;

- Certificates covering routine tests carried out on wires before stranding of conductors;

- Certificates covering the sample tests carried out on wires after stranding and type tests on complete conductor before shipping of conductors;

- Curves of creep versus load and time;

- OPGW short-circuits temperature curves giving current versus time.

- A list giving per drum, the drum number, the size of conductor, the exact length, the net weight, the gross weight, the number of any joints made during stranding and their distance from the out end;

    - SUPPORTS AND FOUNDATIONS

      - Foundations, excavations and backfilling

The detail design of support foundations, where applicable, shall be submitted to the Project Manager together with load calculations. It is the contractor's responsibility to do soil tests in order to establish load bearing and chemical properties of the soil along the route.

All pole and stay excavations shall be 1 metre wide, 1.5-metre-long and for stays only have a depth of 1.5m: other dimensions shall correspond to the specified pole planting depth.

If the ground structure does not permit deep excavation due to hard rock, a concrete foundation of one cubic meter and minimum depth of 750mm shall be provided or rock drills shall be used whichever method is approved.

Backfilling shall be carried out so that the material is properly consolidated in layers of uncompacted thickness not exceeding 150mm. Each layer shall be thoroughly compacted before the placement of the next layer

In sandy, other loose soil or marshy ground, cement or concrete shall be used for consolidation and strength increases. No casting of concrete will be allowed in wet soil.

All remaining material excavated, and not used for backfilling, shall be removed from site.

Blasting shall not be permitted without the consent of the employer. It is envisaged that it would rarely be used in special occasions.

All steel work below ground shall be galvanised. Steel work cast into concrete shall be securely keyed.

The finish on foundations shall be smooth and neat, sloped to the outside to ensure that no water shall assemble on top of foundations.

          - Form of construction

Supports shall be of single wood pole construction “H’ pole configuration, at angle, and terminal positions shall normally be stayed.

The supports shall be designed to carry the line conductors with the necessary insulator sets, shieldwire, stays and all ancillaries and fittings under the conditions specified.

The line conductors of each circuit shall be arranged in delta formation with one over-running shieldwire per circuit.

The method of attachment of the shieldwire to the poles shall be by means of clamps at intermediate poles and by means of tension compression fittings at section, angle and terminal poles.

At specified positions the supports shall be designed to carry, in an approved manner, additional equipment such as cables and their terminations, isolators, fuses, earth switch, surge arrester or other accessories as may be required.

Cross arms shall be of steel and comply with BS 4360 IEC 1773, IEC 652, IEC 826 or other approved standards.

The Contractor shall develop detailed drawings based on design to be carried out.

          - Type of Structure

The structure nomenclature shall normally be defined by the pole top steelwork which shall be the following standard types.

| Type | Position of Use | Angle of Deviation | Type of Insulators |
| --- | --- | --- | --- |
| A | Intermediate, straight line | 0o - 2 o | Suspension |
| B | Light angle/Section | 0 o - 30 o | Tension |
| C | Medium angle | 30 o - 60o | Tension |
| D | Heavy angle | 60 o - 90o | Tension |
| E | Terminal (Single circuit) | 0 o | Tension |

All structure types with overhead line to cable interfaces shall be equipped with surge diverts.

          - Use of Standard Supports

The standard type of structures shall be designed for use as specified in the following clause on span lengths.  Where a transmission line route makes any deviations not exceeding 2 o, a support with suspension insulators shall normally be used.

Where the distribution line route makes a deviation in excess of 15 o, a support with tension insulators shall normally be used.

          - Conductor Spacing and Clearances

The spacing between individual conductors, phases and the clearance between the clamps, arcing horns, jumpers, loops or other live metal and the support steelwork under all specified conditions shall be not less than the figures stated in 3.19 above

The specified clearance between line conductors and support steelwork shall be obtained on the assumption that the conductor may leave the support point at any angle to the horizontal between 15 upwards and 15 downwards for tension supports where uplift is encountered, all angles measured in the plane containing the conductor.

The shieldwire shall be located to provide a minimum shielding angle to the phase conductors of 30 at the structure.  In addition the shieldwire shall be erected so its sag is 20 per cent less than that of the conductor at everyday temperature, still air.

          - Support and Stay Foundation Design

The foundations shall normally be of the simple earth type employing kicking blocks or foundations bulks as necessary.

In excavating foundations for supports with foundation bulks and for stay and anchor bulks the holes shall be undercut so that the bulks have solid and undisturbed earth on their principal bearing surface wherever possible.

The supports shall be placed in the ground to the planting depths noted in BS 1990 or as dictated by foundation design, but not less than the following:

| Supports | Planting Depth |
| --- | --- |
| up to 10 metres long | 1.6 metres. |
| from 11 and to 14 metres long - | 2 metres. |
| 15 metres and above - | 2.1 metres |
| Stay bulks shall be set at | not less than 2.0 metres below the ground surface. |

All foundation shall be designed to withstand uplift, settlement, overturning and sliding when subjected to the specified conditions of loading.  Allowance shall be made in foundation design for hydrostatic pressure, effects of seasonal rain, drying out, cyclic loading and wind induced vibration.  The Contractor will be required to confirm the foundation design parameters by undertaking a representative sample of soil investigations.

          - Cross arms

Cross-arms shall be of steel angle or channel. Steel cross-arms shall be manufactured from hot dip galvanised standard steel, thickness of zinc plating shall be 60-70 /um

Cross-arms shall be Loop tension banded at both ends.

Tie straps shall be manufactured of mild steel to SABS 221 or Grade 43 of BS 4360.

Gross-arms shall be long enough to accommodate the insulator spacing specified.

Cross-arms and tie straps shall be bolted to poles using galvanised bolts, nuts and washers.  Curved wood pole washers shall be fitted between bolt heads and the poles and between cross-arms and the poles.  Back-straps and U-bolts may be used to attach wooden cross-arms to the poles.

Cured wood poles washers shall be galvanised malleable cast iron or mild steel with a minimum thickness of 6 mm and shall have a minimum square outside dimension of 63mm.

Steelwork on wooden poles shall generally not be earthed except at structures for transformers, isolators, fuse-links, cable boxes, surge arresters or other equipment which impress the impulse flashover value of the insulation provided by the wooden structure.

All metalwork to be earthed, shall be bonded together with 16mm2 bare copper conductors.  These common bonds shall be connected to a 35mm2 bare stranded or solid copper earth down lead conductor.

The connection between the overhead conductors and surge arresters and between the arresters and the earth down lead shall consists of bare copper conductors of not less than 25 mm2.  The connecting leads shall have smooth bends and shall follow the shortest possible route.

The earth down lead conductor shall be stapled to the pole at intervals not exceeding 1m.  Where atmospheric conditions are likely to cause galvanic action, staples shall be of non-ferrous metal and an earth clip used where possible.

The earth conductor shall not be installed in steel conduit, nor shall the conductor be wrapped around the pole at any point since this will increase the reactance of the down lead.

A trench earth shall be installed at earthed structures carrying equipment such as transformers, fuse-links, surge arresters, etc.  extending 10 m on four sides of the structure in the form of a cross.  The ends of the earth wires shall be bonded to four earth electrodes of at least 1.8 m in length driven into the ground.

The earth resistance shall be determined following the installation of the earth.  Earth resistance values specified or required by protective devices shall be checked.  The earth resistance values required to maintain the B.I.L. of the line as specified (assuming an average lightning current value for 25kA), are as follows:

| Line voltage (kV) | Impulse Level (kV) | Earth Resistance (ohm) |
| --- | --- | --- |
| 11 | 95 | 10 |
| 33 | 170 | 10 |

    - WOOD POLE SUPPORTS

          - Wood Pole Supports

Wood Pole supports shall comply with BS 1990 “medium” or another approved standard.

The poles shall be European redwood, pine, fir, spruce, cedar, larch or other approved timber, straight, sound, hard grown, free from large or dead knots or other defects, and shall have the outer and under bark completely removed.  Trees grown in Northern Europe shall have been felled not earlier than 1 November and not later than 1 March, and all trees shall have been felled when the sap is down. Zambian, Tanzanian and South African pine may be applied. Straight impregnated African eucalyptus poles are acceptable.

All poles, foundation bulks and other wooden members shall be properly seasoned, and they shall be submitted to preservation treatment either by pressure creosoting in accordance with BS 144 or by organic solvent or water-borne types of preservatives in accordance with BS 1282 or other approved standards.  As a minimum the poles shall be pressure creosoted to a minimum net retention of 115kg creosote oil per cubic metre of wood according to BS 1990: part 1.

The poles will be inspected, and if satisfactory, branded by the Project Manager at the pole yard, before any work is done on them.

Each pole shall retain the natural butt of the tree and no timber shall be cut from this other than that necessary to accommodate the foundation bulks and to give the butt a flat surface.

All poles shall be notched and drilled to templates, which shall be provided by the Contractor, for the reception of crossarms and other fittings to ensure tight and true fitting.

Unless otherwise specified poles shall be marked at a distance of 3 metres from the butt end to indicate classification of pole, pole length in metres, date impregnated (last two figures of year), and species code letter as agreed.

          - Table of WOOD POLES sizes

Suitable pole sizes applicable for general use are tabled below. However, special design situations may warrant the purchase of poles greater in length and size than those tabled. Under these circumstances the appropriate pole length, class and diameter will be determined by the size and type of conductor used in the construction along with its designed ultimate tension and line profile details. The most suitable pole will be selected from the appropriate pole tables.

| Pole Length in Meters | Classification | Top Dia in mm min -max | Min Dia 1.5m from the Butt mm | System usage |
| --- | --- | --- | --- | --- |
| 7 | Light | 125-150 | 200 | LV & MV |
| 7 | Medium | 140-170 | 200 | LV & MV |
| 9 | Light | 125-150 | 180 | LV & MV |
| 9 | Medium | 150-180 | 220 | MV & 11kV |
| 9 | Stout | 190-240 | 275 | 11kV & 33kV |
| 10 | Light | 125-160 | 185 | LV & MV |
| 10 | Medium | 150-180 | 230 | MV & 11kV |
| 10 | Stout | 190-245 | 285 | 11kV & 33kV |
| 11 | Light | 125-160 | 195 | LV & MV |
| 11 | Medium | 150-190 | 240 | MV.Dual. & 11kV |
| 11 | Stout | 190-250 | 295 | 11kV & 33kV |
| 12 | Light | 125-165 | 200 | LV & MV |
| 12 | Medium | 150-190 | 250 | MV & 11kV |
| 12 | Stout | 190-250 | 305 | 11kV & 33kV |
| 14 | Medium | 160-205 | 260 | MV & 11kV |
| 14 | Stout | 195-255 | 335 | 11kV,33kV |
| 16 | Medium | 170-215 | 305 | 11kV |
| 16 | Stout | 200-265 | 365 | 11kV,33kV. |

          - Poles

Wooden poles shall be to BS1990 /SABS 753. The poles shall have minimum top diameters of 150mm for 9m poles and 11m poles used for overhead line construction. Poles for transformer substations shall have a minimum length of 11m, and minimum top diameters of 190mm.

Poles 9m long shall be subjected to a fibre stress of 55 MPa when a cantilever loading of 5.93 kN is applied; when the cantilever loading of a 11 m pole is 7.05 kN, the stress shall be 55 MPa.

Poles for transformer substations shall be at least 11m long, with a planting depth of at least 1.8m.

Poles for MV conductors may be 9 m, 10 m or 11 m long. MV dual construction poles shall be 11m long and shall be buried 18m into the ground.

Preservatives of the poles shall comply with the requirements for BS144, BS4072 or type A1 of SABS 590 and the impregnation shall be carried out using the empty-cell pressure process.

Poles shall be Loop tension banded at both ends.

    - OVERHEAD LINE INSULATORS

          - General

Pin, post and reel type insulators shall be brown glazed porcelain and shall generally comply with the requirements of the following publications:

33kV Line Post 		IEC 273

33kV Tension Unit 	IEC 305, IEC 120, IEC 372-1

33kV Pin 		BS 137

Tension insulators shall be either of strings of toughened glass or porcelain disc insulators or comprise epoxy resin long rod type units.  The design of insulators and fittings shall be such as to avoid local corona formation and no significant radio interference shall be exhibited.  The insulator units and the complete insulator sets shall conform to the electrical and mechanical design criteria given in “General Technical Requirements”.

In addition to the above requirements a proportion of disc and pin insulators shall be the vandal proof type of either silicon or EPDM rubber construction as specified in the Technical Schedules.

          - Pin insulators

Pin type insulators for use on 33 kV shall have as a minimum the electrical characteristics required in Technical Schedules, and they shall be fitted with galvanised mild steel spindles having a minimum failing load of 10kN.  The threaded portion of all insulator spindles shall fit a nominal 27.5 mm hole.

Spindles for pilot insulators shall have a minimum failing load of 700N.  Conductor sizes to be accommodated shall vary from 6.0 mm to 19.0 mm diameter with preformed distribution ties.

All pin insulators shall comply with the requirements of anti-fog type insulators.

          - Tension insulators

Tension insulator sets shall be either made up of strings of toughened glass disc insulators of 254 mm diameter and fixing centres at 140 mm of 16 mm ball and socket couplings or of epoxy resin long rod type insulators of equivalent electrical and mechanical performance.

All disc insulators or their equivalents shall comply with the requirements of anti-fog type units and shall have a minimum failing load of 80 kN.

The tension strings shall generally be 10-15 % longer than suspension strings. If cap and pin insulators of the same size are used, their number should be 1-3 greater. The testing shall be performed according to IEC 383.

    - STAYS

          - Stays

Stays shall comprise stranded galvanized steel stay wire and shall conform to the requirements of BS 183 where applicable or other approved standard and be tested in accordance with BS 215 in so far as it applies to steel wires.  The steel guy wires shall be performed so that they remain inert and do not move relative to each other when the guy is cut.  The individual stay wire shall have a breaking stress not less than Grade 1000 equivalent.

The provisions of the Specification in relation to conductor drums shall also apply to stranded stay wire.  The attachment of the stays to the supports shall be made in an approved manner.

All stays shall be equipped with stay insulators. The stay insulators shall be positioned so that they are lower in elevation than any bare live metal on the support.

The angle between the stays and pole shall not be less than 30o or more than 45o.

Stay rods, stay blocks and stay foundations shall be of approved dimensions and types.  Stay rods shall be fabricated in galvanised steel to the requirements of BS 4360 where applicable or another approved standard.

    - ALL DIELECTRIC SELF SUPPORTING (ADSS) CABLE

All Dielectric Self Supporting (ADSS) cables will be used for access to connect Malole Substation to Mungwi town substation. ADSS will be implemented on 33 kV power distribution networks. The optical fibre shall be standard single mode fibre, G.652D.

        - Optical Requirements

Table: Standard Single Mode Fibre (G.652D)

| ATTRIBUTE | VALUE |
| --- | --- |
| Number of Fibres | 12 |
| Type of propagation mode | Standard single mode (ITU-T G.652D) |
| Coating diameter | > 200 m |
| Coating concentricity error | < 10 m |
| Cladding non-circularity | ≤ 1.0 % |
| Cladding diameter | 125 m +/- 1.0 m |
| Mode field diameter @1550 nm | 10.50 m ±1.0 µm |
| Mode field concentricity error | ≤0.5 µm |
| Finished Cable Attenuation Coefficient | ≤ 0.22 dB/km @1550 nm |
| Chromatic Dispersion Coefficient | ≤ 3.5 ps/(nm.km) @1228-1399 nm ≤ 18 ps/(nm.km) @1550 nm |
| Polarization Mode Dispersion (PMD) | ≤ 0.1 ps/√ km |
| Cut-off Wave Length | 1100-1280 nm (measured on 2 m fibre) ≤1270 nm (measured on 22 m fibre) |
| Maximum Splice Loss | 0.03 dB |

        - Mechanical Requirements for ADSS

The ADSS cable shall conform to IEEE P1222 and IEC 60794-1. The ADSS cable shall house the optical fibres that shall be twenty-four (24) in number. ADSS shall be resilient to the effects of the following:

- Fire

- Moisture ingress

- Mechanical forces:

- crushing

- bending

- twisting

- tensile stress/strain

- Aeolian vibrations and galloping

- Electrical tracking

- Birds

- Ultraviolet

- Adverse tropical weather

- Pollution

Sectioning of the ADSS cable and splicing of the optical fibres shall generally be arranged on dead-end structures (Poles/Towers) but where necessary this may be carried out on other structures providing that such structures are capable of withstanding additional stringing loads. No mid-span joints shall be allowed in the ADSS.

        - Optical Fibre Joints

  - Description of Work

- Dismantling of the fibre cable ends

- Fusion splicing at the ground

- Testing and printing out every approved splice

- Installation of joint boxes on the tower legs

- Winding up the joint ends and mounting them into the boxes. Cable organizers (Trays) shall be used on towers to neatly harness secure the and  fastening the ADSS to the tower leg

- Laying and splicing of optical fibre cable from the ADSS on the substation gantry to the telecommunication room

- Installation of optical fibre termination cubicles complete with optical patch panels in the telecommunications rooms.

  - Requirements

- The splice boxes shall withstand the environmental requirements.

- All splice boxes shall be covered by a metal white shield for sun and shot protection

- All splices shall be documented on PC file and print out including attenuation and monitor picture

- Splice attenuation shall be better than 0.04 dB

- Splice protection sleeves shall be provided

        - Splicing

The Contractor shall ensure the ADSS is properly spliced as required. Carry out tests during installation to ensure the quality of the splices is adequate as specified herein, and continuity of the fibres is ensured. Contractor shall obtain his own equipment for splicing fibre optic cable and carrying out tests.

        - ADSS Fittings And Installation

The Contractor shall present a stringing methodology for the ADSS cable. The Contractor shall also design and furnish all associated ADSS hardware and accessories required for a complete operational ADSS system.

All joints in optical fibre shall be arc fusion welded and each complete splice shall be housed in a protective, weatherproof splice box mounted on the tower leg or pole. The joint boxes shall have the capacity for up to minimum 48 single fibre splices and shall store excess fibre for at least 1 re-splicing.

The Contractor shall carry out the installation of the ADSS and the fittings. The contractor shall also supply and install the optical fibre approach cable from the Gantry/Terminal tower to the equipment rooms.

        - DUCT FIBRE / UNDERGROUND FIBRE

        - General

This type of fibre will be installed at substations to link ADSS from the substation gantries to the equipment rooms. The fibre that will be required in these circumstances is underground fibre that will be buried. These fibres will be buried in High Density Polyethylene (HDPE) pipes.

        - Optical Requirements

The optical characteristics for the buried and duct fibres shall be the same as for ADSS and shall be standard single mode fibre conforming to ITU-T G.652.

  - Technical Schedules

    - Preamble

The Bidder shall examine the specifications of this section in close connection with the other sections of this Bid Document. Special attention shall be paid to General Specification and Particular Technical Specifications and the Drawings.

If the Specifications and/or Drawings do not contain particulars of materials or works which are necessary for the proper and safe completion, operation and maintenance of the equipment in question, all such materials and works shall be deemed to be included in the supply for the turn-key based solution requested here-in.

In the event of any difference between the Drawings and the Specifications, the former shall prevail.

Should the Bidder find discrepancies in or omissions from these Specifications or from the other Documents, or should he be in doubt as to their meaning, he should immediately contact the Employer for interpretation, clarification, or correction thereof before submitting his Bid. Such action shall, however, in no case be considered as a cause for altering the closing date of the Bid.

    - Technical Schedule List

IMPORTANT!

The following technical schedules must be filled in by Bidders and submitted with the bid without fail. Failure to do so may lead to bid being considered as non-responsive.

Successful Tenderer shall be required to provide previous type test certificate and or results and Quality Assurance Certificate at contract award stage.

      - TECHNICAL SCHEDULE FOR 33kV ZINC OXIDE SURGE ARRESTOR

| S/N | TECHNICAL DETAILS | UNITS | REQUIREMENTS | TENDERER’S GUARANTEE |
| --- | --- | --- | --- | --- |
| 1 | Type of Surge arrestor |  | Zinc oxide 33kV surge arrestor, |  |
| 2 | Nominal system voltage | kV | 33 |  |
| 3 | Highest system voltage | kV | 36 |  |
| 4 | Basic Insulation Level (BIL) | kV | 170 |  |
| 5 | Type of system earthing |  | Solid |  |
|  | #### Ratings and type of surge arrester |  |  |  |
| 6 | Specification to which surge arrester complies |  | IEC 60099-4:1991 |  |
| 7 | Rated voltage of surge arrester | kV | 36 |  |
| 8 | Nominal, 8/20 µs, discharge current rating of surge arrester | kA | 10 |  |
| 9 | Maximum continuous operating voltage of surge arrester (MCOV) | kV | 29 |  |
| 10 | Gapless or gapped type metal-oxide surge arrester |  | Gapless |  |
| 11 | Rated frequency of surge arrester | Hz | 50 |  |
| 12 | Insulation material |  | Silicon Rubber |  |
| 13 | Design altitude of surge arrester (above sea level) | m | 1 500 m |  |
| 14 | Design ambient temperature of surge arrester | oC | -1 to 40 |  |
| 15 | Phase-to-ground Specific creepage of surge arrester | mm/kV | 31 |  |
| 16 | Corrosion protection of metal and alloy parts: galvanizing specification and/or stainless steel grade |  | SABS 763 |  |
|  | Test |  |  |  |
| 17 | Minimum one minute wet power frequency withstand voltage of external insulation of surge arrester housing | kV | 70 |  |
| 18 | Maximum steep current impulse residual voltage for a 10 kA, 1/20 µs, discharge current | kV | 99.7 |  |
| 19 | Maximum lightning impulse residual voltage for a 10 kA, 8/20 µs, discharge current | kV | 91.8 |  |
| 20 | Lightning, 1,2/50 µs, impulse withstand level of external insulation of surge arrester housing |  | 80 |  |
| 21 | Line discharge class rating |  | 1 |  |
| 22 | Long duration current, 2 000 µs, impulse withstand | A | 250 A |  |
| 23 | High current, 4/10 µs, impulse withstand | kA | 100 kA |  |
| 24 | Type test |  | Supplier to provide previous type test certificate/results together with the bid |  |
| 25 | Routine tests |  | Supplier to provide drawings showing dimensions with the bid |  |
| 26 | Drawings |  | Supplier to provide routine test certificate/results on delivery |  |
| 27 | Quality Assurance |  | Supplier to provide Quality Assurance certificate with the bid |  |
| 28 | Technical details/brochure |  | Bidders to provide complete technical details/brochure with the bid |  |
| 29 | Galvanised steel supports complete with bolts |  | To be provided by the supplier |  |

      - TECHNICAL SCHEDULE FOR ACSR CONDUCTOR

| S/N | DETAIL | UNIT | REQUIREMENTS | TENDERER’S GUARANTEE |
| --- | --- | --- | --- | --- |
| 1 | Description |  | 350 mm2 stranded aluminium conductor steel reinforced (ACSR) |  |
| 2 | Cross section area- aluminium | mm2 | 381.7 |  |
| 3 | Cross section area- steel | mm2 | 49.5 |  |
| 4 | Total cross section area | mm2 | 431.2 |  |
| 5 | Mass | kg/km | 1444 |  |
| 6 | Code name |  | Bison |  |
| 7 | Designation as per IEC61089 |  | A1/S2B |  |
| 8 | Material of conductor |  | Hard-drawn Aluminium with galvanized steel core reinforcement |  |
| 9 | Stranding and wire diameter |  |  |  |
| 10 | Aluminium | No/mm | 54/3 |  |
| 11 | Steel | No/mm | 7/3 |  |
| 12 | Overall diameter | mm | 27 |  |
| 13 | Ultimate tensile strength | kN | 120.90 |  |
| 14 | Final modulus of elasticity | MPa | 68650 |  |
| 15 | Coefficient of linear thermal expansion | 10-6/°C | 19.3 |  |
| 16 | DC Resistance @ 20 oC | Ohms/km | 0.07573 |  |
| 17 | Operating ambient temperature | 0C | -1 to 40 |  |
| 18 | Maximum humidity | % | 85 |  |
| 19 | Altitude above sea level | m | 1400 |  |
| 20 | Drums |  | Treated wooden drums |  |
| 21 | Length per drum | m | 2000 |  |
| 22 | Applicable standard |  | IEC 61089, BS 215 parts 1 & 2 |  |
| 23 | Previous Type Test certificate to be provided with bid | Yes/No | Yes |  |
| 24 | Sample Test and Routine Test certificates to be provided on delivery | Yes/No | Yes |  |
| 25 | Quality Assurance certificate to be provide with bid | Yes/No | Yes |  |

      - TECHNICAL SCHEDULE FOR OPGW CONDUCTOR

| Item | Description | Units | Required | Guaranteed |
| --- | --- | --- | --- | --- |
| CABLE |  |  |  |  |
| 1 | Manufacturer |  |  |  |
| 2 | Country of origin |  |  |  |
| 3 | Characteristics |  |  |  |
| 3.1 | Type of OPGW |  |  |  |
| 3.2 | Number of layers |  | Min.2 |  |
| 3.3 | Material of outer layer wires |  | AA |  |
| 3.4 | No. of Fibres |  | 48 |  |
| 3.5 | Diameter | mm | approx..17 |  |
| 3.6 | Maximum D.C. resistance at 20o C | Ohms/km | 0.258 |  |
| 3.7 | Rated breaking strength | kN | ≥105 |  |
| 3.8 | Unit weight | Kg/km | approx..682 |  |
| 3.9 | Modulus of Elasticity | MPa | ≥96400 |  |
| 3.10 | Coefficient of Expansion | 10-6/°C | ≤17.1 |  |
| 3.11 | Short-Circuit Current (for 0.5s) | kA | ≥20 |  |
| 3.12 | Lightning Class acc. IEEE1138 |  | 2 |  |
| 3.13 | Min. Bending Radius | mm |  |  |
| OPTICAL FIBRE |  |  |  |  |
| 4 | Manufacturer |  |  |  |
| 5 | Country of origin |  |  |  |
| 6 | Type |  |  |  |
| 7 | Characteristics |  |  |  |
| 7.1 | Classification of fibre |  | ITU-T G.652D |  |
| 7.2 | Core Concentricity Error | µm | 0.6 |  |
| 7.3 | Cladding Diameter | µm | 125 |  |
| 7.4 | Tolerance | µm | ± 0.7 |  |
| 7.5 | Operating wavelength | nm | 1310/1550 |  |
| 7.6 | Fibre Material |  | acrylic |  |
| 7.7 | Fibre attenuation coefficient at 1310 mm | dB/km | ≤ 0.36 |  |
| 7.8 | Fibre attenuation coefficient at 1550 mm | dB/km | ≤ 0.24 |  |
| 7.9 | Fibre attenuation coefficient at 1625 mm | dB/km | ≤ 0.26 |  |
| 7.10 | Fibre Bandwidth (normalized for 1 km) |  |  |  |
| 7.11 | Fibre Dispersion at 1550 mm | ps/nm.km | ≤ 18 |  |
| 7.12 | Fibre Dispersion at 1625 mm | ps/nm.km | ≥ 22 |  |
| OPGW JOINT BOX |  |  |  |  |
| 8 | Manufacturer |  |  |  |
| 9 | Country of origin |  |  |  |
| 10 | Joint box material |  | INOX |  |
| 11 | Characteristics |  |  |  |
| 11.1 | Number of cassettes |  | Min. 4 |  |
| 11.2 | Number of inlet glands (available) |  | Min.3 |  |

      - TECHNICAL SCHEDULE FOR 33KV ISOLATOR

| S/N | TECHNICAL DETAIL | UNITS | REQUIREMENT | TENDERER’S GUARANTEE |
| --- | --- | --- | --- | --- |
|  | Type |  | Side break |  |
|  | Rated Voltage | kV | 33/36 |  |
|  | Rated Current | A | 1250 |  |
|  | Number of Phases |  | 3 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Operation |  | Hand operated |  |
|  | Lightning impulse withstand (Dry) | kV peak | 170 |  |
|  | Power Frequency withstand (1 min) | kV rms | 70 |  |
|  | Rated short time withstand (3s) | kA | 31.5 |  |
|  | Creepage | mm/kV | 31 |  |
|  | TYPE TEST |  | Supplier shall provide previous type test certificate/results together with the bid |  |
|  | DRAWINGS |  | Supplier shall provide drawings showing dimensions |  |
|  | QUALITY ASSURANCE |  | Supplier shall provide Quality Assurance certificate with the bid |  |

      - TECHNICAL SCHEDULE FOR TENSION INSULATORS

| No. | Particulars | Unit | ZESCO Minimum specs | Bidder To Fill In |
| --- | --- | --- | --- | --- |
|  |  |  | BISON | BISON |
|  | INSULATOR UNITS |  |  |  |
| 1 | Type and IEC designation |  |  |  |
| 2 | Maker's name |  |  |  |
| 3 | Standard to which complied |  | IEC 61109 |  |
| 4 | (a) Material from which insulator sheds are manufactured |  | Silicone |  |
|  | (b) Material from which insulator rod is manufactured |  | ECR Boron free glass |  |
| 5 | Weight of insulator | Kg |  |  |
| 6 | Number of sheds per insulator |  | 8 |  |
| 7 | Dry arc distance, minimum | mm | 400 |  |
|  | INSULATOR SET COMPLETE |  |  |  |
| 8 | Number of Strings per phase | No. | 1 |  |
| 9 | Length of complete, without fittings | mm |  |  |
|  | Length of complete, including fittings | mm |  |  |
| 10 | Weight of insulator set | kg |  |  |
| 11 | Breaking strength of complete set | kN | 90 |  |
| 12 | Overall creepage distance per string | mm | 900 |  |
| 13 | Power frequency (50Hz) withstand voltage | kV |  |  |
| 13.1 | Dry, one minute | kVrms | 110 |  |
| 13.2 | Wet, one minute | kVrms | 95 |  |
| 14 | Dry lightning impulse withstand voltage |  |  |  |
| 14.1 | 1.2/50 Positive wave | kVp | 170 |  |
| 14.2 | 1.2/50 Negative wave | kVp | 185 |  |
| 15 | Physical Particulars |  |  |  |
|  | (a) Rod diameter | mm | 20 |  |
|  | (b) Whether coupling, interchangeable with IEC Publication No. 120, 20 mm, or 16 mm nominal shank diameter, as applicable | - |  |  |
|  | (c) Colour |  | Grey |  |
|  | (d) Material of housing including sheds |  | Resistant ECR |  |
|  | (e) Material of core |  | FRP Rod |  |
|  | (f) Material of socket type cap |  | Galvanized steel |  |
|  | (g) Material of ball type in. |  | Galvanized steel |  |
|  | (h) Whether galvanised or not |  | YES |  |
|  | (i) method of attachment of (f) and (g) to fibre rod |  | Crimping |  |
|  | (j) Method of sealing |  | Labyrinth |  |
|  | (k)Thickness of single shed | mm | 4 |  |
| 16 | Recommended maximum sustained load | kN | 90 |  |
| 17 | Mechanical Strength |  |  |  |
|  | (a) Breaking strength | kN | 90 |  |
|  | (b) Electromechanical strength | kN | 80 |  |
| 18 | Whether complete drawings of insulator assemblies are submitted with bid |  | YES |  |
| 19 | Whether the insulator are complete in every respect |  | YES |  |

      - TECHNICAL SCHEDULE FOR SUSPENSION INSULATORS

| No. | Particulars | Unit | ZESCO Minimum specs | Bidder To Fill In |
| --- | --- | --- | --- | --- |
|  |  |  | BISON | BISON |
|  | INSULATOR UNITS |  |  |  |
| 1 | Type and IEC designation |  |  |  |
| 2 | Maker's name |  |  |  |
| 3 | Standard to which complied |  | IEC 61109 |  |
| 4 | (a) Material from which insulator sheds are manufactured |  | Silicone |  |
|  | (b) Material from which insulator rod is manufactured |  | ECR Boron free glass |  |
| 5 | Weight of insulator | Kg |  |  |
| 6 | Number of sheds per insulator |  | 13 |  |
| 7 | Dry arc distance, minimum | mm | 300 |  |
|  | INSULATOR SET COMPLETE |  |  |  |
| 8 | Number of Strings per phase | No. | 1 |  |
| 9 | Length of complete, without fittings | mm |  |  |
|  | Length of complete, including fittings | mm |  |  |
| 10 | Weight of insulator set | kg |  |  |
| 11 | Breaking strength of complete set | kN | 70 |  |
| 12 | Overall creepage distance per string | mm | 900 |  |
| 13 | Power frequency (50Hz) withstand voltage | kV |  |  |
| 13.1 | Dry, one minute | kVrms | 110 |  |
| 13.2 | Wet, one minute | kVrms | 95 |  |
| 14 | Dry lightning impulse withstand voltage |  |  |  |
| 14.1 | 1.2/50 Positive wave | kVp | 170 |  |
| 14.2 | 1.2/50 Negative wave | kVp | 185 |  |
| 15 | Physical Particulars |  |  |  |
|  | (a) Rod diameter | mm | 20 |  |
|  | (b) Whether coupling, interchangeable with IEC Publication No. 120, 20 mm, or 16 mm nominal shank diameter, as applicable | - |  |  |
|  | (c) Colour |  | Grey |  |
|  | (d) Material of housing including sheds |  | Resistant ECR |  |
|  | (e) Material of core |  | FRP Rod |  |
|  | (f) Material of socket type cap |  | Galvanized steel |  |
|  | (g) Material of ball type in. |  | Galvanized steel |  |
|  | (h) Whether galvanised or not |  | YES |  |
|  | (i) method of attachment of (f) and (g) to fibre rod |  | Crimping |  |
|  | (j) Method of sealing |  | Labyrinth |  |
|  | (k)Thickness of single shed | mm | 4 |  |
| 16 | Recommended maximum sustained load | kN | 70 |  |
| 17 | Mechanical Strength |  |  |  |
|  | (a) Breaking strength | kN | 70 |  |
|  | (b) Electromechanical strength | kN | 60 |  |
| 18 | Whether complete drawings of insulator assemblies are submitted with bid |  | YES |  |
| 19 | Whether the insulator are complete in every respect |  | YES |  |

      - TECHNICAL SCHEDULE FOR WOODEN POLE 14 METRES LONG MIN. TOP DIAMETER

| S/N | DESCRIPTION |  |  | UNIT | REQUIREMENT | TENDERER’S GUARANTEE |
| --- | --- | --- | --- | --- | --- | --- |
|  | Type |  |  |  | Flat top cut 14m eucalyptus pole |  |
|  | pole length |  |  | m | 14 |  |
|  | Minimum top diameter |  |  | mm | 180 - 200 |  |
|  | Poles shall be strength tested for a fibre stress of 55Mpa and/or 75Mpa |  |  |  |  |  |
|  | For poles strength tested for a fibre stress of 55Mpa | Force required to cause a fibre stress of 55 MPa | Cantilever loading | KN | 6.46 |  |
|  |  |  | Midpoint loading | KN | 16.02 |  |
|  | For poles strength tested for a fibre stress of 75Mpa | Force required to cause a fibre stress of 75 MPa | Cantilever loading | KN | 8.81 |  |
|  |  |  | Midpoint loading | KN | 21.84 |  |
|  | Average moisture content of poles at the time of treatment shall not exceed 250 g/kg but no individual pole, shall have a moisture content that exceeds 280 g/kg |  |  | Yes/No | Yes |  |
|  | Preservative |  |  |  | Creosote |  |
|  | Minimum retention of creosote per batch |  |  | kg/m3 | 115 |  |
|  | Nail plate |  |  |  | Zinc coated steel |  |
|  | Hazard class |  |  |  | H4 |  |
|  | Nail plate thickness |  |  | mm | 1.2 |  |
|  | Minimum nail plate coverage of the applicable pole ends (tip and butt ends) |  |  | % | 50 |  |
|  | Minimum punched nail length |  |  | mm | 14 |  |
|  | Pole name plate marking shall include: - Name of manufacture - Identification mark of the plant at which the pole was treated - The month and the four digits of the year during which the pole was treated e.g. 01/2013 - Hazard class and the Species e.g. H4, E1 - Strength class e.g. 55 MPa or 75 MPa - The length of the pole, in metre - Batch Number - Specification Number e.g. PIESA 1001 – 2004 |  |  | Yes/No | Yes |  |
|  | Name plate position |  |  | m | 3,5 ± 0.050 from the butt |  |
|  | Ambient Temperature range |  |  | °C | -1 to 40 |  |
|  | Relative Humidity |  |  | % | 85 |  |
|  | Altitude above sea level |  |  | m | 1500 |  |
|  | Previous strength test results/certification from a recognized third party testing facility to be provided with bid for at least one of the following: 9m, 10m and/or 12m pole(s). |  |  | Yes/No | Yes |  |
|  | Quality assurance certification to be provided with bid |  |  | Yes/No | Yes |  |
|  | Strength test results on samples to be provided on delivery |  |  | Yes/No | Yes |  |
|  | Detailed Drawings showing dimensions and tolerances to be provided with Bid |  |  | Yes/No | Yes |  |
|  | Applicable standard |  |  |  | SANS 754 or equivalent regional standard |  |

    - OTHER REQUIREMENTS FOR WOOD POLES

    - Securing of nail plates

- Each nail plate shall be embedded in the pole end and no nail shall be bent.

- A nail plate shall be so positioned in the middle of the cut end that its edges do not protrude over the round face of the timber.

- No wire binding of poles.

# DRAWINGS

- DRAWINGS, DOCUMENTATION AND SAMPLES

  - Drawings and documentation

All drawings shall be to scale and comply in full with the Technical Specification and be fully detailed.

The Contractor shall submit samples of materials as required from time to time by the Employer.

The Contractor shall submit all drawings or samples of materials for review in sufficient time to permit modifications to be made and the drawings or samples resubmitted without delaying the initial deliveries or the completion of the Contract Works.

If the Contractor shall require review of any drawing within four (4) weeks of its submission in order to avoid delay in the completion of the Contract Works, he shall advise the Employer to such effect when submitting the drawing.

The number of copies of each drawing or of any subsequent revision to be submitted to the Employer is given below.  Following review, further copies of the reviewed drawing shall be supplied to the Employer for distribution to Employer and to Site.

Drawings for review shall be submitted electronically in a commonly used format and as paper prints and shall bear the authorized Contract reference.

All drawings shall be drawn to one of the preferred scales quoted in Section 7 of BS Publication PD6031 or available on a standard ruler and on paper of the appropriate size from the International Series of A sizes.

All detail drawings submitted for review shall be to scale and of a size not less than 1/25 full size.  All important dimensions shall be given and the material of which each part is to be constructed shall be indicated.

Except as otherwise specifically approved, all drawings shall be of size not greater than A0 (normally 841 mm x 1189 mm) not smaller than A4 (normally 210 mm x 297 mm).  All prints shall be folded to A4 size and the title, drawing number and revision suffix shall remain visible.

All dimensions marked on the drawings shall be considered correct although measurement by scale may differ there from.  Detailed drawings shall be acted on where they differ from general arrangement drawings.

The Employer reserves the right to request any further additional information that may be considered necessary in order fully to review the Contractor’s drawings.

Any drawing modified from a previously submitted drawing shall bear a new version number.  Revised drawings reissued for review shall have at least one copy clearly marked indicating the amendments to the drawing.  Revision boxes must be provided giving the date, revision letter and brief description of each drawing.

Any drawing or document submitted for information only shall be indicated as such by the Contractor.  Drawings submitted for information only will not be returned to the Contractor unless the Employer considers that such drawings do need to be reviewed, in which case they will be returned suitably stamped with comments.

All drawings submitted by the Contractor shall include the following particulars in a suitable format: Contractor’s name, date, scale, number and title of the drawing, contract number, and overhead line title and equipment description.

The Contractor shall when submitting drawings provide an indexing system for all the drawings divided for each type of equipment.

The drawing format and the indexing system will be agreed at the first Contract meeting between the Contractor and the Employer.

Drawings, samples and models already submitted by the Contractor and reviewed by the Employer (and such drawings, samples and models as shall be thereafter submitted by the Contractor and reviewed by the Employer) shall not be departed from without the instruction in writing of the Employer.

All drawings, samples and models shall be submitted in accordance with the previsions in the Schedules and shall become the property of Employer.

Minimum number of copies of each drawing/calculation/documentation or of any subsequent revision to be submitted to the Employer is given below:

|  | Prints | Electronic Copy by E-mail (see notes | Electronic Copy – on media (CD/USB) |
| --- | --- | --- | --- |
| For approval |  |  |  |
| Calculations and drawings |  | 2 |  |
| Other design documents |  | 2 |  |
| Method statements |  | 2 |  |
| Commissioning procedures |  | 2 |  |
| For construction |  |  |  |
| Calculations and drawings | 2 | 2 |  |
| Other design documents | 2 | 2 |  |
| Method Statements | 2 | 2 |  |
| Commissioning procedures | 2 | 2 |  |
| Final records |  |  |  |
| Calculations and drawings | 3 | 2 | 4 |
| Other design documents | 3 | 2 | 4 |
| Method Statements | 3 | 2 | 4 |
| Commissioning procedures | 3 | 2 | 4 |

  - Sample Drawings

    - Important Instructions to Bidders!

The Bidder shall examine the drawings of this section in close connection with the other documents and particulars forming these Bid Documents.

Where the Specifications and/or Drawings do not contain specific materials or works which are necessary for the proper and safe completion, operation, and maintenance of the equipment in question, all such materials and works shall be deemed to be included in the supply for the turn-key based substations.

In the event of any difference between the Drawings and the Specifications, the latter shall prevail.

Should the Bidder find discrepancies in or omissions from these Specifications or from the other Documents, or should he be in doubt as to their meaning, he should immediately contact the Project Manager for interpretation, clarification, or correction thereof before submitting his Bid. Such action shall, however, in no case be considered as a cause for altering the closing date of the Bid.

    - List of Drawings

The drawing listed below are included for bidders familiarization with the expected 33 kV H-Structures for the 33 kV overhead lines.

- G11390 - 33kV Double Earthed Structure-Straight Line Section Pole

- G11391 - 33KV Section Angle Pole Double Earthed Structure

- G11392 - 33KV Terminal Pole Double Earthed Structure

- G11393 - 33KV Intermediate Pole Double Earthed Construction

- G11394 - 33KV Through Pole (15 Deg) Double Earthed construction

  - Submittals to be attached to the Bid

    - Overhead Line Submittals

      - Drawings

The following are the drawings to be submitted with the Bid:

- General arrangement of:

    - Suspension insulator sets and fittings

    - Tension insulator sets and fittings

- Detailed drawings of:

    - Tension Insulator unit

    - Suspension Insulator unit

    - Crossarm Channel

    - Tension Strap

    - Parallel Groove (P.G.) Clamp

    - Pistol Clamp

    - Strain Clamp

    - Adaptor (Socket & Tongue)

    - Pigtail Hook

    - ’D’ Bracket complete Pin

    - Brass Tap Line

    - Shackle Insulator

    - Stay Assembly Complete

    - Stay Insulator

    - Line conductor tension anchor clamp and midspan joint

    - Cross-section of the complete OPGW, the design and make-up of the cable.

      - Documentation

The following is a list of documentation to be submitted with the Bid.

- Programme of anticipated works, to conform with completion times required in the Special Conditions of Contract.

- Details of the method of working to demonstrate that the specified Quality Assurance requirements will be complied with.

- Copies of any standards proposed in substitution for International Electro-technical Commission Standards or Recommendations or British Standards accompanied where necessary by English translations of the appropriate sections.

- Record of previous service experience of the fibre-optic earth wire offered.

- Documentary evidence of satisfactory service history of the insulators.

- Other supporting documentation considered appropriate by the Bid.

  - Submittals during contract period

    - Programme of submittals

The Contractor shall arrange his design and drawing programme so that the works can be properly co-ordinated by the Employer.  He shall provide the documentation as specified below within four (4) weeks of the award of Contract, together with any drawings and information considered necessary by the Contractor or Employer.

- Confirmation of contract documentation

- A detailed schedule of all plant to be supplied under the Contract.  This schedule shall have space for the following information as a minimum requirement in respect of each item:

  - Manufacturer

  - Country of origin

  - Planned FOB delivery date

  - Planned date of arrival on site

  - Sub-order number (as applicable)

  - Allocated drawing numbers

- A preliminary schedule of drawings to be submitted to the Employer for approval in respect of all items of equipment to be supplied under the Contract.  The schedule shall include a programme for submittal of all drawings required by the Specification.

The schedule shall have space for at least the following information to be added at a later date: -

  - Drawing number

  - Drawing title

  - Proposed date of submission

  - Actual date of submission

  - Resubmissions

  - Revision numbers

  - Date of approval

  - Release as a working drawing

  - Date to site

  - Date to Employer

  - Date of as-built drawing

    - Drawing numbers

The Contractor will apply drawing numbers to all drawings, including those from sub-contractors and those issued for information before they are submitted to the Employer.  The Contractor’s drawing office will be expected to issue the numbers in batches that will cover broad subject areas.  For instance, the Contractor might propose batches for pole structure, insulators, conductors, profiles, etc.  The Contractor shall submit to the Employer for approval the subject areas he proposes to use prior to the issue of any drawing.  The Contractor shall each month issue an up-to-date drawing list to the Employer.

    - Overhead Line Drawings & Records

      - Drawings to be submitted during the contract period

- Design drawings and documents detailing:

- Calculations giving the design basis to be employed for the sags and tensions for the line and earth conductors for both final and erection conditions and calculations providing data for the manufacture of the sag templates.

- Derivation of applied loads for all towers including wind on structure.

- Detailed live metal or wire clearance diagrams for each type of tower.

- Basis to be employed for the design of structures.

- Analysis of maximum member and connection loads and capacities for all members in standard towers, body and leg extensions.

- Structure foundation loads for all loading cases demonstrating that the critical condition for any combination of body and leg extension has been considered.

- Foundation designs for all standard classes, including stub and cleat designs.

- Concrete mix design.

- Arrangement drawings of:

- Each type of standard tower, body and leg extension showing connection to foundations, insulator and earth conductor attachments and complete with all necessary erection information and part list including weight.

- Stubs, foundations (including details of reinforcement, excavation, stub setting).

- Special towers, extensions and foundations (as required).

- Detail drawings of:

  - Suspension and tension insulator sets, with all fittings and securing devices.

  - Insulator units, showing cross section and details of securing device.

  - Line conductor tension clamps and joints.

  - Tension make-offs and suspension clamps for earth conductors.

  - Vibration dampers for line and earth conductors including calculations to demonstrate the efficacy of the proposed system.

  - All OPGW ancillary equipment.

  - Tower earthing arrangements.

  - Tower obstruction lighting and marking.

  - Proposed live-line maintenance equipment.

  - Danger and property, route and tower number, circuit colour, phase and aerial number plates.

  - Curves showing the initial and final sags and tensions of the line and earth conductors at different spans and temperatures, all in accordance with the Specification.

  - Route plans, schedules and profile drawings all in accordance with the Specification.

      - Specific required Contractor’s Records

Throughout the progress of all distribution line Works, the Contractor shall maintain the Following technical documents and records in format approved by the Employer which will facilitate their respective incorporation into the operation and maintenance manuals described:

- All road, rail, crossing details including crossing of major bodies of water as appropriate, identification of key access points and any other relevant as-built information;

- Included with this structure list shall be an approved table summarizing all pertinent data relating to the line design and construction, including but not limited to conductor and insulator types, manufacture and specifications, lists of Drawings relating to the line;

- All Plan and Profile sheets shall be suitably completed and corrected to show as-constructed 33 kV H-structure and final amended span lengths, shield wire and conductor maximum temperature curves and any other relevant data normally presented on profile sheets;

- Detailed 33 kV H-Structure records shall include pole bury depth, soil description and earth resistance measurement shall also be given;

- A complete set of stringing and sagging records sheets shall be kept. These sheets shall show the ruling span, control span, check spans, sagging spans and details of temperature and actual observed sag;

- A complete set of records indicating the location of midspan tension joints (if any) and showing the phase conductor or shield wire concerned.

- A complete set of distribution line software design packages for the 33kV structures and 33 kV line profiles.

      - Final Records

The list of drawings required for final record purposes is given below:

- Insulator sets plus component parts

- Earth conductor suspension and tension sets plus component parts

- All types of connectors and joints

- Earthing details

- Line conductor and earth conductor initial/final sag-tension charts

- Wire clearance diagrams

- Profiles and strip plans

- Route maps

- Line schedules

- Earth resistance chart

- Notice plates and accessories.

    - Final records- General Requirements

After completion of work on Site all Contract drawings shall be revised where necessary to show the equipment as installed and the number of copies of revised drawings as specified in this Section shall be submitted for review.  A complete set of reviewed records shall be provided comprising, one full size reproducible copy and one full size print.  Record drawings shall be endorsed “As Built” and shall be correctly titled and carry the Employer’s review number, Contractor’s drawing number and where appropriate Employer’s number allocated to the item.

After final review of the “As Built” record drawings the Contractor shall submit complete sets of records on compact discs, one of which is for Employer as detailed in Part 2.  Electronic copies of the drawings shall be in electronic format suitable for reproduction on paper using Employer’s preferred software packages.  Each disc shall provide a comprehensive drawing list containing the drawing number, sheet, revision and title of every drawing.  Each single file drawing record shall be self-supporting without referencing other files.  Non-standard items such as fonts, line types, etc. should not be used.  If compression techniques are applied to files, then any software necessary to decompress the files shall be included on the discs.  The Contractor shall ensure that all information contained on the discs has been checked for virus contamination.  Each compact disc shall be supplied suitably encased and accompanied with printed documentation describing the contents of the compact discs, the formats and software used to compile the discs and the print hardware required to reproduce the record drawings.

Final record copies shall be handed over before the issue of the Taking Over Certificate.

    - Installation and maintenance instructions

The Contract Price shall be deemed to include illustrated installation and maintenance instructions written in English.

Before commencement of conductor stringing the Contractor shall submit to the Employer for review fully detailed operating and maintenance instructions for compressors and any other working equipment.  Also, to be included are instructions on the method of making compression joints and the methods to be used for the erection of all fittings on the line together with the necessary tests and checks to ensure fitting has been successfully effected.  The instructions are to be as simple and clear as possible, fully illustrated with drawings and diagrams as necessary and detailed with part numbers for ordering of replacements.  Two (2) copies are required for use of the Employer during erection work.

Further copies are to be reproduced as a book or books of approximately A4 size and bound into strong black durable imitation leather covers inscribed upon the front generally in the form of the title page to this document except that the references to Specification, Conditions of Contract, drawings, etc, will be replaced by “Installation and Maintenance Instructions”.  The name of Employer shall be inscribed upon the spine.  The finished books are to be handed to the Employer not later than one (1) month before the Taking-Over Certificate is issued.